## ELINK (3)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_50%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 32.18
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 59.56
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 200.5 | 200.5
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 857.0001 | 857.0001
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.2158 | 5.2158
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.4352 | 153.4352
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.7969 | 99.7969
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.47583 | 0.47583
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 5.5636 | 5.5636
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 88.7768 | 88.7768
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 73.9174 | 73.9174
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 1.3878 | 1.3878
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 13.7909 | 13.7909
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 2.8631 | 2.8631
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 14.3538 | 14.3538
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 2.8631 | 2.8631
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 14.3538 | 14.3538
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 1.3878 | 1.3878
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 13.7909 | 13.7909
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 198.5162 | 198.5162
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 222.4745 | 222.4745
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 40.05
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 531.4 | 531.4
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 29.22
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 71.35 | 71.35
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 22.93 | 22.93
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 15.31 | 15.31
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.268 | 5.268
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 4.556 | 4.556
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.806 | 1.806
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.11 | 1.11
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.331 | 0.331
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 32.18
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 59.56
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~~4~~-5000~ | Plant Summary: Gross power | kW | 55563.4844 | 55563.4844
~~~7~~-5000~ | Plant Summary: Net power | kW | 50058.3711 | 50058.3711
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 5505.1123 | 5505.1123
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 5227.2949 | 5227.2949
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 277.8174 | 277.8174
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 34.8285 | 34.8285
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10336.3652 | 10336.3652
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.3778 | 31.3778
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11473.0957 | 11473.0957
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 159534.5781 | 159534.5781
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.3778 | 31.3778
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.3778 | 31.3778
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.4082 | 28.4082
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12672.4102 | 12672.4102
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 176211.1719 | 176211.1719
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 159534.5781 | 159534.5781
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.3778 | 31.3778
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 0.55332 | 0.55332
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.50125 | 0.50125
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 159534.5781 | 159534.5781
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 176211.1719 | 176211.1719
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 1400.8823 | 1400.8823
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 16955324 | 16955324
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 21785416 | 21785416
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 405.4728 | 405.4728
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 4652.0288 | 4652.0288
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 4.5337 | 4.5337
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 439.0747 | 439.0747
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 21785.416 | 21785.416
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 435.2003 | 435.2003
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 217199.0469 | 217199.0469
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 6535.625 | 6535.625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 44.1091 | 44.1091
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 122.7651 | 122.7651
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.83582 | 0.83582
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 110028.5547 | 110028.5547
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.03633 | 0.03633
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 4.938 | 4.938
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 16955324 | 16955324
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 16955324 | 16955324
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 3304113.25 | 3304113.25
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 20259438 | 20259438
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 21785416 | 21785416
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 55563.4883 | 55563.4883
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 520.5316 | 520.5316
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 217.5947 | 217.5947
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 578.6446 | 578.6446
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 146.0763 | 146.0763
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 299.2756 | 299.2756
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 146.0763 | 146.0763
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 299.2756 | 299.2756
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 497.6537 | 497.6537
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 52.5018 | 52.5018
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 649.8464 | 649.8464
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 649.8465 | 649.8465
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 497.6537 | 497.6537
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 116.6833 | 116.6833
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 555.6349 | 555.6349
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 277.8174 | 277.8174
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 5227.2949 | 5227.2949
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 159534.5781 | 159534.5781
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 9.6954 | 9.6954
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 271946.6562 | 271946.6562
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 365712.4375 | 365712.4375
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 15467.9766 | 15467.9766
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 4933.8022 | 4933.8022
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 11213.1104 | 11213.1104
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 1368.9108 | 1368.9108
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 7549.6353 | 7549.6353
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 3353.9839 | 3353.9839
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 7162.0562 | 7162.0562
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 5518.8594 | 5518.8594
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 520.5316 | 520.5316
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 217.5947 | 217.5947
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 578.6446 | 578.6446
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 146.0763 | 146.0763
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 299.2756 | 299.2756
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 146.0763 | 146.0763
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 299.2756 | 299.2756
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 497.6537 | 497.6537
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 52.5018 | 52.5018
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 649.8464 | 649.8464
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 649.8465 | 649.8465
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 497.6537 | 497.6537
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 160.4 | 160.4
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 40.1 | 40.1
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 89.6174 | 89.6174
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 303.0413 | 303.0413
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2743.5149 | 2743.5149
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 857.0001 | 857.0001
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 303.0413 | 303.0413
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 65.91
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 2.9438
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.2498
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 17.1003
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0031714
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79282
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 94420.7578 | 94420.7578
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 61569.6211 | 61569.6211
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 15392.4053 | 15392.4053
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 7443.2061 | 7443.2061
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 10015.5273 | 10015.5273
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 1396.3406 | 1396.3406
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 1888.4152 | 1888.4152
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 273.5357 | 273.5357
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 638.25 | 638.25
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 95.7607 | 95.7607
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 172.9346 | 172.9346
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 166.4993 | 166.4993
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.085227 | 0.085227
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.31018 | 0.31018
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 37.8785 | 37.8785
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 909.0823 | 909.0823
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 159534.5781 | 159534.5781
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 176211.1719 | 176211.1719
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 378.7842 | 378.7842
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 141.7473 | 141.7473
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 2.5038 | 2.5038
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.14905 | 0.14905
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.39087 | 0.39087
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 3.5437 | 3.5437
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.0631 | 1.0631
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 2.4806 | 2.4806
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 2.9438
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 17.1003
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.2158 | 5.2158
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.4352 | 153.4352
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.2567 | 5.2567
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 147.4578 | 147.4578
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 621.2406 | 621.2406
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 185.8018 | 185.8018
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 5.2158 | 5.2158
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 253.7416 | 253.7416
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2968.178 | 2968.178
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.6261 | 1.6261
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 15.0098 | 15.0098
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 163.4898 | 163.4898
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 691.1366 | 691.1366
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 23.4067 | 23.4067
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 647.1015 | 647.1015
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 210.8345 | 210.8345
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.9985 | 23.9985
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 79.3894 | 79.3894
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0035 | 460.0035
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 205.3774 | 205.3774
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3299.7864 | 3299.7864
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 79.3894 | 79.3894
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0049 | 436.0049
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 210.3333 | 210.3333
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3237.772 | 3237.772
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 4.9558 | 4.9558
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 667.8066 | 667.8066
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5995 | 22.5995
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 80.9772 | 80.9772
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.105 | 434.105
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 200.5 | 200.5
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3230.1714 | 3230.1714
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 80.9772 | 80.9772
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5055 | 411.5055
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 205.3774 | 205.3774
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3169.3186 | 3169.3186
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 4.8774 | 4.8774
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 667.8066 | 667.8066
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 16.1319 | 16.1319
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 98.3662 | 98.3662
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 16.7952 | 16.7952
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 16.7952 | 16.7952
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 16.1319 | 16.1319
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 201.0013 | 201.0013
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 97.683 | 97.683
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 946.6247 | 946.6247
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 220.1776 | 220.1776
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 201.0013 | 201.0013
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 89.6174 | 89.6174
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 303
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1361.6749 | 1361.6749
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 266.7267 | 266.7267
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 2.4806 | 2.4806
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 527.1766 | 527.1766
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 264.9475 | 264.9475
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 56.5243
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1159.5444 | 1159.5444
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 23174.1426 | 23174.1426
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 23174.1426 | 23174.1426
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 173.8061 | 173.8061
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 8.0656 | 8.0656
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.7969 | 99.7969
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 217.5947 | 217.5947
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 126.1789 | 126.1789
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 317212.8438 | 317212.8438
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 266.7265 | 266.7265
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 2.4806 | 2.4806
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 2.4755 | 2.4755
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0050378 | 0.0050378
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3910.4263 | 3910.4263
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 12309.6279 | 12309.6279
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9417 | 7.9417
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 24.9997 | 24.9997
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 98.3914 | 98.3914
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2166 | 1.2166
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 286.3094 | 286.3094
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 286.3094 | 286.3094
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 283.4463 | 283.4463
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 14.3538 | 14.3538
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 2.8631 | 2.8631
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 314.2394 | 314.2394
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 95.689 | 95.689
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 299.2756 | 299.2756
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 286.3094 | 286.3094
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 95.6675 | 95.6675
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 12.9662 | 12.9662
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 300.6249 | 300.6249
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 556.3565 | 556.3565
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 556.3565 | 556.3565
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 550.793 | 550.793
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 88.7768 | 88.7768
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.137 | 80.137
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 5.5636 | 5.5636
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 607.5768 | 607.5768
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.1674 | 96.1674
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 578.6446 | 578.6446
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 556.3565 | 556.3565
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.1482 | 96.1482
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 22.2881 | 22.2881
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 584.1743 | 584.1743
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 138.7824 | 138.7824
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 138.7824 | 138.7824
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 137.3946 | 137.3946
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 13.7909 | 13.7909
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 1.3878 | 1.3878
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 153.3801 | 153.3801
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.0316 | 95.0316
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 146.0763 | 146.0763
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 138.7824 | 138.7824
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.0068 | 95.0068
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 7.2939 | 7.2939
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 145.7216 | 145.7216
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 286.3094 | 286.3094
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 286.3094 | 286.3094
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 283.4463 | 283.4463
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 14.3538 | 14.3538
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 2.8631 | 2.8631
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 314.2394 | 314.2394
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 95.689 | 95.689
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 299.2756 | 299.2756
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 286.3094 | 286.3094
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 95.6675 | 95.6675
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 12.9662 | 12.9662
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 300.6249 | 300.6249
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 138.7824 | 138.7824
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 138.7824 | 138.7824
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 137.3946 | 137.3946
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 13.7909 | 13.7909
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 1.3878 | 1.3878
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 153.3801 | 153.3801
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.0316 | 95.0316
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 146.0763 | 146.0763
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 138.7824 | 138.7824
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.0068 | 95.0068
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 7.2939 | 7.2939
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 145.7216 | 145.7216
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.32451 | 0.32451
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 70.9113 | 70.9113
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 4847.1968 | 4847.1968
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 4152.4326 | 4152.4326
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 694.7637 | 694.7637
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 22.4597 | 22.4597
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.0882 | 1.0882
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 101.987 | 101.987
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 6733.3198 | 6733.3198
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 5927.1265 | 5927.1265
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 806.1935 | 806.1935
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 31.0753 | 31.0753
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 1.7706 | 1.7706
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 116.4022 | 116.4022
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 3142.157 | 3142.157
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 2943.1038 | 2943.1038
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 199.0532 | 199.0532
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.4141 | 14.4141
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 4.4667 | 4.4667
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 147.634 | 147.634
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 7274.0278 | 7274.0278
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 6517.9141 | 6517.9141
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 395.3543 | 395.3543
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 360.7595 | 360.7595
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 33.027 | 33.027
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 0.19775 | 0.19775
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 15.0098 | 15.0098
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 198.3262 | 198.3262
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 10132.6807 | 10132.6807
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 7854.5508 | 7854.5508
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 1278.6514 | 1278.6514
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 999.4786 | 999.4786
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 41.5853 | 41.5853
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 22.4804 | 22.4804
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 218.3745 | 218.3745
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 5937.5054 | 5937.5054
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 4773.2168 | 4773.2168
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1016.0961 | 1016.0961
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 148.1922 | 148.1922
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 23.62 | 23.62
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.7725 | -3.7725
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7607 | 15181.7607
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 37.8785 | 37.8785
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 159534.5781 | 159534.5781
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 176211.1719 | 176211.1719
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 1400.8823 | 1400.8823
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15162.0674
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15181.7607
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16839.0098
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 10.41
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 40.05
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 6.9687
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 32.1803
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 59.0533 | 59.0533
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.026705 | 0.026705
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 32.1803
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 56.7375 | 56.7375
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.025658 | 0.025658
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 32.1803
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 59.0533 | 59.0533
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.026705 | 0.026705
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 32.1803
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 56.7375 | 56.7375
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.025658 | 0.025658
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.3099
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 477.9645 | 477.9645
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 463.6255 | 463.6255
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 497.6536 | 497.6536
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 3993.5029 | 3993.5029
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 3993.5029 | 3993.5029
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 515.0408 | 515.0408
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.0574 | 96.0574
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 497.6536 | 497.6536
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 477.9645 | 477.9645
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.0436 | 96.0436
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 19.6891 | 19.6891
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 494.6637 | 494.6637
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.3099
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 477.9645 | 477.9645
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 463.6255 | 463.6255
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 497.6536 | 497.6536
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 3993.5029 | 3993.5029
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 3993.5029 | 3993.5029
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 515.0408 | 515.0408
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.0574 | 96.0574
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 497.6536 | 497.6536
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 477.9645 | 477.9645
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.0436 | 96.0436
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 19.6891 | 19.6891
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 494.6637 | 494.6637
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.0574 | 96.0574
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 70.7352 | 70.7352
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.8677 | 6.8677
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.8677 | 6.8677
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 75.0006 | 75.0006
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 49.2097 | 49.2097
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 47.7334 | 47.7334
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 52.5018 | 52.5018
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 185.8018 | 185.8018
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.4265 | 45.4265
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.1982 | 190.1982
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 185.8018 | 185.8018
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3251 | 7.3251
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5033 | 45.5033
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.1231 | 191.1231
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 54.3362 | 54.3362
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 93.7513 | 93.7513
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 52.5018 | 52.5018
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 49.2097 | 49.2097
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 93.7294 | 93.7294
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 3.2922 | 3.2922
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 50.929 | 50.929
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1055.7338 | 1055.7338
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 96.0399 | 96.0399
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 96.0399 | 96.0399
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 49.9999 | 49.9999
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 625.0675 | 625.0675
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 606.3155 | 606.3155
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 649.8464 | 649.8464
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 105.4173 | 105.4173
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 105.4173 | 105.4173
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 99.4872 | 99.4872
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 141.7198 | 141.7198
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 602.7352 | 602.7352
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 903.2138 | 903.2138
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.4074 | 96.4074
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 649.8464 | 649.8464
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 625.0675 | 625.0675
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.187 | 96.187
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 24.7789 | 24.7789
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 868.7739 | 868.7739
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1055.7338 | 1055.7338
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 96.0399 | 96.0399
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 96.0399 | 96.0399
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 49.9999 | 49.9999
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 625.0676 | 625.0676
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 606.3156 | 606.3156
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 649.8465 | 649.8465
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 105.4173 | 105.4173
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 105.4173 | 105.4173
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 99.4872 | 99.4872
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 141.7198 | 141.7198
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 602.7352 | 602.7352
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 903.2139 | 903.2139
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.4074 | 96.4074
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 649.8465 | 649.8465
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 625.0676 | 625.0676
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.187 | 96.187
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 24.7789 | 24.7789
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 868.7739 | 868.7739
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 0.55332 | 0.55332
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 185.2484 | 185.2484
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 185.8018 | 185.8018
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.4265 | 45.4265
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.1982 | 190.1982
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0070449 | 0.0070449
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99296 | 0.99296
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 1.3954e-09 | 1.3954e-09
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 11678.3018 | 11678.3018
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 5719.4507 | 5719.4507
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 5958.8516 | 5958.8516
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 5690.9956 | 5690.9956
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 5929.2056 | 5929.2056
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 58.1006 | 58.1006
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.052159 | 0.052159
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 1 | 1
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.40651 | 0.40651
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.2843 | 1.2843
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.44961 | 0.44961
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 2.5383 | 2.5383
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.3002 | 0.3002
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 3.9634 | 3.9634
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.089333 | 0.089333
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 3.056 | 3.056
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.035412 | 0.035412
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 1.2933 | 1.2933
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.021765 | 0.021765
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 2.6303 | 2.6303
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0064902 | 0.0064902
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 1.8249 | 1.8249
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 0.97683 | 0.97683
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 502.5092 | 502.5092
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 202.6887 | 202.6887
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.9482 | 0.9482
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7491 | 10.7491
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.04664 | 0.04664
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.95336 | 0.95336
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00077311 | 0.00077311
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99816 | 0.99816
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010692 | 0.0010692
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95643 | 0.95643
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.043574 | 0.043574
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92886 | 0.92886
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.071139 | 0.071139
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99214 | 0.99214
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0078553 | 0.0078553
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.94048 | 0.94048
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.059521 | 0.059521
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96981 | 0.96981
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0034013 | 0.0034013
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.026784 | 0.026784
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94383 | 0.94383
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.056166 | 0.056166
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.96243 | 0.96243
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.037571 | 0.037571
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 1.3954e-09 | 1.3954e-09
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50399 | 0.50399
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49601 | 0.49601
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 130.4938 | 130.4938
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 57.0002
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.9678
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 1303.4756 | 1303.4756
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 2.9438
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.2498
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 17.1003
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 65.91
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79282
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0031714
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.829
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 93.8988
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 32.8529
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0050378 | 0.0050378
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9417 | 7.9417
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9997 | 24.9997
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 2.9438
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 17.1003
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 210.3333 | 210.3333
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 79.3894 | 79.3894
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3237.772 | 3237.772
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0049 | 436.0049
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 210.3333 | 210.3333
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 72.8343 | 72.8343
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 531.4 | 531.4
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3484.0369 | 3484.0369
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 266.7267 | 266.7267
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 2.4806 | 2.4806
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 857.0001 | 857.0001
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 709.7034 | 709.7034
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 14388.4736 | 14388.4736
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 6.5551 | 6.5551
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 200.5 | 200.5
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 87.8602 | 87.8602
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2923.342 | 2923.342
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 339.0002 | 339.0002
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 200.5 | 200.5
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 80.9772 | 80.9772
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3230.1714 | 3230.1714
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 266.7267 | 266.7267
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 2.4806 | 2.4806
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 709.7033 | 709.7033
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 527.1765 | 527.1765
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 17088.9531 | 17088.9531
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 128.1671 | 128.1671
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 6.8831 | 6.8831
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 97.683 | 97.683
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 220.1776 | 220.1776
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 946.6247 | 946.6247
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 201.0013 | 201.0013
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 97.683 | 97.683
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 220.1776 | 220.1776
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 946.6247 | 946.6247
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.2 | 0.2
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 72.8343 | 72.8343
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 531.3991 | 531.3991
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3484.0369 | 3484.0369
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 210.3333 | 210.3333
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 72.6343 | 72.6343
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 531.3125 | 531.3125
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3484.0369 | 3484.0369
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 99.4872 | 99.4872
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.1051 | 152.1051
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 99.4872 | 99.4872
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.1051 | 152.1051
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 99.4872 | 99.4872
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 156.931 | 156.931
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 667.8068 | 667.8068
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 105.4173 | 105.4173
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 99.4872 | 99.4872
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 156.931 | 156.931
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 667.8068 | 667.8068
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 99.4872 | 99.4872
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 156.931 | 156.931
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 667.8068 | 667.8068
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 105.4173 | 105.4173
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 99.4872 | 99.4872
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 156.931 | 156.931
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 667.8068 | 667.8068
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 105.4173 | 105.4173
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 105.4173 | 105.4173
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 39.3118
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 164.8358
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 7987.0059 | 7987.0059
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 29.2416
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 122.5732
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 7987.0059 | 7987.0059
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 92838.1484 | 92838.1484
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 55563.4844 | 55563.4844
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.2237 | 98.2237
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 87.5125 | 87.5125
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 29.1708 | 29.1708
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 64.8241 | 64.8241
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.2478 | 98.2478
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 74.9175 | 74.9175
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 530.7554 | 530.7554
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 209.9458 | 209.9458
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 58341.6562 | 58341.6562
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.2478 | 98.2478
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 55563.4844 | 55563.4844
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 56568.332 | 56568.332
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.2237 | 98.2237
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1004.8465 | 1004.8465
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 882.1718 | 882.1718
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 122.6747 | 122.6747
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 9.0153 | 9.0153
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.2218 | 4.2218
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 111424.125 | 111424.125
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 8.673 | 8.673
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.1754 | 3.1754
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 104761.9141 | 104761.9141
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 17.6883 | 17.6883
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.2218 | 4.2218
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 216186.0469 | 216186.0469
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 19.9505 | 19.9505
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.0661 | 5.0661
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 13980676 | 13980676
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 16955324 | 16955324
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 71.35 | 71.35
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 71.35 | 71.35
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 530.7554 | 530.7554
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 209.9458 | 209.9458
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3484.0369 | 3484.0369
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 209.7123 | 209.7123
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 71.35 | 71.35
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3484.0369 | 3484.0369
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 22.93 | 22.93
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3217.8464 | 3217.8464
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 22.93 | 22.93
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 388.5145 | 388.5145
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 209.7123 | 209.7123
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3217.8464 | 3217.8464
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 7.5035 | 7.5035
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.0072664 | 0.0072664
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1116 | 3.1116
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 72.7786 | 72.7786
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 74.9673 | 74.9673
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 74.9673 | 74.9673
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 15506.7432 | 15506.7432
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 15467.9766 | 15467.9766
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 38.7668 | 38.7668
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 22.93 | 22.93
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 22.93 | 22.93
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 388.5145 | 388.5145
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 200.5742 | 200.5742
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3217.8464 | 3217.8464
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 200.5742 | 200.5742
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 22.93 | 22.93
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3217.8464 | 3217.8464
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 15.31 | 15.31
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3129.0718 | 3129.0718
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 15.31 | 15.31
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 341.5981 | 341.5981
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 200.5742 | 200.5742
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3129.0718 | 3129.0718
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 10.0253 | 10.0253
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.019774 | 0.019774
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4977 | 1.4977
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 77.431 | 77.431
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 77.8336 | 77.8336
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 77.8336 | 77.8336
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 4946.1675 | 4946.1675
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 4933.8022 | 4933.8022
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 12.3654 | 12.3654
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 15.31 | 15.31
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 15.31 | 15.31
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 341.5981 | 341.5981
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 186.3056 | 186.3056
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3129.0718 | 3129.0718
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 186.3056 | 186.3056
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 15.31 | 15.31
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3129.0718 | 3129.0718
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 5.268 | 5.268
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2911.8601 | 2911.8601
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 5.268 | 5.268
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.9248 | 226.9248
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 186.3056 | 186.3056
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2911.8601 | 2911.8601
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 22.1664 | 22.1664
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.026568 | 0.026568
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9062 | 2.9062
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 81.94 | 81.94
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 83.3065 | 83.3065
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 83.3065 | 83.3065
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 11241.2129 | 11241.2129
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 11213.1104 | 11213.1104
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 28.103 | 28.103
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 5.268 | 5.268
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 5.268 | 5.268
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.9248 | 226.9248
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 184.8421 | 184.8421
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2911.8601 | 2911.8601
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 184.8421 | 184.8421
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 5.268 | 5.268
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2911.8601 | 2911.8601
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 4.556 | 4.556
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2885.1326 | 2885.1326
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 4.556 | 4.556
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 212.7618 | 212.7618
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 184.8421 | 184.8421
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2885.1326 | 2885.1326
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 24.7252 | 24.7252
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.069329 | 0.069329
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1563 | 1.1563
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 82.971 | 82.971
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 82.9709 | 82.9709
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 82.9709 | 82.9709
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 1372.3416 | 1372.3416
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 1368.9108 | 1368.9108
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 3.4309 | 3.4309
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 4.556 | 4.556
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 4.556 | 4.556
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 212.7618 | 212.7618
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 173.8402 | 173.8402
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2885.1326 | 2885.1326
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 173.8402 | 173.8402
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 4.556 | 4.556
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2885.1326 | 2885.1326
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 1.806 | 1.806
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2728.4001 | 2728.4001
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 1.806 | 1.806
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 129.6388 | 129.6388
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 173.8402 | 173.8402
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2728.4001 | 2728.4001
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 48.7446 | 48.7446
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.074341 | 0.074341
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5227 | 2.5227
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.2419 | 85.2419
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 85.9414 | 85.9414
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 85.9414 | 85.9414
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 7568.5566 | 7568.5566
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 7549.6353 | 7549.6353
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 18.9214 | 18.9214
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 1.806 | 1.806
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 1.806 | 1.806
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 129.6388 | 129.6388
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 168.5928 | 168.5928
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2728.4001 | 2728.4001
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 168.5928 | 168.5928
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 1.806 | 1.806
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2728.4001 | 2728.4001
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.11 | 1.11
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2656.6035 | 2656.6035
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.11 | 1.11
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 102.5497 | 102.5497
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 168.5928 | 168.5928
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2656.6035 | 2656.6035
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 71.2185 | 71.2185
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.16579 | 0.16579
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.627 | 1.627
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 84.8771 | 84.8771
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 84.877 | 84.877
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 84.877 | 84.877
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 3362.3899 | 3362.3899
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 3353.9839 | 3353.9839
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 8.406 | 8.406
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.11 | 1.11
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.11 | 1.11
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 102.5497 | 102.5497
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 159.1236 | 159.1236
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2656.6035 | 2656.6035
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 159.1236 | 159.1236
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.11 | 1.11
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2656.6035 | 2656.6035
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.331 | 0.331
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2494.166 | 2494.166
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.331 | 0.331
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 71.3726 | 71.3726
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 159.1236 | 159.1236
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2494.166 | 2494.166
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 198.6041 | 198.6041
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.24374 | 0.24374
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.3535 | 3.3535
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 86.8568 | 86.8568
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.2836 | 85.2836
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.2836 | 85.2836
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 7180.0063 | 7180.0063
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 7162.0562 | 7162.0562
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 17.95 | 17.95
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.331 | 0.331
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.331 | 0.331
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 71.3726 | 71.3726
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 153.1451 | 153.1451
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2494.166 | 2494.166
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 153.1451 | 153.1451
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.331 | 0.331
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2494.166 | 2494.166
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2356.2915 | 2356.2915
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 153.3265 | 153.3265
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2364.5938 | 2364.5938
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 572.9338 | 572.9338
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 3.8712 | 3.8712
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 147.9986 | 147.9986
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2032.2527 | 2032.2527
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 606.3444 | 606.3444
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 7.8189 | 7.8189
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 10.5824 | 10.5824
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 0.72049 | 0.72049
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 3.3604 | 3.3604
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 86.8102 | 86.8102
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.9608 | 76.9608
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 81.5877 | 81.5877
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 5532.6909 | 5532.6909
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 5518.8594 | 5518.8594
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 13.8317 | 13.8317
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 71.35 | 71.35
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 1.806 | 1.806
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 530.7554 | 530.7554
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 498.2152 | 498.2152
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 1.806 | 1.806
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 498.2152 | 498.2152
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.9298 | 497.9298
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 71.35 | 71.35
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 1.806 | 1.806
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 530.7554 | 530.7554
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 498.2152 | 498.2152
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 1.806 | 1.806
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 498.2152 | 498.2152
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.9298 | 497.9298
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.23352 | 0.23352
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3484.0369 | 3484.0369
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.061311 | 0.061311
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.18144 | 0.18144
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.1134 | 0.1134
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 93.442 | 93.442
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 84.5987 | 84.5987
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 159.5346 | 159.5346
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 176.2112 | 176.2112
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 37.8785 | 37.8785
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 149072.3281 | 149072.3281
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 72.6343 | 72.6343
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 531.3125 | 531.3125
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 210.3333 | 210.3333
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3484.0369 | 3484.0369
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 97.683 | 97.683
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 220.1776 | 220.1776
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 201.0013 | 201.0013
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 946.6247 | 946.6247
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 126.1789 | 126.1789
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 266.7265 | 266.7265
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 2.4806 | 2.4806
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 82.1807 | 82.1807
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 6.9277 | 6.9277
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.61743 | 0.61743
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 110.7232 | 110.7232
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.6375
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 88.1147 | 88.1147
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.84084 | 0.84084
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 65.91
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 2.9438
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 17.1003
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79282
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 3.5511
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 40.6977
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 56.7375 | 56.7375
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 40.3933
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 13.1139 | 13.1139
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2018
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 59.0533 | 59.0533
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 14.3538 | 14.3538
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 49.0609
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 59.0533 | 59.0533
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 28.3036
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 13.0025 | 13.0025
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.2616
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 264.9479 | 264.9479
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 266.7265 | 266.7265
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 2.4806 | 2.4806
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 216.205 | 216.205
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.94953 | 0.94953
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 267.0956 | 267.0956
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 117.2363 | 117.2363
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.63198 | 0.63198
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 65.91
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 3.5511
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99235
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 709.7034 | 709.7034
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 266.7265 | 266.7265
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 2.4806 | 2.4806
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 743.4164 | 743.4164
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6787 | 1.6787
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 809.689 | 809.689
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 213.0601 | 213.0601
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34775 | 0.34775
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 65.91
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 527.1766 | 527.1766
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 266.7265 | 266.7265
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 2.4806 | 2.4806
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 516.4397 | 516.4397
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4205 | 1.4205
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 579.4244 | 579.4244
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.6375
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 173.9293 | 173.9293
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42598 | 0.42598
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 65.91
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 2.9438
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 17.1003
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79282
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 3.5511
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 223.0611
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 118.1066 | 118.1066
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.1335
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.68255
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 204.3276
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.053411 | 0.053411
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 40.6496 | 40.6496
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.80708
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 92378.9219 | 92378.9219
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 48.0609
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 118.1066 | 118.1066
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 29.6329
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.053411 | 0.053411
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 26.0343 | 26.0343
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2602
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 92378.9219 | 92378.9219
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 857.0001 | 857.0001
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 266.7265 | 266.7265
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 2.4806 | 2.4806
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 926.2608 | 926.2608
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.8605 | 1.8605
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1002.186 | 1002.186
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 244.3768 | 244.3768
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.30318 | 0.30318
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 65.91
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 214.6979
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 113.475 | 113.475
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.14532
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.68683
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 195.5857
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.051316 | 0.051316
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 41.4292 | 41.4292
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76084
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 88756.2188 | 88756.2188
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 39.6977
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 113.475 | 113.475
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 42.4078
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.051316 | 0.051316
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 26.2638 | 26.2638
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2002
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 88756.2188 | 88756.2188
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.9668
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 124.9789 | 124.9789
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 266.7265 | 266.7265
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0050378 | 0.0050378
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 81.1229 | 81.1229
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 7.1278 | 7.1278
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.61652 | 0.61652
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 109.3952 | 109.3952
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.6375
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 88.586 | 88.586
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.83637 | 0.83637
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 65.91
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 2.9438
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 17.1003
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79282
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 3.5511
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 123.7789 | 123.7789
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 266.7265 | 266.7265
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0050378 | 0.0050378
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 80.0668 | 80.0668
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 7.3589 | 7.3589
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.61468 | 0.61468
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 108.0676 | 108.0676
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 88.7768 | 88.7768
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.83457 | 0.83457
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 65.91
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 3.5511
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 130.4938 | 130.4938
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 266.7265 | 266.7265
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0050378 | 0.0050378
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 86.0002 | 86.0002
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 6.3151 | 6.3151
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.61837 | 0.61837
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 115.5015 | 115.5015
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.6375
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 54.3115 | 54.3115
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 85.7673 | 85.7673
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.86386 | 0.86386
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 65.91
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 2.9438
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 17.1003
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79282
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 3.5511
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 208770.2188 | 208770.2188
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 59.0533 | 59.0533
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 14.3538 | 14.3538
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 49.0609
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 59.0533 | 59.0533
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 28.3036
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 13.0025 | 13.0025
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.2616
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 40.6977
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 56.7375 | 56.7375
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 40.3933
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 13.1139 | 13.1139
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2018
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 56.7375 | 56.7375
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 13.7909 | 13.7909
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 56.7375 | 56.7375
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 13.7909 | 13.7909
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 56.7375 | 56.7375
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 13.1319 | 13.1319
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 56.7375 | 56.7375
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.025658 | 0.025658
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 13.1319 | 13.1319
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 44378.1094 | 44378.1094
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 59.0533 | 59.0533
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 13.0172 | 13.0172
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 59.0533 | 59.0533
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.026705 | 0.026705
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 13.0172 | 13.0172
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 46189.4609 | 46189.4609
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 5.2158 | 5.2158
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 253.7416 | 253.7416
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.6261 | 1.6261
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.2668 | 7.2668
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2968.1777 | 2968.1777
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 420.6892 | 420.6892
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.1038 | 1.1038
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.1838 | 2.1838
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.09 | 2.09
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039246 | 0.039246
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8314e-05 | 1.8314e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 5.268 | 5.268
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.9248 | 226.9248
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.4635 | 1.4635
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.1526 | 7.1526
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2911.8601 | 2911.8601
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 364.3715 | 364.3715
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0768 | 1.0768
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.3347 | 2.3347
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.036703 | 0.036703
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7191e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 79.3894 | 79.3894
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0049 | 436.0049
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 210.3333 | 210.3333
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.5114 | 6.5114
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3237.772 | 3237.772
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 690.2834 | 690.2834
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.3309 | 1.3309
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 26.688 | 26.688
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.593 | 2.593
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.066689 | 0.066689
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.6025e-05 | 2.6025e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 29.2416
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 3993.5029 | 3993.5029
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13137
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 995.916
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 89.6174 | 89.6174
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0164 | 303.0164
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 201.0013 | 201.0013
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2834 | 3.2834
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1361.6749 | 1361.6749
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1185.8135 | -1185.8135
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.00017478 | -0.00017478
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 705.8901 | 705.8901
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.0755 | 6.0755
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.53992 | 0.53992
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.4711e-05 | 8.4711e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 3993.5029 | 3993.5029
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 3993.5029 | 3993.5029
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 97.683 | 97.683
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 220.1776 | 220.1776
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 201.0013 | 201.0013
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.5059 | 2.5059
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 946.6248 | 946.6248
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1600.8638 | -1600.8638
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.33876 | -0.33876
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 846.463 | 846.463
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5583 | 4.5583
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65592 | 0.65592
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.00012274 | 0.00012274
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 210.8345 | 210.8345
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.030277 | 0.030277
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 58.3322 | 58.3322
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 72.6343 | 72.6343
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 531.3125 | 531.3125
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 210.3333 | 210.3333
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.8758 | 6.8758
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.4804 | 1.4804
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 20.5638 | 20.5638
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.3853 | 2.3853
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.076292 | 0.076292
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.009e-05 | 3.009e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 99.4872 | 99.4872
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 156.931 | 156.931
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 201.0013 | 201.0013
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 667.8068 | 667.8068
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1879.6818 | -1879.6818
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.55865 | -0.55865
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.8741 | 915.8741
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 1.806 | 1.806
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 129.6388 | 129.6388
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 0.59128 | 0.59128
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.2286 | 7.2286
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2728.4001 | 2728.4001
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 180.9117 | 180.9117
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0121 | 1.0121
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 0.99065 | 0.99065
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.0795 | 2.0795
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027512 | 0.027512
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3358e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 22.93 | 22.93
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 388.5145 | 388.5145
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 209.7123 | 209.7123
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 7.0222 | 7.0222
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3217.8464 | 3217.8464
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 670.3578 | 670.3578
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.2242 | 1.2242
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 7.7635 | 7.7635
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2141 | 2.2141
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.05537 | 0.05537
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3917e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 22.93 | 22.93
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 388.5145 | 388.5145
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 200.5742 | 200.5742
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 7.0222 | 7.0222
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3217.8464 | 3217.8464
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 670.3578 | 670.3578
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.2242 | 1.2242
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 7.7635 | 7.7635
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2141 | 2.2141
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.05537 | 0.05537
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3917e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 22.93 | 22.93
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 388.5145 | 388.5145
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 9.138 | 9.138
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 7.0222 | 7.0222
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3217.8464 | 3217.8464
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 670.3578 | 670.3578
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.2242 | 1.2242
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 7.7635 | 7.7635
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2141 | 2.2141
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.05537 | 0.05537
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3917e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 15.31 | 15.31
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 341.5981 | 341.5981
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 200.5742 | 200.5742
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.0637 | 7.0637
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3129.0718 | 3129.0718
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 581.5831 | 581.5831
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1737 | 1.1737
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 5.5574 | 5.5574
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1788 | 2.1788
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.049494 | 0.049494
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1939e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 15.31 | 15.31
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 341.5981 | 341.5981
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 14.2686 | 14.2686
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 7.0637 | 7.0637
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3129.0718 | 3129.0718
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 581.5831 | 581.5831
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1737 | 1.1737
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 5.5574 | 5.5574
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.1788 | 2.1788
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.049494 | 0.049494
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1939e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 15.31 | 15.31
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 341.5981 | 341.5981
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 186.3056 | 186.3056
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 7.0637 | 7.0637
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3129.0718 | 3129.0718
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 581.5831 | 581.5831
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1737 | 1.1737
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 5.5574 | 5.5574
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.1788 | 2.1788
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.049494 | 0.049494
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1939e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 29.2416
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 3993.5029 | 3993.5029
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13137
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 995.916
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 5.2158 | 5.2158
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 226.3482 | 226.3482
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.4635 | 1.4635
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.1551 | 7.1551
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2910.8601 | 2910.8601
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 363.3716 | 363.3716
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0765 | 1.0765
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.3139 | 2.3139
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1213 | 2.1213
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.03664 | 0.03664
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7168e-05 | 1.7168e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 5.268 | 5.268
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.9248 | 226.9248
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 184.8421 | 184.8421
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.1526 | 7.1526
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2911.8601 | 2911.8601
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 364.3715 | 364.3715
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0768 | 1.0768
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.3347 | 2.3347
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.036703 | 0.036703
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7191e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 105.4173 | 105.4173
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.030277 | 0.030277
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 58.3322 | 58.3322
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 5.2158 | 5.2158
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 499.93 | 499.93
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.16261 | 0.16261
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 8.0692 | 8.0692
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.3491 | 1.3491
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.4677 | 1.4677
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1462 | 2.1462
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067232 | 0.067232
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8584e-05 | 2.8584e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.0882 | 1.0882
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 74.5113 | 74.5113
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 25.1272 | 25.1272
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.0097 | 1.0097
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 311.9835 | 311.9835
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2235.5051 | -2235.5051
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.051307 | -0.051307
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 975.1884 | 975.1884
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1923 | 4.1923
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66367 | 0.66367
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00038054 | 0.00038054
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.4977 | 6.4977
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 68.9117 | 68.9117
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 185.8018 | 185.8018
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.94132 | 0.94132
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 288.9659 | 288.9659
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2258.5227 | -2258.5227
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.19041 | -0.19041
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 978.6756 | 978.6756
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1877 | 4.1877
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.65956 | 0.65956
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00041037 | 0.00041037
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.030277 | 0.030277
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 58.3322 | 58.3322
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 15.0098 | 15.0098
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 163.4898 | 163.4898
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 23.4067 | 23.4067
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9765 | 1.9765
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 691.1367 | 691.1367
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1856.3519 | -1856.3519
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.078986 | -0.078986
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 904.5494 | 904.5494
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3461 | 4.3461
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68196 | 0.68196
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016593 | 0.00016593
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 4.556 | 4.556
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 212.7618 | 212.7618
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 184.8421 | 184.8421
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.1639 | 7.1639
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2885.1326 | 2885.1326
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 337.6441 | 337.6441
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0666 | 1.0666
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.0766 | 2.0766
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1165 | 2.1165
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035269 | 0.035269
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6618e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 4.556 | 4.556
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 212.7618 | 212.7618
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 11.0019 | 11.0019
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.1639 | 7.1639
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2885.1326 | 2885.1326
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 337.6441 | 337.6441
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0666 | 1.0666
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.0766 | 2.0766
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1165 | 2.1165
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035269 | 0.035269
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6618e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 4.556 | 4.556
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 212.7618 | 212.7618
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 173.8402 | 173.8402
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.1639 | 7.1639
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2885.1326 | 2885.1326
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 337.6441 | 337.6441
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0666 | 1.0666
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.0766 | 2.0766
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1165 | 2.1165
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035269 | 0.035269
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6618e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 1.806 | 1.806
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 129.6388 | 129.6388
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 173.8402 | 173.8402
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.2286 | 7.2286
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2728.4001 | 2728.4001
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 180.9117 | 180.9117
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0121 | 1.0121
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 0.99065 | 0.99065
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.0795 | 2.0795
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027512 | 0.027512
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3358e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 1.806 | 1.806
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 129.6388 | 129.6388
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 4.6561 | 4.6561
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.2286 | 7.2286
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2728.4001 | 2728.4001
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 180.9117 | 180.9117
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0121 | 1.0121
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 0.99065 | 0.99065
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.0795 | 2.0795
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027512 | 0.027512
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3358e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.7706 | 1.7706
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 105.5917 | 105.5917
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 15.658 | 15.658
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.3697 | 1.3697
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 442.7386 | 442.7386
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2104.75 | -2104.75
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.020688 | -0.020688
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 954.3304 | 954.3304
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2223 | 4.2223
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68046 | 0.68046
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00026639 | 0.00026639
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.084 | 6.084
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 99.9881 | 99.9881
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 185.8018 | 185.8018
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3065 | 1.3065
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 419.4251 | 419.4251
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2128.0635 | -2128.0635
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.12162 | -0.12162
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 958.6367 | 958.6367
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2142 | 4.2142
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.67859 | 0.67859
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00028234 | 0.00028234
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.2567 | 5.2567
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 147.4578 | 147.4578
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 185.8018 | 185.8018
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8159 | 1.8159
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 621.2406 | 621.2406
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1926.2479 | -1926.2479
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.012914 | -0.012914
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 919.4474 | 919.4474
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3028 | 4.3028
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68481 | 0.68481
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018544 | 0.00018544
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 105.4173 | 105.4173
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.030277 | 0.030277
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 58.3322 | 58.3322
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.4265 | 45.4265
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 185.8018 | 185.8018
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64421 | 0.64421
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.1984 | 190.1984
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.2903 | -2357.2903
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061047 | -0.061047
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0576 | 990.0576
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63579 | 0.63579
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059097 | 0.00059097
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3251 | 7.3251
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5034 | 45.5034
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 185.8018 | 185.8018
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64492 | 0.64492
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1232 | 191.1232
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3652 | -2356.3652
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.2496 | -0.2496
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3243 | 990.3243
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63623 | 0.63623
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059026 | 0.00059026
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 4.4667 | 4.4667
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 212.0916 | 212.0916
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 11.0019 | 11.0019
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.1708 | 7.1708
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2884.1326 | 2884.1326
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 336.6441 | 336.6441
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0665 | 1.0665
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.0381 | 2.0381
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1138 | 2.1138
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.035189 | 0.035189
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6592e-05 | 1.6592e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 4.4667 | 4.4667
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 120.0192 | 120.0192
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 11.0019 | 11.0019
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5278 | 1.5278
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 503.9983 | 503.9983
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2043.4902 | -2043.4902
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.055655 | -0.055655
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 943.2499 | 943.2499
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2437 | 4.2437
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68431 | 0.68431
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00023217 | 0.00023217
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.6704 | 5.6704
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 114.4093 | 114.4093
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 185.8018 | 185.8018
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.4667 | 1.4667
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 480.3049 | 480.3049
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2067.1836 | -2067.1836
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.086331 | -0.086331
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 947.777 | 947.777
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.2342 | 4.2342
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68323 | 0.68323
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00024454 | 0.00024454
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 22.4804 | 22.4804
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 205.5711 | 205.5711
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 9.138 | 9.138
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.3824 | 2.3824
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 877.7553 | 877.7553
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1669.7333 | -1669.7333
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.031313 | -0.031313
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 858.5145 | 858.5145
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5225 | 4.5225
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.66051 | 0.66051
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012995 | 0.00012995
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 1.806 | 1.806
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 129.6388 | 129.6388
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 168.5928 | 168.5928
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.2286 | 7.2286
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2728.4001 | 2728.4001
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 180.9117 | 180.9117
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0121 | 1.0121
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 0.99065 | 0.99065
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.0795 | 2.0795
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027512 | 0.027512
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3358e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 89.6174 | 89.6174
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 303.0413 | 303.0413
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 200.5 | 200.5
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.6815 | 5.6815
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2743.5149 | 2743.5149
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 196.0263 | 196.0263
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 48.552 | 48.552
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 6.0727 | 6.0727
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.073613 | 0.073613
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 1.9902e-05 | 1.9902e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.11 | 1.11
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 102.5497 | 102.5497
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 168.5928 | 168.5928
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.2626 | 7.2626
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2656.6035 | 2656.6035
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 109.1149 | 109.1149
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.98979 | 0.98979
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.65757 | 0.65757
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2185 | 4.2185
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025078 | 0.025078
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2368e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.11 | 1.11
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 102.5497 | 102.5497
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 9.4692 | 9.4692
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.2626 | 7.2626
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2656.6035 | 2656.6035
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 109.1149 | 109.1149
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.98979 | 0.98979
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.65757 | 0.65757
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2185 | 4.2185
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025078 | 0.025078
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2368e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.11 | 1.11
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 102.5497 | 102.5497
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 159.1236 | 159.1236
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.2626 | 7.2626
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2656.6035 | 2656.6035
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 109.1149 | 109.1149
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.98979 | 0.98979
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.65757 | 0.65757
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2185 | 4.2185
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025078 | 0.025078
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2368e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.331 | 0.331
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 71.3726 | 71.3726
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 159.1236 | 159.1236
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.344 | 7.344
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2494.166 | 2494.166
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -53.3225 | -53.3225
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.94236 | 0.94236
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.22256 | 0.22256
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1904 | 4.1904
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022102 | 0.022102
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1311e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.331 | 0.331
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 71.3726 | 71.3726
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 6.5698 | 6.5698
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.4052 | 7.4052
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2515.2473 | 2515.2473
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -32.2414 | -32.2414
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.95141 | 0.95141
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.22044 | 0.22044
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1904 | 4.1904
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022102 | 0.022102
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1311e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.331 | 0.331
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 71.3726 | 71.3726
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 153.1451 | 153.1451
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.344 | 7.344
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2494.166 | 2494.166
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -53.3225 | -53.3225
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.94236 | 0.94236
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.22256 | 0.22256
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1904 | 4.1904
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022102 | 0.022102
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1311e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 185.2484 | 185.2484
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 99.0735 | 99.0735
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 198.527 | 198.527
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 201.0013 | 201.0013
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.304 | 2.304
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 849.2836 | 849.2836
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1698.2048 | -1698.2048
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.41908 | -0.41908
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 872.5988 | 872.5988
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4436 | 4.4436
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.67205 | 0.67205
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013675 | 0.00013675
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 39.3118
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 7987.0059 | 7987.0059
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.56313
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 164.8359
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2382.6526
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.17681
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 992.599
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1779
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62836
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006607
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 29.2957
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 7987.0059 | 7987.0059
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20507
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 995.9927
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 22.4804 | 22.4804
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 387.712 | 387.712
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 9.138 | 9.138
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 7.0295 | 7.0295
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3216.8464 | 3216.8464
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 669.3579 | 669.3579
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.2233 | 1.2233
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 7.6165 | 7.6165
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.211 | 2.211
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055236 | 0.055236
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3883e-05 | 2.3883e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 15.0098 | 15.0098
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 340.8437 | 340.8437
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 14.2686 | 14.2686
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 7.071 | 7.071
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3128.0718 | 3128.0718
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 580.5831 | 580.5831
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1732 | 1.1732
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 5.4527 | 5.4527
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.1759 | 2.1759
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.04938 | 0.04938
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1909e-05 | 2.1909e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 1.7706 | 1.7706
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 128.9974 | 128.9974
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 4.6561 | 4.6561
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.2351 | 7.2351
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2727.4004 | 2727.4004
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 179.9118 | 179.9118
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0121 | 1.0121
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 0.97253 | 0.97253
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.0769 | 2.0769
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027444 | 0.027444
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3335e-05 | 1.3335e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.0882 | 1.0882
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 101.987 | 101.987
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 9.4692 | 9.4692
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.2689 | 7.2689
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2655.6035 | 2655.6035
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 108.115 | 108.115
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98974 | 0.98974
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.64553 | 0.64553
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2178 | 4.2178
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.025019 | 0.025019
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2348e-05 | 1.2348e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.32451 | 0.32451
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 70.9113 | 70.9113
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 6.5698 | 6.5698
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.4109 | 7.4109
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2514.2473 | 2514.2473
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -33.2413 | -33.2413
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.95134 | 0.95134
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.2164 | 0.2164
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1902 | 4.1902
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022062 | 0.022062
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1296e-05 | 1.1296e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 497.3904 | 497.3904
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.22489 | 0.22489
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6341 | 9.6341
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3722 | 1.3722
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049218 | 0.049218
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1278 | 2.1278
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066575 | 0.066575
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8475e-05 | 2.8475e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 99.4872 | 99.4872
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 156.931 | 156.931
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 105.4173 | 105.4173
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 667.8069 | 667.8069
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1879.6816 | -1879.6816
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.55865 | -0.55865
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.874 | 915.874
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 71.35 | 71.35
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 530.7554 | 530.7554
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 209.9458 | 209.9458
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.8837 | 6.8837
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.4766 | 1.4766
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 20.1983 | 20.1983
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.3808 | 2.3808
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.076115 | 0.076115
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.0061e-05 | 3.0061e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 99.4872 | 99.4872
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 156.931 | 156.931
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 9.8333 | 9.8333
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 667.8068 | 667.8068
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1879.6818 | -1879.6818
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.55865 | -0.55865
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.8741 | 915.8741
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9114 | 6.9114
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4516 | 46.4516
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 185.8018 | 185.8018
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65735 | 0.65735
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0504 | 195.0504
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.4382 | -2352.4382
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24179 | -0.24179
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9033 | 989.9033
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63733 | 0.63733
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058056 | 0.00058056
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 5.268 | 5.268
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.9248 | 226.9248
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 186.3056 | 186.3056
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.1526 | 7.1526
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2911.8601 | 2911.8601
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 364.3715 | 364.3715
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0768 | 1.0768
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.3347 | 2.3347
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.036703 | 0.036703
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7191e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.0996 | 52.0996
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 31.9219 | 31.9219
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73086 | 0.73086
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.0808 | 218.0808
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.4077 | -2329.4077
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090351 | -0.0090351
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.0851 | 987.0851
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.6433 | 0.6433
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00052778 | 0.00052778
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.32451 | 0.32451
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.0603 | 52.0603
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 31.697 | 31.697
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73035 | 0.73035
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9292 | 217.9292
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5593 | -2329.5593
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.033854 | -0.033854
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1099 | 987.1099
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64327 | 0.64327
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052812 | 0.00052812
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 153.3265 | 153.3265
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.4677 | 7.4677
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2364.5938 | 2364.5938
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -182.8949 | -182.8949
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.90857 | 0.90857
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.073966 | 0.073966
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.331 | 0.331
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 71.3726 | 71.3726
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 5.9785 | 5.9785
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.344 | 7.344
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2494.166 | 2494.166
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -53.3225 | -53.3225
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.94236 | 0.94236
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.22256 | 0.22256
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1904 | 4.1904
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022102 | 0.022102
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1311e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.22489 | 0.22489
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 99.4872 | 99.4872
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 156.931 | 156.931
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 105.4173 | 105.4173
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 667.8069 | 667.8069
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1879.6816 | -1879.6816
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.55865 | -0.55865
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.874 | 915.874
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 99.4872 | 99.4872
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 156.931 | 156.931
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 4.9558 | 4.9558
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 667.8068 | 667.8068
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1879.6818 | -1879.6818
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.55865 | -0.55865
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.8741 | 915.8741
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 99.4872 | 99.4872
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 156.931 | 156.931
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 105.4173 | 105.4173
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 667.8069 | 667.8069
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1879.6816 | -1879.6816
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.55865 | -0.55865
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.874 | 915.874
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 99.4872 | 99.4872
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 156.931 | 156.931
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 210.8345 | 210.8345
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 667.8068 | 667.8068
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1879.6818 | -1879.6818
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.55865 | -0.55865
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.8741 | 915.8741
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 99.4872 | 99.4872
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 156.931 | 156.931
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 105.4173 | 105.4173
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 667.8069 | 667.8069
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1879.6816 | -1879.6816
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.55865 | -0.55865
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.874 | 915.874
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 99.4872 | 99.4872
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.1051 | 152.1051
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8528 | 1.8528
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.57433 | -0.57433
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 920.3876 | 920.3876
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.2859 | 4.2859
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.69035 | 0.69035
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018164 | 0.00018164
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 99.4872 | 99.4872
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.1051 | 152.1051
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8528 | 1.8528
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.57433 | -0.57433
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 920.3876 | 920.3876
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.2859 | 4.2859
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.69035 | 0.69035
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018164 | 0.00018164
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 79.3894 | 79.3894
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0035 | 460.0035
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 205.3774 | 205.3774
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.5974 | 6.5974
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3299.7864 | 3299.7864
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 752.2979 | 752.2979
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.3738 | 1.3738
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 25.4746 | 25.4746
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.516 | 2.516
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.06903 | 0.06903
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7075e-05 | 2.7075e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 105.4173 | 105.4173
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.030277 | 0.030277
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 58.3322 | 58.3322
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 105.4173 | 105.4173
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.030277 | 0.030277
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 58.3322 | 58.3322
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.030277 | 0.030277
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 58.3322 | 58.3322
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 29.2416
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 7987.0059 | 7987.0059
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13137
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 995.916
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 71.35 | 71.35
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 530.7554 | 530.7554
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 210.3333 | 210.3333
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.8837 | 6.8837
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.4766 | 1.4766
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 20.1983 | 20.1983
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.3808 | 2.3808
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.076115 | 0.076115
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.0061e-05 | 3.0061e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 98.6599 | 98.6599
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 222.1428 | 222.1428
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 201.0013 | 201.0013
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5239 | 2.5239
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 955.6248 | 955.6248
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1591.8638 | -1591.8638
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.33672 | -0.33672
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 844.043 | 844.043
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5698 | 4.5698
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65433 | 0.65433
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00012164 | 0.00012164
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 80.9772 | 80.9772
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5055 | 411.5055
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 205.3774 | 205.3774
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.4049 | 6.4049
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3169.3186 | 3169.3186
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 621.8301 | 621.8301
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.2871 | 1.2871
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 28.7492 | 28.7492
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.7285 | 2.7285
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.064792 | 0.064792
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.4944e-05 | 2.4944e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 99.4872 | 99.4872
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 156.931 | 156.931
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 4.8774 | 4.8774
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.9012 | 1.9012
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 667.8068 | 667.8068
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1879.6818 | -1879.6818
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.55865 | -0.55865
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.8741 | 915.8741
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2983 | 4.2983
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.68947 | 0.68947
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017561
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 87.8602 | 87.8602
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 339.0002 | 339.0002
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 200.5 | 200.5
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.9919 | 5.9919
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2923.342 | 2923.342
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 375.8534 | 375.8534
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1271 | 1.1271
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 39.1054 | 39.1054
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 3.8917 | 3.8917
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.064882 | 0.064882
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1633e-05 | 2.1633e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 89.6174 | 89.6174
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0413 | 303.0413
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 200.5 | 200.5
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.6815 | 5.6815
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2743.5149 | 2743.5149
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 196.0263 | 196.0263
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 48.552 | 48.552
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.0727 | 6.0727
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.073613 | 0.073613
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 1.9902e-05 | 1.9902e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 80.9772 | 80.9772
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.105 | 434.105
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 200.5 | 200.5
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.4924 | 6.4924
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3230.1714 | 3230.1714
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 682.6827 | 682.6827
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3295 | 1.3295
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 27.3874 | 27.3874
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.6149 | 2.6149
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.066716 | 0.066716
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.5947e-05 | 2.5947e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 72.8343 | 72.8343
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 531.3991 | 531.3991
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 210.3333 | 210.3333
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.8746 | 6.8746
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3484.0369 | 3484.0369
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 936.5485 | 936.5485
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.481 | 1.481
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 20.6207 | 20.6207
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.386 | 2.386
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.076319 | 0.076319
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0095e-05 | 3.0095e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 97.683 | 97.683
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 220.1776 | 220.1776
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 201.0013 | 201.0013
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.5059 | 2.5059
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 946.6248 | 946.6248
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1600.8638 | -1600.8638
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.33876 | -0.33876
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 846.463 | 846.463
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5583 | 4.5583
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65592 | 0.65592
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00012274 | 0.00012274
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 37.8785 | 37.8785
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15181.7607
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15162.0674
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 6.9687
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 159534.5781 | 159534.5781
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 176211.1719 | 176211.1719
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 40.05
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 10.41
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [24] - LPH-4 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [24] - LPH-4 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3

## ELINK (2)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_75%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 32.18
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 59.56
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 302.6 | 302.6
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 877.2 | 877.2
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.27 | 5.27
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.8281 | 153.8281
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.7867 | 99.7867
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.48096 | 0.48096
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 8.8073 | 8.8073
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 4.1063e-06 | 4.1063e-06
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 140.5461 | 140.5461
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 77.3859 | 77.3859
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 2.0986 | 2.0986
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 20.8544 | 20.8544
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 4.3295 | 4.3295
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 21.7056 | 21.7056
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 4.3295 | 4.3295
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 21.7056 | 21.7056
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 2.0986 | 2.0986
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 20.8544 | 20.8544
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 203.7692 | 203.7692
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 228.1 | 228.1
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 40.05
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 535 | 535
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 29.22
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 79.583 | 79.583
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 25.58 | 25.58
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 17.08 | 17.08
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.877 | 5.877
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.082 | 5.082
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 2.014 | 2.014
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.238 | 1.238
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.37 | 0.37
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 32.18
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 59.56
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~~4~~-5000~ | Plant Summary: Gross power | kW | 84949.1719 | 84949.1719
~~~7~~-5000~ | Plant Summary: Net power | kW | 76382.5781 | 76382.5781
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 8566.5879 | 8566.5879
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 8141.8418 | 8141.8418
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 424.7458 | 424.7458
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 35.2128 | 35.2128
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10223.5615 | 10223.5615
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.6618 | 31.6618
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11370.1719 | 11370.1719
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 241245.2969 | 241245.2969
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.6618 | 31.6618
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.6618 | 31.6618
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.6653 | 28.6653
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12558.7285 | 12558.7285
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 266463.3438 | 266463.3438
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 241245.2969 | 241245.2969
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.6618 | 31.6618
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 0.80861 | 0.80861
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.7565 | 0.7565
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 241245.2969 | 241245.2969
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 266463.3438 | 266463.3438
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 2118.3889 | 2118.3889
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 21524160 | 21524160
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 27664248 | 27664248
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 618.6989 | 618.6989
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 7034.7129 | 7034.7129
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 6.6254 | 6.6254
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 663.9607 | 663.9607
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 27664.248 | 27664.248
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 362.1801 | 362.1801
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 337297.7812 | 337297.7812
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 8299.2754 | 8299.2754
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 52.4356 | 52.4356
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 150.3115 | 150.3115
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.67928 | 0.67928
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 173040.9219 | 173040.9219
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.035451 | 0.035451
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.038 | 5.038
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 21524160 | 21524160
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 21524160 | 21524160
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 4202914.5 | 4202914.5
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 25727074 | 25727074
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 27664248 | 27664248
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 84949.1719 | 84949.1719
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 776.8948 | 776.8948
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 338.9996 | 338.9996
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 913.4019 | 913.4019
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 219.9757 | 219.9757
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 451.0894 | 451.0894
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 219.9757 | 219.9757
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 451.0894 | 451.0894
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 736.1543 | 736.1543
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 79.0789 | 79.0789
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 1095.5714 | 1095.5714
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 1095.5718 | 1095.5718
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 736.1543 | 736.1543
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 178.3932 | 178.3932
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 849.4917 | 849.4917
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 424.7458 | 424.7458
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 8141.8418 | 8141.8418
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 241245.2969 | 241245.2969
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 14.1686 | 14.1686
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 403332.0625 | 403332.0625
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 542398.875 | 542398.875
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 23560.2559 | 23560.2559
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 7491.4194 | 7491.4194
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 16869.459 | 16869.459
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 2069.4629 | 2069.4629
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 11401.7744 | 11401.7744
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 5108.3857 | 5108.3857
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 10812.9766 | 10812.9766
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 8920.5137 | 8920.5137
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 776.8948 | 776.8948
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 338.9996 | 338.9996
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 913.4019 | 913.4019
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 219.9757 | 219.9757
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 451.0894 | 451.0894
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 219.9757 | 219.9757
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 451.0894 | 451.0894
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 736.1543 | 736.1543
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 79.0789 | 79.0789
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 1095.5714 | 1095.5714
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 1095.5718 | 1095.5718
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 736.1543 | 736.1543
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 242.08 | 242.08
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 60.52 | 60.52
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 99.9299 | 99.9299
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 310.948 | 310.948
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2725.6003 | 2725.6003
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 877.2 | 877.2
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 310.948 | 310.948
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 65.91
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 2.9438
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.2498
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 17.1003
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0031714
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79282
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 139866.9531 | 139866.9531
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 91818.0156 | 91818.0156
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 22954.5039 | 22954.5039
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 11639.4473 | 11639.4473
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 13454.999 | 13454.999
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 2111.5203 | 2111.5203
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 2797.3391 | 2797.3391
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 404.327 | 404.327
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 943.4295 | 943.4295
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 96.9402 | 96.9402
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 178.753 | 178.753
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 139.7315 | 139.7315
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.12888 | 0.12888
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.46904 | 0.46904
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 57.2791 | 57.2791
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 1374.6976 | 1374.6976
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 241245.2969 | 241245.2969
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 266463.3438 | 266463.3438
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 572.7906 | 572.7906
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 204.1042 | 204.1042
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 3.7861 | 3.7861
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.22539 | 0.22539
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.59107 | 0.59107
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 5.1026 | 5.1026
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.5308 | 1.5308
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 3.5718 | 3.5718
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 2.9438
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 17.1003
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.27 | 5.27
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.8281 | 153.8281
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.3108 | 5.3108
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 150.0223 | 150.0223
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 632.2855 | 632.2855
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 279.323 | 279.323
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 5.8188 | 5.8188
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 253.3819 | 253.3819
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2965.3818 | 2965.3818
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.2329 | 1.2329
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 16.7451 | 16.7451
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 164.2944 | 164.2944
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 694.7332 | 694.7332
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 38.2623 | 38.2623
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 318.8181 | 318.8181
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.999 | 23.999
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 88.5249 | 88.5249
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0032 | 460.0032
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 310.3009 | 310.3009
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3286.5439 | 3286.5439
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 88.5249 | 88.5249
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0042 | 436.0042
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 318.0616 | 318.0616
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3222.7476 | 3222.7476
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 7.7607 | 7.7607
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 671.9551 | 671.9551
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5994 | 22.5994
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 90.2954 | 90.2954
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.104 | 434.104
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 302.6 | 302.6
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3214.6116 | 3214.6116
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 90.2954 | 90.2954
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5047 | 411.5047
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 310.3009 | 310.3009
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3151.5093 | 3151.5093
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 7.7009 | 7.7009
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 671.9551 | 671.9551
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 24.3943 | 24.3943
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 149.4225 | 149.4225
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 25.3974 | 25.3974
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 25.3974 | 25.3974
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 24.3943 | 24.3943
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 303.3565 | 303.3565
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 108.9236 | 108.9236
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 973.8266 | 973.8266
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 226.0548 | 226.0548
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 303.3565 | 303.3565
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 99.9299 | 99.9299
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 303
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1360.303 | 1360.303
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 403.3392 | 403.3392
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 3.5718 | 3.5718
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 526.1609 | 526.1609
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 282.9344 | 282.9344
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 56.5243
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1252.0874 | 1252.0874
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 32567.1992 | 32567.1992
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 32567.1992 | 32567.1992
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 244.254 | 244.254
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 8.9937 | 8.9937
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.7867 | 99.7867
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 338.9996 | 338.9996
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 144.8047 | 144.8047
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 502057.2188 | 502057.2188
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 403.339 | 403.339
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 3.5718 | 3.5718
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 3.5642 | 3.5642
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0076183 | 0.0076183
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3723.5483 | 3723.5483
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 11721.3564 | 11721.3564
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9419 | 7.9419
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 25.0002 | 25.0002
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 149.4688 | 149.4688
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2264 | 1.2264
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 432.9519 | 432.9519
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 432.9519 | 432.9519
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 428.6224 | 428.6224
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 21.7056 | 21.7056
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 4.3295 | 4.3295
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 473.6438 | 473.6438
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 95.9992 | 95.9992
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 451.0894 | 451.0894
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 432.9519 | 432.9519
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 95.9792 | 95.9792
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 18.1374 | 18.1374
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 454.5995 | 454.5995
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 880.7316 | 880.7316
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 880.7316 | 880.7316
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 871.9243 | 871.9243
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 140.5461 | 140.5461
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1388 | 80.1388
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 8.8073 | 8.8073
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 959.0719 | 959.0719
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.441 | 96.441
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 913.4019 | 913.4019
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 880.7316 | 880.7316
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.4232 | 96.4232
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 32.6702 | 32.6702
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 924.7681 | 924.7681
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 209.8643 | 209.8643
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 209.8643 | 209.8643
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 207.7656 | 207.7656
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 20.8544 | 20.8544
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 2.0986 | 2.0986
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 230.9745 | 230.9745
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.4263 | 95.4263
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 219.9757 | 219.9757
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 209.8643 | 209.8643
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.4034 | 95.4034
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 10.1114 | 10.1114
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 220.3575 | 220.3575
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 432.9519 | 432.9519
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 432.9519 | 432.9519
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 428.6224 | 428.6224
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 21.7056 | 21.7056
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 4.3295 | 4.3295
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 473.6438 | 473.6438
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 95.9992 | 95.9992
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 451.0894 | 451.0894
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 432.9519 | 432.9519
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 95.9792 | 95.9792
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 18.1374 | 18.1374
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 454.5995 | 454.5995
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 209.8643 | 209.8643
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 209.8643 | 209.8643
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 207.7656 | 207.7656
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 20.8544 | 20.8544
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 2.0986 | 2.0986
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 230.9745 | 230.9745
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.4263 | 95.4263
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 219.9757 | 219.9757
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 209.8643 | 209.8643
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.4034 | 95.4034
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 10.1114 | 10.1114
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 220.3575 | 220.3575
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.36275 | 0.36275
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 73.5249 | 73.5249
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 8133.1494 | 8133.1494
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 6908.4692 | 6908.4692
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 1224.6805 | 1224.6805
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 25.0644 | 25.0644
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.2137 | 1.2137
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 105.1123 | 105.1123
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 10296.0127 | 10296.0127
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 9051.6143 | 9051.6143
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 1244.3993 | 1244.3993
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 31.5876 | 31.5876
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 1.9745 | 1.9745
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 119.8065 | 119.8065
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 4820.6636 | 4820.6636
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 4514.3022 | 4514.3022
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 306.3611 | 306.3611
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.6921 | 14.6921
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 4.9824 | 4.9824
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 151.7031 | 151.7031
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 10672.3506 | 10672.3506
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 9578.3809 | 9578.3809
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 546.8643 | 546.8643
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 547.1055 | 547.1055
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 32.1848 | 32.1848
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 1.7031 | 1.7031
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 16.7451 | 16.7451
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 203.5792 | 203.5792
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 16953.6602 | 16953.6602
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 13003.7227 | 13003.7227
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 2102.4268 | 2102.4268
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 1847.5114 | 1847.5114
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 46.0335 | 46.0335
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 25.0784 | 25.0784
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 224.1231 | 224.1231
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 9242.5488 | 9242.5488
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 7414.2236 | 7414.2236
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1584.2157 | 1584.2157
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 244.1092 | 244.1092
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 24.2367 | 24.2367
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.8912 | -3.8912
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7598 | 15181.7598
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 57.2791 | 57.2791
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 241245.2969 | 241245.2969
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 266463.3438 | 266463.3438
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 2118.3889 | 2118.3889
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15162.0674
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15181.7607
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16839.0098
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 10.41
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 40.05
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 6.9687
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 32.1803
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 89.2993 | 89.2993
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.040383 | 0.040383
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 32.1803
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 85.7974 | 85.7974
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.0388 | 0.0388
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 32.1803
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 89.2993 | 89.2993
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.040383 | 0.040383
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 32.1803
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 85.7974 | 85.7974
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.0388 | 0.0388
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.3099
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 708.8832 | 708.8832
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 687.6167 | 687.6167
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 736.1543 | 736.1543
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 5922.8818 | 5922.8818
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 5922.8818 | 5922.8818
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 761.8742 | 761.8742
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.3084 | 96.3084
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 736.1543 | 736.1543
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 708.8832 | 708.8832
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.2955 | 96.2955
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 27.2711 | 27.2711
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 733.6503 | 733.6503
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.3099
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 708.8832 | 708.8832
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 687.6167 | 687.6167
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 736.1543 | 736.1543
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 5922.8818 | 5922.8818
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 5922.8818 | 5922.8818
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 761.8742 | 761.8742
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.3084 | 96.3084
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 736.1543 | 736.1543
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 708.8832 | 708.8832
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.2955 | 96.2955
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 27.2711 | 27.2711
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 733.6503 | 733.6503
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.3084 | 96.3084
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 71.2931 | 71.2931
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.9218 | 6.9218
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.9218 | 6.9218
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 74.9993 | 74.9993
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 74.5636 | 74.5636
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 72.3267 | 72.3267
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 79.0789 | 79.0789
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 279.323 | 279.323
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.429 | 45.429
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.2088 | 190.2088
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 279.323 | 279.323
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3792 | 7.3792
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5065 | 45.5065
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.141 | 191.141
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 81.8418 | 81.8418
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 94.31 | 94.31
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 79.0789 | 79.0789
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 74.5636 | 74.5636
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 94.2901 | 94.2901
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 4.5153 | 4.5153
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 77.1687 | 77.1687
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1180.5334 | 1180.5334
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 107.3929 | 107.3929
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 107.3929 | 107.3929
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 1056.9429 | 1056.9429
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 1025.2346 | 1025.2346
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 1095.5714 | 1095.5714
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 159.409 | 159.409
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 159.409 | 159.409
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 110.8402 | 110.8402
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 142.1197 | 142.1197
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 605.1828 | 605.1828
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 1522.7216 | 1522.7216
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.678 | 96.678
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 1095.5714 | 1095.5714
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 1056.9429 | 1056.9429
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.4741 | 96.4741
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 38.6285 | 38.6285
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 1469.0322 | 1469.0322
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1180.5334 | 1180.5334
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 107.3929 | 107.3929
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 107.3929 | 107.3929
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 1056.9431 | 1056.9431
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 1025.2349 | 1025.2349
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 1095.5717 | 1095.5717
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 159.4091 | 159.4091
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 159.4091 | 159.4091
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 110.8402 | 110.8402
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 142.1197 | 142.1197
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 605.1828 | 605.1828
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 1522.7219 | 1522.7219
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.678 | 96.678
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 1095.5717 | 1095.5717
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 1056.9431 | 1056.9431
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.4741 | 96.4741
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 38.6285 | 38.6285
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 1469.0326 | 1469.0326
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 0.80861 | 0.80861
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 278.5143 | 278.5143
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 279.323 | 279.323
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.429 | 45.429
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.2088 | 190.2088
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0068832 | 0.0068832
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99312 | 0.99312
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 9.2275e-10 | 9.2275e-10
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 17659.7168 | 17659.7168
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 8648.8496 | 8648.8496
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 9010.8672 | 9010.8672
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 8605.8203 | 8605.8203
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 8966.0371 | 8966.0371
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 87.8602 | 87.8602
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.058188 | 0.058188
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 0.99999 | 0.99999
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.30821 | 0.30821
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.4325 | 1.4325
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.50157 | 0.50157
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 3.9949 | 3.9949
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.3349 | 0.3349
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 6.6332 | 6.6332
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.099647 | 0.099647
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 4.5174 | 4.5174
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.03949 | 0.03949
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 2.0011 | 2.0011
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.024275 | 0.024275
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 4.05 | 4.05
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0072549 | 0.0072549
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 3.0657 | 3.0657
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 1.0892 | 1.0892
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 758.4005 | 758.4005
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 306.62 | 306.62
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.95408 | 0.95408
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7401 | 10.7401
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.048497 | 0.048497
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.9515 | 0.9515
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00038762 | 0.00038762
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99854 | 0.99854
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010696 | 0.0010696
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95468 | 0.95468
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.045318 | 0.045318
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92118 | 0.92118
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.078817 | 0.078817
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99602 | 0.99602
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0039756 | 0.0039756
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.9415 | 0.9415
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.058502 | 0.058502
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96868 | 0.96868
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0037952 | 0.0037952
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.027525 | 0.027525
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94249 | 0.94249
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.05751 | 0.05751
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.95797 | 0.95797
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.042032 | 0.042032
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 9.2275e-10 | 9.2275e-10
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50194 | 0.50194
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49806 | 0.49806
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 149.4019 | 149.4019
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 57.0002
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.9678
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 1971.0919 | 1971.0919
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 2.9438
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.2498
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 17.1003
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 65.91
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79282
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0031714
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.829
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 93.8988
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 32.8529
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0076183 | 0.0076183
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9419 | 7.9419
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 25.0002 | 25.0002
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 2.9438
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 17.1003
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 318.0616 | 318.0616
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 88.5249 | 88.5249
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3222.7476 | 3222.7476
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0042 | 436.0042
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 318.0616 | 318.0616
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 81.2155 | 81.2155
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 535 | 535
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3484.0393 | 3484.0393
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 403.3392 | 403.3392
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 3.5718 | 3.5718
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 877.2 | 877.2
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 721.3113 | 721.3113
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 23085.5762 | 23085.5762
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 7.3094 | 7.3094
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 302.6 | 302.6
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 97.9705 | 97.9705
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2885.6704 | 2885.6704
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 338.9995 | 338.9995
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 302.6 | 302.6
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 90.2954 | 90.2954
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3214.6116 | 3214.6116
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 403.3392 | 403.3392
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 3.5718 | 3.5718
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 721.3112 | 721.3112
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 526.1608 | 526.1608
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 27649.7539 | 27649.7539
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 207.3731 | 207.3731
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 7.6751 | 7.6751
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 108.9236 | 108.9236
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 226.0548 | 226.0548
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 973.8266 | 973.8266
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 303.3565 | 303.3565
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 108.9236 | 108.9236
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 226.0548 | 226.0548
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 973.8266 | 973.8266
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.2 | 0.2
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 81.2155 | 81.2155
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 534.9996 | 534.9996
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3484.0393 | 3484.0393
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 318.0616 | 318.0616
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 81.0155 | 81.0155
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 534.9143 | 534.9143
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3484.0393 | 3484.0393
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 110.8402 | 110.8402
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.3365 | 152.3365
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 110.8402 | 110.8402
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.3365 | 152.3365
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 110.8402 | 110.8402
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 157.7357 | 157.7357
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 671.955 | 671.955
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 159.409 | 159.409
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 110.8402 | 110.8402
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 157.7357 | 157.7357
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 671.955 | 671.955
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 110.8402 | 110.8402
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 157.7357 | 157.7357
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 671.955 | 671.955
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 159.4091 | 159.4091
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 110.8402 | 110.8402
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 157.7357 | 157.7357
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 671.955 | 671.955
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 159.409 | 159.409
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 159.4091 | 159.4091
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 39.3118
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 164.8358
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 11845.7637 | 11845.7637
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 29.2416
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 122.5732
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 11845.7637 | 11845.7637
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 137691.0469 | 137691.0469
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 84949.1719 | 84949.1719
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.5098 | 98.5098
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 133.7949 | 133.7949
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 44.5983 | 44.5983
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 99.1074 | 99.1074
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.5301 | 98.5301
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 83.5621 | 83.5621
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 534.3031 | 534.3031
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 317.5981 | 317.5981
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 89196.625 | 89196.625
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.5301 | 98.5301
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 84949.1719 | 84949.1719
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 86234.2422 | 86234.2422
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.5098 | 98.5098
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1285.0681 | 1285.0681
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 1127.7323 | 1127.7323
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 157.3358 | 157.3358
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 10.1967 | 10.1967
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.7668 | 4.7668
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 153301.8281 | 153301.8281
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 9.6167 | 9.6167
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.3817 | 3.3817
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 141649.9688 | 141649.9688
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 19.8134 | 19.8134
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.7668 | 4.7668
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 294951.8125 | 294951.8125
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 22.2876 | 22.2876
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.7201 | 5.7201
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 17720680 | 17720680
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 21524160 | 21524160
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 79.583 | 79.583
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 79.583 | 79.583
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 534.3031 | 534.3031
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 317.5981 | 317.5981
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3484.0393 | 3484.0393
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 317.3646 | 317.3646
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 79.583 | 79.583
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3484.0393 | 3484.0393
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 25.58 | 25.58
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3216.1196 | 3216.1196
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 25.58 | 25.58
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 389.8145 | 389.8145
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 317.3646 | 317.3646
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3216.1196 | 3216.1196
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 10.1606 | 10.1606
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.009856 | 0.009856
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1111 | 3.1111
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 73.3373 | 73.3373
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 75.504 | 75.504
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 75.504 | 75.504
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 23619.3027 | 23619.3027
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 23560.2559 | 23560.2559
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 59.0482 | 59.0482
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 25.58 | 25.58
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 25.58 | 25.58
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 389.8145 | 389.8145
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 302.9824 | 302.9824
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3216.1196 | 3216.1196
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 302.9824 | 302.9824
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 25.58 | 25.58
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3216.1196 | 3216.1196
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 17.08 | 17.08
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3126.8857 | 3126.8857
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 17.08 | 17.08
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 342.3405 | 342.3405
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 302.9824 | 302.9824
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3126.8857 | 3126.8857
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 13.5446 | 13.5446
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.026752 | 0.026752
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4977 | 1.4977
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 77.9852 | 77.9852
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 78.3809 | 78.3809
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 78.3809 | 78.3809
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 7510.1943 | 7510.1943
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 7491.4194 | 7491.4194
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 18.7755 | 18.7755
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 17.08 | 17.08
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 17.08 | 17.08
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 342.3405 | 342.3405
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 279.1023 | 279.1023
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3126.8857 | 3126.8857
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 279.1023 | 279.1023
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 17.08 | 17.08
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3126.8857 | 3126.8857
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 5.877 | 5.877
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2908.7532 | 2908.7532
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 5.877 | 5.877
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.651 | 226.651
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 279.1023 | 279.1023
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2908.7532 | 2908.7532
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 29.6662 | 29.6662
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.035637 | 0.035637
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9062 | 2.9062
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 82.4998 | 82.4998
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 83.8321 | 83.8321
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 83.8321 | 83.8321
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 16911.7402 | 16911.7402
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 16869.459 | 16869.459
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 42.2793 | 42.2793
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 5.877 | 5.877
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 5.877 | 5.877
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.651 | 226.651
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 277.9927 | 277.9927
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2908.7532 | 2908.7532
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 277.9927 | 277.9927
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 5.877 | 5.877
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2908.7532 | 2908.7532
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 5.082 | 5.082
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2881.887 | 2881.887
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 5.082 | 5.082
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 212.3696 | 212.3696
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 277.9927 | 277.9927
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2881.887 | 2881.887
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 33.2176 | 33.2176
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.093305 | 0.093305
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1564 | 1.1564
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 83.6006 | 83.6006
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 83.6009 | 83.6009
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 83.6009 | 83.6009
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 2074.6494 | 2074.6494
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 2069.4629 | 2069.4629
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 5.1866 | 5.1866
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 5.082 | 5.082
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 5.082 | 5.082
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 212.3696 | 212.3696
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 261.7295 | 261.7295
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2881.887 | 2881.887
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 261.7295 | 261.7295
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 5.082 | 5.082
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2881.887 | 2881.887
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 2.014 | 2.014
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2724.6687 | 2724.6687
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 2.014 | 2.014
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 128.8454 | 128.8454
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 261.7295 | 261.7295
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2724.6687 | 2724.6687
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 65.5072 | 65.5072
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.10016 | 0.10016
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5233 | 2.5233
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.5746 | 85.5746
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 86.4603 | 86.4603
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 86.4603 | 86.4603
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 11430.3506 | 11430.3506
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 11401.7744 | 11401.7744
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 28.5758 | 28.5758
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 2.014 | 2.014
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 2.014 | 2.014
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 128.8454 | 128.8454
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 253.5319 | 253.5319
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2724.6687 | 2724.6687
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 253.5319 | 253.5319
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 2.014 | 2.014
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2724.6687 | 2724.6687
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.238 | 1.238
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2651.9521 | 2651.9521
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.238 | 1.238
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 105.6857 | 105.6857
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 253.5319 | 253.5319
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2651.9521 | 2651.9521
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 96.2876 | 96.2876
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.22306 | 0.22306
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.6268 | 1.6268
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 85.9563 | 85.9563
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 85.9564 | 85.9564
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 85.9564 | 85.9564
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 5121.1885 | 5121.1885
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 5108.3857 | 5108.3857
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 12.803 | 12.803
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.238 | 1.238
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.238 | 1.238
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 105.6857 | 105.6857
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 238.9514 | 238.9514
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2651.9521 | 2651.9521
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 238.9514 | 238.9514
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.238 | 1.238
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2651.9521 | 2651.9521
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.37 | 0.37
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2488.6399 | 2488.6399
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.37 | 0.37
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 73.9944 | 73.9944
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 238.9514 | 238.9514
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2488.6399 | 2488.6399
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 267.4097 | 267.4097
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.3279 | 0.3279
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.3459 | 3.3459
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 87.6155 | 87.6155
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.6762 | 85.6762
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.6762 | 85.6762
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 10840.0771 | 10840.0771
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 10812.9766 | 10812.9766
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 27.1002 | 27.1002
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.37 | 0.37
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.37 | 0.37
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 73.9944 | 73.9944
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 228.9078 | 228.9078
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2488.6399 | 2488.6399
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 228.9078 | 228.9078
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.37 | 0.37
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2488.6399 | 2488.6399
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2337.9866 | 2337.9866
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 229.0892 | 229.0892
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2348.3352 | 2348.3352
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 849.1328 | 849.1328
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 5.0345 | 5.0345
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 168.6629 | 168.6629
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2274.7305 | 2274.7305
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 704.4923 | 704.4923
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 10.0124 | 10.0124
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 13.7394 | 13.7394
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 0.96222 | 0.96222
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 3.7563 | 3.7563
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 87.5884 | 87.5884
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.5028 | 76.5028
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 81.9491 | 81.9491
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 8942.8711 | 8942.8711
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 8920.5137 | 8920.5137
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 22.3572 | 22.3572
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 79.583 | 79.583
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 2.014 | 2.014
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 534.303 | 534.303
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 498.3212 | 498.3212
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 2.014 | 2.014
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 498.3212 | 498.3212
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.9309 | 497.9309
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 79.583 | 79.583
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 2.014 | 2.014
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 534.303 | 534.303
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 498.3212 | 498.3212
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 2.014 | 2.014
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 498.3212 | 498.3212
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.9309 | 497.9309
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.23352 | 0.23352
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3484.0393 | 3484.0393
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.061311 | 0.061311
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.18144 | 0.18144
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.1134 | 0.1134
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 92.5073 | 92.5073
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.7524 | 83.7524
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 241.2453 | 241.2453
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 266.4633 | 266.4633
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 57.2791 | 57.2791
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 223169.4844 | 223169.4844
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 81.0155 | 81.0155
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 534.9143 | 534.9143
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 318.0616 | 318.0616
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3484.0393 | 3484.0393
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 108.9236 | 108.9236
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 226.0548 | 226.0548
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 303.3565 | 303.3565
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 973.8266 | 973.8266
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 144.8047 | 144.8047
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 403.339 | 403.339
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 3.5718 | 3.5718
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 98.8401 | 98.8401
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 4.0338 | 4.0338
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.668 | 0.668
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 131.3855 | 131.3855
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.6375
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 139.4603 | 139.4603
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.80337 | 0.80337
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 65.91
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 2.9438
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 17.1003
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79282
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 3.5511
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 40.6977
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 85.7974 | 85.7974
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 40.3933
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 19.8305 | 19.8305
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2018
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 89.2993 | 89.2993
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 21.7056 | 21.7056
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 49.0609
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 89.2993 | 89.2993
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 28.3036
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 19.6621 | 19.6621
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.2616
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 282.9344 | 282.9344
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 403.339 | 403.339
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 3.5718 | 3.5718
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 235.1016 | 235.1016
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.98737 | 0.98737
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 287.7981 | 287.7981
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 183.2084 | 183.2084
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.61154 | 0.61154
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 65.91
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 3.5511
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99235
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 721.3113 | 721.3113
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 403.339 | 403.339
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 3.5718 | 3.5718
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 757.9541 | 757.9541
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6939 | 1.6939
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 824.6564 | 824.6564
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 325.9907 | 325.9907
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34369 | 0.34369
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 65.91
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 526.1609 | 526.1609
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 403.339 | 403.339
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 3.5718 | 3.5718
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 515.1992 | 515.1992
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4189 | 1.4189
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 578.1714 | 578.1714
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.6375
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 262.679 | 262.679
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42652 | 0.42652
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 65.91
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 2.9438
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 17.1003
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79282
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 3.5511
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 223.0611
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 178.5986 | 178.5986
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.1335
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.68255
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 204.3276
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.080767 | 0.080767
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 61.4695 | 61.4695
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.80708
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 139693.7188 | 139693.7188
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 48.0609
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 178.5986 | 178.5986
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 29.6329
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.080767 | 0.080767
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 39.3686 | 39.3686
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2602
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 139693.7188 | 139693.7188
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 877.2 | 877.2
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 403.339 | 403.339
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 3.5718 | 3.5718
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 950.8564 | 950.8564
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.884 | 1.884
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1028.9951 | 1028.9951
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 376.1472 | 376.1472
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.29786 | 0.29786
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 65.91
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 214.6979
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 171.5948 | 171.5948
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.14532
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.68683
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 195.5857
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.077599 | 0.077599
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 62.6484 | 62.6484
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76084
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 134215.5312 | 134215.5312
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 39.6977
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 171.5948 | 171.5948
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 42.4078
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.077599 | 0.077599
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 39.7156 | 39.7156
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2002
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 134215.5312 | 134215.5312
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.9668
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 143.6047 | 143.6047
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 403.339 | 403.339
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0076183 | 0.0076183
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 97.7534 | 97.7534
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 4.1353 | 4.1353
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.66722 | 0.66722
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 130.0515 | 130.0515
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.6375
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 140.2252 | 140.2252
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.79899 | 0.79899
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 65.91
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 2.9438
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 17.1003
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79282
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 3.5511
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 142.4047 | 142.4047
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 403.339 | 403.339
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0076183 | 0.0076183
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 96.6685 | 96.6685
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 4.2538 | 4.2538
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.66552 | 0.66552
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 128.7178 | 128.7178
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 140.5461 | 140.5461
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.79717 | 0.79717
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 65.91
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 3.5511
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 149.4019 | 149.4019
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 403.339 | 403.339
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0076183 | 0.0076183
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 103.0201 | 103.0201
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 3.696 | 3.696
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.66921 | 0.66921
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 136.5 | 136.5
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.6375
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 82.1289 | 82.1289
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 135.7712 | 135.7712
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.8252 | 0.8252
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 65.91
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 2.9438
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 17.1003
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79282
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 3.5511
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 315698.5 | 315698.5
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 89.2993 | 89.2993
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 21.7056 | 21.7056
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 49.0609
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 89.2993 | 89.2993
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 28.3036
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 19.6621 | 19.6621
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.2616
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 40.6977
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 85.7974 | 85.7974
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 40.3933
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 19.8305 | 19.8305
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2018
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 85.7974 | 85.7974
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 20.8544 | 20.8544
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 85.7974 | 85.7974
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 20.8544 | 20.8544
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 85.7974 | 85.7974
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 19.8578 | 19.8578
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 85.7974 | 85.7974
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.0388 | 0.0388
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 19.8578 | 19.8578
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 67107.7656 | 67107.7656
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 89.2993 | 89.2993
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 19.6843 | 19.6843
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 89.2993 | 89.2993
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.040383 | 0.040383
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 19.6843 | 19.6843
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 69846.8594 | 69846.8594
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 5.8188 | 5.8188
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 253.3819 | 253.3819
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.2329 | 1.2329
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.212 | 7.212
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2965.3818 | 2965.3818
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 417.8932 | 417.8932
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.1008 | 1.1008
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.4434 | 2.4434
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.1059 | 2.1059
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039303 | 0.039303
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8289e-05 | 1.8289e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 5.877 | 5.877
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.651 | 226.651
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.1096 | 1.1096
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.0971 | 7.0971
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2908.7532 | 2908.7532
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 361.2646 | 361.2646
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0735 | 1.0735
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.6134 | 2.6134
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1449 | 2.1449
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.036802 | 0.036802
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7167e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 88.5249 | 88.5249
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0042 | 436.0042
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 318.0616 | 318.0616
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.4448 | 6.4448
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3222.7476 | 3222.7476
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 675.2592 | 675.2592
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.3439 | 1.3439
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 30.1401 | 30.1401
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.6764 | 2.6764
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.067879 | 0.067879
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.606e-05 | 2.606e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 29.2416
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 5922.8818 | 5922.8818
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13137
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 995.916
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 99.9299 | 99.9299
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0157 | 303.0157
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 303.3565 | 303.3565
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2785 | 3.2785
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1360.303 | 1360.303
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1187.1855 | -1187.1855
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.035857 | -0.035857
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 708.331 | 708.331
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 5.7974 | 5.7974
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.54237 | 0.54237
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.5145e-05 | 8.5145e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 5922.8818 | 5922.8818
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 5922.8818 | 5922.8818
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 108.9236 | 108.9236
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 226.0548 | 226.0548
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 303.3565 | 303.3565
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.558 | 2.558
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 973.8266 | 973.8266
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1573.662 | -1573.662
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.37376 | -0.37376
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 839.886 | 839.886
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5874 | 4.5874
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65187 | 0.65187
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.00011971 | 0.00011971
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 318.8181 | 318.8181
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.031068 | 0.031068
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 56.9378 | 56.9378
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 81.0155 | 81.0155
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 534.9143 | 534.9143
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 318.0616 | 318.0616
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.828 | 6.828
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.5065 | 1.5065
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 22.9505 | 22.9505
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.4145 | 2.4145
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.077447 | 0.077447
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.0283e-05 | 3.0283e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 110.8402 | 110.8402
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 157.7357 | 157.7357
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 303.3565 | 303.3565
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.908 | 1.908
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 671.9552 | 671.9552
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1875.5333 | -1875.5333
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.62498 | -0.62498
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.7547 | 915.7547
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 2.014 | 2.014
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 128.8454 | 128.8454
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 0.99333 | 0.99333
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.17 | 7.17
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2724.6687 | 2724.6687
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 177.1802 | 177.1802
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0082 | 1.0082
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 1.1098 | 1.1098
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.1032 | 2.1032
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027589 | 0.027589
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3315e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 25.58 | 25.58
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 389.8145 | 389.8145
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 317.3646 | 317.3646
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 6.9709 | 6.9709
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3216.1196 | 3216.1196
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 668.6311 | 668.6311
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.2256 | 1.2256
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 8.6763 | 8.6763
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2349 | 2.2349
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.05578 | 0.05578
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3967e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 25.58 | 25.58
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 389.8145 | 389.8145
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 302.9824 | 302.9824
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 6.9709 | 6.9709
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3216.1196 | 3216.1196
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 668.6311 | 668.6311
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.2256 | 1.2256
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 8.6763 | 8.6763
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2349 | 2.2349
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.05578 | 0.05578
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3967e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 25.58 | 25.58
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 389.8145 | 389.8145
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 14.3822 | 14.3822
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 6.9709 | 6.9709
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3216.1196 | 3216.1196
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 668.6311 | 668.6311
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.2256 | 1.2256
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 8.6763 | 8.6763
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2349 | 2.2349
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.05578 | 0.05578
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3967e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 17.08 | 17.08
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 342.3405 | 342.3405
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 302.9824 | 302.9824
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.0112 | 7.0112
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3126.8857 | 3126.8857
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 579.3972 | 579.3972
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1729 | 1.1729
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 6.2137 | 6.2137
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1991 | 2.1991
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.049773 | 0.049773
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.1961e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 17.08 | 17.08
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 342.3405 | 342.3405
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 23.8801 | 23.8801
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 7.0112 | 7.0112
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3126.8857 | 3126.8857
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 579.3972 | 579.3972
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1729 | 1.1729
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 6.2137 | 6.2137
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.1991 | 2.1991
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.049773 | 0.049773
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.1961e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 17.08 | 17.08
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 342.3405 | 342.3405
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 279.1023 | 279.1023
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 7.0112 | 7.0112
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3126.8857 | 3126.8857
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 579.3972 | 579.3972
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1729 | 1.1729
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 6.2137 | 6.2137
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.1991 | 2.1991
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.049773 | 0.049773
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.1961e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 29.2416
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 5922.8818 | 5922.8818
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13137
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 995.916
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 5.8188 | 5.8188
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 226.0666 | 226.0666
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.1096 | 1.1096
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.0996 | 7.0996
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2907.7532 | 2907.7532
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 360.2646 | 360.2646
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0732 | 1.0732
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.5902 | 2.5902
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1438 | 2.1438
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.036737 | 0.036737
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7144e-05 | 1.7144e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 5.877 | 5.877
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.651 | 226.651
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 277.9927 | 277.9927
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.0971 | 7.0971
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2908.7532 | 2908.7532
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 361.2646 | 361.2646
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0735 | 1.0735
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.6134 | 2.6134
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1449 | 2.1449
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.036802 | 0.036802
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7167e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 159.4091 | 159.4091
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.031068 | 0.031068
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 56.9378 | 56.9378
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 5.8188 | 5.8188
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 500.233 | 500.233
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.12329 | 0.12329
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 8.0189 | 8.0189
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.349 | 1.349
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.6375 | 1.6375
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1484 | 2.1484
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067311 | 0.067311
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8597e-05 | 2.8597e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.2137 | 1.2137
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 77.1238 | 77.1238
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 38.0479 | 38.0479
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.041 | 1.041
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 322.9474 | 322.9474
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2224.5413 | -2224.5413
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.052495 | -0.052495
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 973.6211 | 973.6211
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.194 | 4.194
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66557 | 0.66557
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00036791 | 0.00036791
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.5519 | 6.5519
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 71.5246 | 71.5246
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 279.323 | 279.323
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.97318 | 0.97318
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 299.9137 | 299.9137
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2247.5747 | -2247.5747
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.18593 | -0.18593
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 977.1834 | 977.1834
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1892 | 4.1892
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.66167 | 0.66167
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00039604 | 0.00039604
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.031068 | 0.031068
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 56.9378 | 56.9378
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 16.7451 | 16.7451
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 164.2944 | 164.2944
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 38.2623 | 38.2623
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9843 | 1.9843
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 694.7333 | 694.7333
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1852.7552 | -1852.7552
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.090272 | -0.090272
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 903.8487 | 903.8487
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.348 | 4.348
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68184 | 0.68184
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016509 | 0.00016509
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 5.082 | 5.082
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 212.3696 | 212.3696
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 277.9927 | 277.9927
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.108 | 7.108
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2881.887 | 2881.887
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 334.3983 | 334.3983
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0632 | 1.0632
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.3247 | 2.3247
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1395 | 2.1395
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035354 | 0.035354
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6589e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 5.082 | 5.082
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 212.3696 | 212.3696
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 16.2632 | 16.2632
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.108 | 7.108
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2881.887 | 2881.887
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 334.3983 | 334.3983
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0632 | 1.0632
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.3247 | 2.3247
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1395 | 2.1395
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035354 | 0.035354
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6589e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 5.082 | 5.082
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 212.3696 | 212.3696
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 261.7295 | 261.7295
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.108 | 7.108
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2881.887 | 2881.887
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 334.3983 | 334.3983
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0632 | 1.0632
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.3247 | 2.3247
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1395 | 2.1395
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035354 | 0.035354
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6589e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 2.014 | 2.014
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 128.8454 | 128.8454
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 261.7295 | 261.7295
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.17 | 7.17
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2724.6687 | 2724.6687
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 177.1802 | 177.1802
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0082 | 1.0082
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 1.1098 | 1.1098
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.1032 | 2.1032
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027589 | 0.027589
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3315e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 2.014 | 2.014
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 128.8454 | 128.8454
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 7.2042 | 7.2042
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.17 | 7.17
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2724.6687 | 2724.6687
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 177.1802 | 177.1802
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0082 | 1.0082
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 1.1098 | 1.1098
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.1032 | 2.1032
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027589 | 0.027589
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3315e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.9745 | 1.9745
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 108.7193 | 108.7193
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 23.4674 | 23.4674
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.4045 | 1.4045
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 455.9657 | 455.9657
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2091.5229 | -2091.5229
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.021336 | -0.021336
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 951.9878 | 951.9878
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2266 | 4.2266
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68148 | 0.68148
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00025822 | 0.00025822
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.1382 | 6.1382
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 103.1144 | 103.1144
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 279.323 | 279.323
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3417 | 1.3417
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 432.6099 | 432.6099
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2114.8787 | -2114.8787
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.11608 | -0.11608
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 956.3689 | 956.3689
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2181 | 4.2181
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.67982 | 0.67982
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00027331 | 0.00027331
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.3108 | 5.3108
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 150.0223 | 150.0223
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 279.323 | 279.323
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8421 | 1.8421
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 632.2855 | 632.2855
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1915.203 | -1915.203
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.0084685 | -0.0084685
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 917.0516 | 917.0516
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3096 | 4.3096
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68443 | 0.68443
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018197 | 0.00018197
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 159.409 | 159.409
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.031068 | 0.031068
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 56.9378 | 56.9378
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.429 | 45.429
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 279.323 | 279.323
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64424 | 0.64424
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.2089 | 190.2089
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.2798 | -2357.2798
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061042 | -0.061042
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0566 | 990.0566
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63579 | 0.63579
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059094 | 0.00059094
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3792 | 7.3792
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5065 | 45.5065
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 279.323 | 279.323
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64496 | 0.64496
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1411 | 191.1411
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3474 | -2356.3474
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.25035 | -0.25035
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3253 | 990.3253
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63624 | 0.63624
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059023 | 0.00059023
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 4.9824 | 4.9824
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 211.6805 | 211.6805
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 16.2632 | 16.2632
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.1148 | 7.1148
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2880.887 | 2880.887
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 333.3984 | 333.3984
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0631 | 1.0631
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.2815 | 2.2815
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1365 | 2.1365
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.03527 | 0.03527
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6562e-05 | 1.6562e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 4.9824 | 4.9824
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 123.4267 | 123.4267
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 16.2632 | 16.2632
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5644 | 1.5644
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 518.5051 | 518.5051
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2028.9835 | -2028.9835
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.057441 | -0.057441
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 940.4945 | 940.4945
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2497 | 4.2497
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68486 | 0.68486
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00022523 | 0.00022523
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.7245 | 5.7245
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 117.8152 | 117.8152
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 279.323 | 279.323
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.5038 | 1.5038
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 494.7392 | 494.7392
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2052.7493 | -2052.7493
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.080241 | -0.080241
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 945.0842 | 945.0842
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.2397 | 4.2397
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68398 | 0.68398
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00023691 | 0.00023691
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 25.0205 | 25.0205
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 210.818 | 210.818
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 14.3822 | 14.3822
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.4314 | 2.4314
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 901.6562 | 901.6562
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1645.8323 | -1645.8323
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.032899 | -0.032899
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 852.2228 | 852.2228
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5515 | 4.5515
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.65669 | 0.65669
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012659 | 0.00012659
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 2.014 | 2.014
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 128.8454 | 128.8454
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 253.5319 | 253.5319
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.17 | 7.17
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2724.6687 | 2724.6687
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 177.1802 | 177.1802
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0082 | 1.0082
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 1.1098 | 1.1098
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.1032 | 2.1032
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027589 | 0.027589
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3315e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 99.9299 | 99.9299
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 310.948 | 310.948
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 302.6 | 302.6
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.6163 | 5.6163
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2725.6003 | 2725.6003
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 178.1117 | 178.1117
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 55.4062 | 55.4062
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 6.727 | 6.727
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.078958 | 0.078958
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 2.0339e-05 | 2.0339e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.238 | 1.238
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 105.6857 | 105.6857
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 253.5319 | 253.5319
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.2014 | 7.2014
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2651.9521 | 2651.9521
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 104.4635 | 104.4635
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.9855 | 0.9855
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.7314 | 0.7314
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2225 | 4.2225
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025406 | 0.025406
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.238 | 1.238
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 105.6857 | 105.6857
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 14.5805 | 14.5805
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.2014 | 7.2014
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2651.9521 | 2651.9521
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 104.4635 | 104.4635
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.9855 | 0.9855
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.7314 | 0.7314
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2225 | 4.2225
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025406 | 0.025406
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.238 | 1.238
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 105.6857 | 105.6857
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 238.9514 | 238.9514
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.2014 | 7.2014
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2651.9521 | 2651.9521
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 104.4635 | 104.4635
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.9855 | 0.9855
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.7314 | 0.7314
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2225 | 4.2225
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025406 | 0.025406
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.37 | 0.37
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 73.9944 | 73.9944
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 238.9514 | 238.9514
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.28 | 7.28
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2488.6399 | 2488.6399
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -58.8486 | -58.8486
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.9379 | 0.9379
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.24821 | 0.24821
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1921 | 4.1921
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022335 | 0.022335
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1398e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.37 | 0.37
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 73.9944 | 73.9944
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 11.037 | 11.037
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.3412 | 7.3412
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2509.8826 | 2509.8826
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -37.606 | -37.606
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.94705 | 0.94705
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.24582 | 0.24582
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1921 | 4.1921
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022335 | 0.022335
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1398e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.37 | 0.37
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 73.9944 | 73.9944
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 228.9078 | 228.9078
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.28 | 7.28
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2488.6399 | 2488.6399
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -58.8486 | -58.8486
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.9379 | 0.9379
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.24821 | 0.24821
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1921 | 4.1921
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022335 | 0.022335
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1398e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 278.5143 | 278.5143
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 110.4265 | 110.4265
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 203.7776 | 203.7776
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 303.3565 | 303.3565
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.3515 | 2.3515
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 873.1451 | 873.1451
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1674.3435 | -1674.3435
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.46184 | -0.46184
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 867.3748 | 867.3748
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4619 | 4.4619
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.6696 | 0.6696
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013335 | 0.00013335
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 39.3118
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 11845.7637 | 11845.7637
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.56313
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 164.8359
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2382.6526
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.17681
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 992.599
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1779
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62836
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006607
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 29.2957
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 11845.7637 | 11845.7637
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20507
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 995.9927
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 25.0784 | 25.0784
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 388.9782 | 388.9782
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 14.3822 | 14.3822
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 6.9782 | 6.9782
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3215.1196 | 3215.1196
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 667.6311 | 667.6311
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.2246 | 1.2246
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 8.512 | 8.512
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.2314 | 2.2314
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055637 | 0.055637
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3932e-05 | 2.3932e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 16.7451 | 16.7451
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 341.5572 | 341.5572
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 23.8801 | 23.8801
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 7.0184 | 7.0184
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3125.8857 | 3125.8857
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 578.3973 | 578.3973
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1723 | 1.1723
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 6.0965 | 6.0965
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.1959 | 2.1959
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.049652 | 0.049652
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1929e-05 | 2.1929e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 1.9745 | 1.9745
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 128.1893 | 128.1893
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 7.2042 | 7.2042
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.1765 | 7.1765
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2723.6687 | 2723.6687
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 176.1802 | 176.1802
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0082 | 1.0082
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 1.0895 | 1.0895
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.1003 | 2.1003
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027517 | 0.027517
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3292e-05 | 1.3292e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.2137 | 1.2137
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 105.1123 | 105.1123
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 14.5805 | 14.5805
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.2076 | 7.2076
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2650.9521 | 2650.9521
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 103.4636 | 103.4636
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98546 | 0.98546
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.71801 | 0.71801
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2218 | 4.2218
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.025345 | 0.025345
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2456e-05 | 1.2456e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.36275 | 0.36275
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 73.5249 | 73.5249
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 11.037 | 11.037
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.3469 | 7.3469
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2508.8826 | 2508.8826
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -38.606 | -38.606
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.94699 | 0.94699
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.24131 | 0.24131
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1918 | 4.1918
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022293 | 0.022293
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1382e-05 | 1.1382e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 497.3914 | 497.3914
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.3402 | 0.3402
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6341 | 9.6341
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3722 | 1.3722
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049218 | 0.049218
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1278 | 2.1278
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066575 | 0.066575
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8475e-05 | 2.8475e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 110.8402 | 110.8402
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 157.7357 | 157.7357
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 159.4091 | 159.4091
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 671.9551 | 671.9551
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.5334
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.62498 | -0.62498
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.7548 | 915.7548
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 79.583 | 79.583
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 534.3031 | 534.3031
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 317.5981 | 317.5981
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.8358 | 6.8358
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.5019 | 1.5019
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 22.5424 | 22.5424
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.4095 | 2.4095
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.077249 | 0.077249
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.025e-05 | 3.025e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 110.8402 | 110.8402
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 157.7357 | 157.7357
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 15.4616 | 15.4616
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 671.9552 | 671.9552
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.5333
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.62498 | -0.62498
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.7547 | 915.7547
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9655 | 6.9655
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4606 | 46.4606
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 279.323 | 279.323
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65747 | 0.65747
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0928 | 195.0928
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.3958 | -2352.3958
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24256 | -0.24256
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9018 | 989.9018
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63734 | 0.63734
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058047 | 0.00058047
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 5.877 | 5.877
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.651 | 226.651
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 279.1023 | 279.1023
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.0971 | 7.0971
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2908.7532 | 2908.7532
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 361.2646 | 361.2646
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0735 | 1.0735
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.6134 | 2.6134
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1449 | 2.1449
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.036802 | 0.036802
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7167e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.1085 | 52.1085
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 49.4251 | 49.4251
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73098 | 0.73098
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.1178 | 218.1178
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.3706 | -2329.3706
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090194 | -0.0090194
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.0809 | 987.0809
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.64331 | 0.64331
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.0005277 | 0.0005277
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.36275 | 0.36275
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.0692 | 52.0692
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 49.0849 | 49.0849
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73046 | 0.73046
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9698 | 217.9698
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5188 | -2329.5188
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.038644 | -0.038644
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1074 | 987.1074
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64328 | 0.64328
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052804 | 0.00052804
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 229.0892 | 229.0892
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.4167 | 7.4167
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2348.3352 | 2348.3352
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -199.1534 | -199.1534
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.90178 | 0.90178
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.074523 | 0.074523
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.37 | 0.37
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 73.9944 | 73.9944
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 10.0436 | 10.0436
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.28 | 7.28
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2488.6399 | 2488.6399
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -58.8486 | -58.8486
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.9379 | 0.9379
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.24821 | 0.24821
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1921 | 4.1921
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022335 | 0.022335
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1398e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.3402 | 0.3402
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 110.8402 | 110.8402
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 157.7357 | 157.7357
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 159.4091 | 159.4091
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 671.9551 | 671.9551
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.5334
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.62498 | -0.62498
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.7548 | 915.7548
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 110.8402 | 110.8402
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 157.7357 | 157.7357
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 7.7607 | 7.7607
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 671.9552 | 671.9552
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.5333
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.62498 | -0.62498
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.7547 | 915.7547
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 110.8402 | 110.8402
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 157.7357 | 157.7357
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 159.409 | 159.409
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 671.9551 | 671.9551
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.5334
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.62498 | -0.62498
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.7548 | 915.7548
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 110.8402 | 110.8402
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 157.7357 | 157.7357
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 318.8181 | 318.8181
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 671.9552 | 671.9552
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.5333
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.62498 | -0.62498
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.7547 | 915.7547
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 110.8402 | 110.8402
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 157.7357 | 157.7357
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 159.409 | 159.409
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 671.9551 | 671.9551
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.5334
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.62498 | -0.62498
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.7548 | 915.7548
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 110.8402 | 110.8402
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.3365 | 152.3365
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8539 | 1.8539
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.64349 | -0.64349
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 920.8002 | 920.8002
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.283 | 4.283
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.69106 | 0.69106
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018163 | 0.00018163
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 110.8402 | 110.8402
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.3365 | 152.3365
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8539 | 1.8539
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.64349 | -0.64349
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 920.8002 | 920.8002
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.283 | 4.283
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.69106 | 0.69106
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018163 | 0.00018163
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 88.5249 | 88.5249
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0032 | 460.0032
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 310.3009 | 310.3009
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.5333 | 6.5333
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3286.5439 | 3286.5439
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 739.0553 | 739.0553
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.3898 | 1.3898
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 28.7111 | 28.7111
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.5812 | 2.5812
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.070086 | 0.070086
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7114e-05 | 2.7114e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 159.409 | 159.409
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.031068 | 0.031068
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 56.9378 | 56.9378
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 159.4091 | 159.4091
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.031068 | 0.031068
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 56.9378 | 56.9378
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.031068 | 0.031068
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 56.9378 | 56.9378
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 29.2416
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 11845.7637 | 11845.7637
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13137
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 995.916
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 79.583 | 79.583
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 534.3031 | 534.3031
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 318.0616 | 318.0616
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.8358 | 6.8358
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.5019 | 1.5019
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 22.5424 | 22.5424
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.4095 | 2.4095
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.077249 | 0.077249
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.025e-05 | 3.025e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 110.0128 | 110.0128
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 228.0075 | 228.0075
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 303.3565 | 303.3565
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5758 | 2.5758
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 982.8267 | 982.8267
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1564.6619 | -1564.6619
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.37221 | -0.37221
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 837.4348 | 837.4348
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5995 | 4.5995
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65019 | 0.65019
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00011867 | 0.00011867
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 90.2954 | 90.2954
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5047 | 411.5047
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 310.3009 | 310.3009
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.3344 | 6.3344
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3151.5093 | 3151.5093
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 604.0209 | 604.0209
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.297 | 1.297
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 32.5707 | 32.5707
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.8424 | 2.8424
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.06623 | 0.06623
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.4977e-05 | 2.4977e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 110.8402 | 110.8402
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 157.7357 | 157.7357
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 7.7009 | 7.7009
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.908 | 1.908
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 671.9552 | 671.9552
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.5333
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.62498 | -0.62498
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.7547 | 915.7547
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2969 | 4.2969
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.69007 | 0.69007
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.00017493
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 97.9705 | 97.9705
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 338.9995 | 338.9995
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 302.6 | 302.6
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.8911 | 5.8911
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2885.6704 | 2885.6704
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 338.1818 | 338.1818
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1177 | 1.1177
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 45.405 | 45.405
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 4.3739 | 4.3739
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.069024 | 0.069024
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1664e-05 | 2.1664e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 99.9299 | 99.9299
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 310.948 | 310.948
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 302.6 | 302.6
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.6163 | 5.6163
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2725.6003 | 2725.6003
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 178.1117 | 178.1117
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 55.4062 | 55.4062
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.727 | 6.727
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.078958 | 0.078958
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.0339e-05 | 2.0339e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 90.2954 | 90.2954
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.104 | 434.104
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 302.6 | 302.6
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.4251 | 6.4251
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3214.6116 | 3214.6116
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 667.1229 | 667.1229
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3428 | 1.3428
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 30.9462 | 30.9462
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.7028 | 2.7028
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.067959 | 0.067959
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.5984e-05 | 2.5984e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 81.2155 | 81.2155
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 534.9996 | 534.9996
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 318.0616 | 318.0616
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.8269 | 6.8269
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3484.0393 | 3484.0393
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 936.5507 | 936.5507
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.5072 | 1.5072
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 23.0075 | 23.0075
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.4152 | 2.4152
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.077475 | 0.077475
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0288e-05 | 3.0288e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 108.9236 | 108.9236
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 226.0548 | 226.0548
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 303.3565 | 303.3565
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.558 | 2.558
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 973.8266 | 973.8266
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1573.662 | -1573.662
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.37376 | -0.37376
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 839.886 | 839.886
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5874 | 4.5874
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65187 | 0.65187
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00011971 | 0.00011971
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 57.2791 | 57.2791
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15181.7607
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15162.0674
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 6.9687
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 241245.2969 | 241245.2969
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 266463.3438 | 266463.3438
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 40.05
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 10.41
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3

## ELINK
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_100%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 32.18
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 59.56
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 387.7 | 387.7
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 893.9999 | 893.9999
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.27 | 5.27
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.8281 | 153.8281
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.782 | 99.782
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.48065 | 0.48065
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 11.2555 | 11.2555
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 179.5939 | 179.5939
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 77.1724 | 77.1724
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 2.6891 | 2.6891
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 26.7221 | 26.7221
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 5.5477 | 5.5477
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 27.8128 | 27.8128
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 5.5477 | 5.5477
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 27.8128 | 27.8128
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 2.6891 | 2.6891
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 26.7221 | 26.7221
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 204.2 | 204.2
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 228.1 | 228.1
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 40.05
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 537.2 | 537.2
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 29.22
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 86.45 | 86.45
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 27.68 | 27.68
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 18.75 | 18.75
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 6.36 | 6.36
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.5 | 5.5
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 2.18 | 2.18
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.34 | 1.34
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.4 | 0.4
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 32.18
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 59.56
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6342
~~~4~~-5000~ | Plant Summary: Gross power | kW | 110027.0938 | 110027.0938
~~~7~~-5000~ | Plant Summary: Net power | kW | 98810.8672 | 98810.8672
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 11216.2236 | 11216.2236
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 10666.0879 | 10666.0879
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 550.1355 | 550.1355
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 35.5933 | 35.5933
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10114.2646 | 10114.2646
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.9649 | 31.9649
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11262.3555 | 11262.3555
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 309123.0938 | 309123.0938
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.9649 | 31.9649
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.9649 | 31.9649
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.9397 | 28.9397
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12439.6396 | 12439.6396
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 341436.5625 | 341436.5625
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 309123.0938 | 309123.0938
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.9649 | 31.9649
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 1.1103 | 1.1103
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.96925 | 0.96925
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 309123.0938 | 309123.0938
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 341436.5625 | 341436.5625
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 2714.4275 | 2714.4275
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 24926490 | 24926490
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 32036946 | 32036946
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 800.368 | 800.368
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 9014.0293 | 9014.0293
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 9.0971 | 9.0971
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 850.7756 | 850.7756
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 32036.9453 | 32036.9453
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 324.2249 | 324.2249
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 442153.9688 | 442153.9688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 9611.084 | 9611.084
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 58.447 | 58.447
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 170.2605 | 170.2605
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.59818 | 0.59818
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 228323.7812 | 228323.7812
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.03486 | 0.03486
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.1153 | 5.1153
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 24926490 | 24926490
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 24926490 | 24926490
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 4867072 | 4867072
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 29793562 | 29793562
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 32036946 | 32036946
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 110027.0938 | 110027.0938
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 989.8578 | 989.8578
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 429.9547 | 429.9547
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 1165.7252 | 1165.7252
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 281.2412 | 281.2412
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 577.0046 | 577.0046
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 281.2412 | 281.2412
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 577.0046 | 577.0046
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 938.1762 | 938.1762
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 101.2423 | 101.2423
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 1527.5677 | 1527.5677
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 1527.5679 | 1527.5679
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 938.1762 | 938.1762
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 231.0569 | 231.0569
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 1100.271 | 1100.271
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 550.1355 | 550.1355
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 10666.0879 | 10666.0879
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 309123.0938 | 309123.0938
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 19.4543 | 19.4543
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 514765.125 | 514765.125
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 692253.4375 | 692253.4375
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 30338.1348 | 30338.1348
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 9286.5107 | 9286.5107
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 21973.248 | 21973.248
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 2657.5557 | 2657.5557
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 14690.1602 | 14690.1602
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 6641.1538 | 6641.1538
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 13977.8457 | 13977.8457
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 12019.8828 | 12019.8828
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 989.8578 | 989.8578
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 429.9547 | 429.9547
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 1165.7252 | 1165.7252
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 281.2412 | 281.2412
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 577.0046 | 577.0046
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 281.2412 | 281.2412
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 577.0046 | 577.0046
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 938.1762 | 938.1762
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 101.2423 | 101.2423
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 1527.5677 | 1527.5677
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 1527.5679 | 1527.5679
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 938.1762 | 938.1762
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 310.16 | 310.16
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 77.54 | 77.54
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 108.5314 | 108.5314
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 317.0735 | 317.0735
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2709.3022 | 2709.3022
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 893.9999 | 893.9999
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 317.0735 | 317.0735
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 20
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 65.91
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 2.9438
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.2498
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 17.1003
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0031714
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79282
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 176073.375 | 176073.375
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 116337.5469 | 116337.5469
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 29084.3867 | 29084.3867
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 15375.0781 | 15375.0781
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 15276.3691 | 15276.3691
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 2705.6272 | 2705.6272
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 3521.4675 | 3521.4675
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 517.7778 | 517.7778
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 1208.1481 | 1208.1481
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 97.8249 | 97.8249
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 183.6435 | 183.6435
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 126.7684 | 126.7684
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.16514 | 0.16514
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.60102 | 0.60102
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 73.3954 | 73.3954
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 1761.4883 | 1761.4883
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 309123.0938 | 309123.0938
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 341436.5625 | 341436.5625
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 733.9534 | 733.9534
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 255.9044 | 255.9044
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 4.8514 | 4.8514
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.28881 | 0.28881
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.75737 | 0.75737
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 6.3976 | 6.3976
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.9193 | 1.9193
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 4.4783 | 4.4783
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 2.9438
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 17.1003
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.27 | 5.27
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.8281 | 153.8281
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.3108 | 5.3108
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 150.0223 | 150.0223
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 632.2855 | 632.2855
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 358.765 | 358.765
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 6.297 | 6.297
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 252.8501 | 252.8501
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2962.6248 | 2962.6248
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.5596 | 1.5596
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 16.894 | 16.894
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 164.6357 | 164.6357
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 696.2255 | 696.2255
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 48.855 | 48.855
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 409.1796 | 409.1796
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.9992 | 23.9992
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 96.1447 | 96.1447
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0024 | 460.0024
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 397.9526 | 397.9526
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3275.2939 | 3275.2939
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 96.1447 | 96.1447
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0033 | 436.0033
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 408.2104 | 408.2104
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3209.927 | 3209.927
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 10.2577 | 10.2577
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 673.9968 | 673.9968
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5989 | 22.5989
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 98.0676 | 98.0676
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.1031 | 434.1031
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 387.7 | 387.7
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3201.3213 | 3201.3213
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 98.0676 | 98.0676
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5042 | 411.5042
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 397.9526 | 397.9526
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3136.2087 | 3136.2087
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 10.2526 | 10.2526
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 673.9968 | 673.9968
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 31.258 | 31.258
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 191.4111 | 191.4111
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 32.5433 | 32.5433
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 32.5433 | 32.5433
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 31.258 | 31.258
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 388.6693 | 388.6693
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 118.2992 | 118.2992
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 974.4664 | 974.4664
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 226.1392 | 226.1392
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 388.6693 | 388.6693
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 108.5314 | 108.5314
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 303
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1359.2157 | 1359.2157
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 516.8243 | 516.8243
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 4.4783 | 4.4783
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 524.1158 | 524.1158
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 281.8529 | 281.8529
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 56.5243
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1246.3896 | 1246.3896
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 41539.5898 | 41539.5898
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 41539.5898 | 41539.5898
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 311.5469 | 311.5469
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 9.7678 | 9.7678
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.782 | 99.782
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 429.9547 | 429.9547
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 143.6583 | 143.6583
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 641553.5625 | 641553.5625
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 516.8241 | 516.8241
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 4.4783 | 4.4783
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 4.4686 | 4.4686
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0097615 | 0.0097615
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3643.4297 | 3643.4297
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 11469.1475 | 11469.1475
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9416 | 7.9416
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 24.9994 | 24.9994
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 191.467 | 191.467
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.211 | 1.211
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 554.769 | 554.769
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 554.769 | 554.769
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 549.2214 | 549.2214
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 27.8128 | 27.8128
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 5.5477 | 5.5477
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 605.8548 | 605.8548
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 96.1656 | 96.1656
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 577.0046 | 577.0046
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 554.769 | 554.769
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 96.1464 | 96.1464
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 22.2355 | 22.2355
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 582.5074 | 582.5074
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 1125.5491 | 1125.5491
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 1125.5491 | 1125.5491
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 1114.2936 | 1114.2936
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 179.5939 | 179.5939
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1304 | 80.1304
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 11.2555 | 11.2555
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 1224.0114 | 1224.0114
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.5707 | 96.5707
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 1165.7251 | 1165.7251
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 1125.5491 | 1125.5491
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.5536 | 96.5536
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 40.176 | 40.176
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 1181.8264 | 1181.8264
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 268.9126 | 268.9126
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 268.9126 | 268.9126
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 266.2235 | 266.2235
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 26.7221 | 26.7221
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 2.6891 | 2.6891
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 295.3033 | 295.3033
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.6382 | 95.6382
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 281.2412 | 281.2412
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 268.9126 | 268.9126
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.6164 | 95.6164
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 12.3286 | 12.3286
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 282.3582 | 282.3582
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 554.769 | 554.769
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 554.769 | 554.769
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 549.2214 | 549.2214
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 27.8128 | 27.8128
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4257
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 5.5477 | 5.5477
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 605.8548 | 605.8548
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 96.1656 | 96.1656
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 577.0046 | 577.0046
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 554.769 | 554.769
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 96.1464 | 96.1464
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 22.2355 | 22.2355
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 582.5074 | 582.5074
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 268.9126 | 268.9126
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 268.9126 | 268.9126
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 266.2235 | 266.2235
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 26.7221 | 26.7221
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.2169
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 2.6891 | 2.6891
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 295.3033 | 295.3033
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.6382 | 95.6382
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 281.2412 | 281.2412
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 268.9126 | 268.9126
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.6164 | 95.6164
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 12.3286 | 12.3286
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 282.3582 | 282.3582
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.39216 | 0.39216
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 75.3816 | 75.3816
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 11224.3428 | 11224.3428
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 9506.7051 | 9506.7051
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 1717.6375 | 1717.6375
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 26.9283 | 26.9283
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.3137 | 1.3137
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 107.417 | 107.417
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 13418.8516 | 13418.8516
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 11821.7529 | 11821.7529
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 1597.0977 | 1597.0977
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 32.0362 | 32.0362
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 2.1373 | 2.1373
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 122.3229 | 122.3229
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 6286.4082 | 6286.4082
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 5902.043 | 5902.043
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 384.3651 | 384.3651
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.9028 | 14.9028
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 5.3922 | 5.3922
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 154.7026 | 154.7026
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 12643.4219 | 12643.4219
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 11362.7988 | 11362.7988
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 616.6586 | 616.6586
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 663.9647 | 663.9647
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 29.6672 | 29.6672
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 4.7026 | 4.7026
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 16.894 | 16.894
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 204.01 | 204.01
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 21750.9238 | 21750.9238
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 16685.2031 | 16685.2031
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 2700.5259 | 2700.5259
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 2365.1956 | 2365.1956
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 46.123 | 46.123
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 25.1632 | 25.1632
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 224.3029 | 224.3029
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 11661.0791 | 11661.0791
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 9369.709 | 9369.709
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1988.4463 | 1988.4463
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 302.9235 | 302.9235
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 23.8913 | 23.8913
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.7971 | -3.7971
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7617 | 15181.7617
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 73.3954 | 73.3954
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 309123.0938 | 309123.0938
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 341436.5625 | 341436.5625
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 2714.4275 | 2714.4275
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15162.0674
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15181.7607
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16839.0098
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 10.41
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 40.05
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 6.9687
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 32.1803
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 114.4249 | 114.4249
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.051746 | 0.051746
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 32.1803
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 109.9377 | 109.9377
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6575
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.8741
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3577
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.825
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91378
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.049716 | 0.049716
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 32.1803
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 114.4249 | 114.4249
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.051746 | 0.051746
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 32.1803
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 7.3473
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 109.9377 | 109.9377
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6575
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.8741
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3577
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029447
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.825
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91378
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.049716 | 0.049716
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.3099
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 904.7342 | 904.7342
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 877.5922 | 877.5922
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 938.1761 | 938.1761
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 7559.2622 | 7559.2622
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 7559.2622 | 7559.2622
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 970.9543 | 970.9543
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.4478 | 96.4478
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 938.1761 | 938.1761
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 904.7342 | 904.7342
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.4354 | 96.4354
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 33.442 | 33.442
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 936.344 | 936.344
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.3099
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 904.7342 | 904.7342
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 877.5922 | 877.5922
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 938.1761 | 938.1761
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 7559.2622 | 7559.2622
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 29.2416
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 122.5732
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 7559.2622 | 7559.2622
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 29.2957
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 122.9911
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 970.9543 | 970.9543
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.4478 | 96.4478
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 938.1761 | 938.1761
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 904.7342 | 904.7342
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.4354 | 96.4354
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 33.442 | 33.442
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 936.344 | 936.344
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.4478 | 96.4478
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 71.2929 | 71.2929
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.9218 | 6.9218
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.9218 | 6.9218
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 75.0006 | 75.0006
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 95.7684 | 95.7684
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 92.8953 | 92.8953
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 101.2423 | 101.2423
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 358.765 | 358.765
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.423 | 45.423
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.1834 | 190.1834
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 358.765 | 358.765
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3792 | 7.3792
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5004 | 45.5004
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.1155 | 191.1155
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 104.7795 | 104.7795
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 94.6121 | 94.6121
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 101.2423 | 101.2423
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 95.7684 | 95.7684
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 94.5932 | 94.5932
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 5.4739 | 5.4739
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 99.1143 | 99.1143
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1284.6265 | 1284.6265
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 116.8622 | 116.8622
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 116.8622 | 116.8622
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 1476.1187 | 1476.1187
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 1431.8351 | 1431.8351
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 1527.5677 | 1527.5677
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 204.5898 | 204.5898
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 204.5898 | 204.5898
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 120.3095 | 120.3095
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 142.4535 | 142.4535
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 607.2243 | 607.2243
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 2123.1482 | 2123.1482
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.8267 | 96.8267
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 1527.5677 | 1527.5677
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 1476.1187 | 1476.1187
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.632 | 96.632
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 51.4491 | 51.4491
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 2051.6396 | 2051.6396
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1284.6265 | 1284.6265
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 116.8622 | 116.8622
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 116.8622 | 116.8622
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 1476.1188 | 1476.1188
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 1431.8352 | 1431.8352
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 1527.5679 | 1527.5679
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 204.5898 | 204.5898
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 204.5898 | 204.5898
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 120.3095 | 120.3095
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 142.4535 | 142.4535
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 607.2243 | 607.2243
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 2123.1484 | 2123.1484
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.8267 | 96.8267
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 1527.5679 | 1527.5679
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 1476.1188 | 1476.1188
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.632 | 96.632
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 51.4491 | 51.4491
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 2051.6399 | 2051.6399
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 1.1103 | 1.1103
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 357.6548 | 357.6548
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 358.765 | 358.765
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.423 | 45.423
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.1834 | 190.1834
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0068469 | 0.0068469
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99315 | 0.99315
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 7.1897e-10 | 7.1897e-10
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.8741
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3577
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029447
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.825
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91378
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 22628.5273 | 22628.5273
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 11082.3271 | 11082.3271
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 11546.2012 | 11546.2012
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 11027.1914 | 11027.1914
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 11488.7578 | 11488.7578
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 112.5767 | 112.5767
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.06297 | 0.06297
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 1 | 1
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.3899 | 0.3899
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.5561 | 1.5561
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.54275 | 0.54275
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 5.0507 | 5.0507
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.36765 | 0.36765
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 8.5197 | 8.5197
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.10784 | 0.10784
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 5.3827 | 5.3827
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.042745 | 0.042745
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 2.6357 | 2.6357
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.026274 | 0.026274
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 5.3243 | 5.3243
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0078431 | 0.0078431
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 4.2495 | 4.2495
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 1.183 | 1.183
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 971.685 | 971.685
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 393.3015 | 393.3015
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.95284 | 0.95284
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7474 | 10.7474
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.050126 | 0.050126
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.94987 | 0.94987
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00038207 | 0.00038207
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99855 | 0.99855
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010696 | 0.0010696
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95535 | 0.95535
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.04465 | 0.04465
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92116 | 0.92116
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.078837 | 0.078837
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99608 | 0.99608
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0039167 | 0.0039167
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.94572 | 0.94572
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.054284 | 0.054284
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96781 | 0.96781
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0040784 | 0.0040784
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.028107 | 0.028107
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94133 | 0.94133
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.058665 | 0.058665
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.95474 | 0.95474
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.045264 | 0.045264
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 7.1897e-10 | 7.1897e-10
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50013 | 0.50013
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49987 | 0.49987
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 148.239 | 148.239
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 57.0002
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.9678
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 2525.6865 | 2525.6865
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 2.9438
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.2498
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 17.1003
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 65.91
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79282
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0031714
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.829
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 93.8988
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 32.8529
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0097615 | 0.0097615
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9416 | 7.9416
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9994 | 24.9994
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 2.9438
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 17.1003
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 408.2104 | 408.2104
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 96.1447 | 96.1447
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3209.927 | 3209.927
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0032 | 436.0032
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 408.2104 | 408.2104
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 88.2061 | 88.2061
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 537.2 | 537.2
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3482.1716 | 3482.1716
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 516.8243 | 516.8243
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 4.4783 | 4.4783
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 894 | 894
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 731.6876 | 731.6876
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 30870.7617 | 30870.7617
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 7.9386 | 7.9386
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 387.7 | 387.7
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 106.4033 | 106.4033
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2851.1492 | 2851.1492
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 338.9836 | 338.9836
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 387.7 | 387.7
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 98.0676 | 98.0676
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3201.3213 | 3201.3213
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 516.8243 | 516.8243
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 4.4783 | 4.4783
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 731.6875 | 731.6875
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 524.1159 | 524.1159
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 37712.1797 | 37712.1797
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 282.8414 | 282.8414
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 8.3357 | 8.3357
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 118.2992 | 118.2992
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 226.1392 | 226.1392
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 974.4664 | 974.4664
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 388.6693 | 388.6693
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 118.2992 | 118.2992
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 226.1392 | 226.1392
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 974.4664 | 974.4664
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.20001 | 0.20001
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 88.2061 | 88.2061
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 537.2003 | 537.2003
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3482.1716 | 3482.1716
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 408.2104 | 408.2104
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 88.0061 | 88.0061
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 537.116 | 537.116
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3482.1716 | 3482.1716
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 120.3095 | 120.3095
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.1979 | 152.1979
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 120.3095 | 120.3095
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.1979 | 152.1979
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 120.3095 | 120.3095
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 158.077 | 158.077
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 673.9965 | 673.9965
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 204.5898 | 204.5898
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 120.3095 | 120.3095
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 158.077 | 158.077
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 673.9965 | 673.9965
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 120.3095 | 120.3095
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 158.077 | 158.077
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 673.9965 | 673.9965
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 204.5898 | 204.5898
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 120.3095 | 120.3095
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 158.077 | 158.077
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 673.9965 | 673.9965
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 204.5898 | 204.5898
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 204.5898 | 204.5898
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 39.3118
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 164.8358
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 15118.5244 | 15118.5244
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 29.2416
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 122.5732
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 15118.5244 | 15118.5244
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 175732.4844 | 175732.4844
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 110027.0938 | 110027.0938
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.6043 | 98.6043
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 173.2927 | 173.2927
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 57.7642 | 57.7642
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 128.365 | 128.365
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.6233 | 98.6233
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 90.7725 | 90.7725
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 536.4592 | 536.4592
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 407.6178 | 407.6178
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 115528.4453 | 115528.4453
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.6233 | 98.6233
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 110027.0938 | 110027.0938
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 111584.4922 | 111584.4922
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.6043 | 98.6043
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1557.3973 | 1557.3973
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 1366.5381 | 1366.5381
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 190.8593 | 190.8593
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 11.0305 | 11.0305
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 5.1286 | 5.1286
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 185334.25 | 185334.25
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 10.2414 | 10.2414
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.5074 | 3.5074
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 170233.7812 | 170233.7812
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 21.2719 | 21.2719
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 5.1286 | 5.1286
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 355568.0312 | 355568.0312
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 23.8759 | 23.8759
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 6.1544 | 6.1544
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 20509736 | 20509736
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 24926490 | 24926490
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 86.45 | 86.45
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 86.45 | 86.45
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 536.4592 | 536.4592
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 407.6178 | 407.6178
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3482.1716 | 3482.1716
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 407.239 | 407.239
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 86.45 | 86.45
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3482.1716 | 3482.1716
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 27.68 | 27.68
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3213.314 | 3213.314
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 27.68 | 27.68
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 390.2057 | 390.2057
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 407.239 | 407.239
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3213.314 | 3213.314
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 12.0183 | 12.0183
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.011633 | 0.011633
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1232 | 3.1232
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 73.4972 | 73.4972
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 75.6653 | 75.6653
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 75.6653 | 75.6653
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 30414.1699 | 30414.1699
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 30338.1348 | 30338.1348
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 76.0354 | 76.0354
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 27.68 | 27.68
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 27.68 | 27.68
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 390.2057 | 390.2057
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 389.0559 | 389.0559
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3213.314 | 3213.314
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 389.0559 | 389.0559
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 27.68 | 27.68
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3213.314 | 3213.314
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 18.75 | 18.75
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3127.1702 | 3127.1702
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 18.75 | 18.75
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 344.0994 | 344.0994
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 389.0559 | 389.0559
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3127.1702 | 3127.1702
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 15.8415 | 15.8415
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.031705 | 0.031705
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4763 | 1.4763
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 78.1537 | 78.1537
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 78.5327 | 78.5327
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 78.5327 | 78.5327
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 9309.7842 | 9309.7842
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 9286.5107 | 9286.5107
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 23.2744 | 23.2744
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 18.75 | 18.75
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 18.75 | 18.75
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 344.0994 | 344.0994
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 358.384 | 358.384
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3127.1702 | 3127.1702
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 358.384 | 358.384
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 18.75 | 18.75
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3127.1702 | 3127.1702
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 6.36 | 6.36
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2905.8972 | 2905.8972
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 6.36 | 6.36
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.2648 | 226.2648
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 358.384 | 358.384
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2905.8972 | 2905.8972
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 35.0919 | 35.0919
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.041681 | 0.041681
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9481 | 2.9481
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 82.7075 | 82.7075
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 84.0439 | 84.0439
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 84.0439 | 84.0439
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 22028.3203 | 22028.3203
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 21973.248 | 21973.248
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 55.0707 | 55.0707
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 6.36 | 6.36
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 6.36 | 6.36
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.2648 | 226.2648
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 356.9803 | 356.9803
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2905.8972 | 2905.8972
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 356.9803 | 356.9803
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 6.36 | 6.36
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2905.8972 | 2905.8972
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 5.5 | 5.5
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2879.03 | 2879.03
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 5.5 | 5.5
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 211.9436 | 211.9436
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 356.9803 | 356.9803
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2879.03 | 2879.03
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 39.2905 | 39.2905
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.11055 | 0.11055
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1564 | 1.1564
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 83.8913 | 83.8913
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 83.8911 | 83.8911
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 83.8911 | 83.8911
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 2664.2161 | 2664.2161
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 2657.5557 | 2657.5557
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 6.6605 | 6.6605
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 5.5 | 5.5
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 5.5 | 5.5
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 211.9436 | 211.9436
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 337.602 | 337.602
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2879.03 | 2879.03
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 337.602 | 337.602
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 5.5 | 5.5
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2879.03 | 2879.03
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 2.18 | 2.18
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2721.9922 | 2721.9922
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 2.18 | 2.18
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 128.3819 | 128.3819
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 337.602 | 337.602
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2721.9922 | 2721.9922
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 77.8079 | 77.8079
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.11919 | 0.11919
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5229 | 2.5229
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.7638 | 85.7638
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 86.6021 | 86.6021
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 86.6021 | 86.6021
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 14726.9775 | 14726.9775
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 14690.1602 | 14690.1602
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 36.8174 | 36.8174
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 2.18 | 2.18
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 2.18 | 2.18
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 128.3819 | 128.3819
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 326.7362 | 326.7362
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2721.9922 | 2721.9922
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 326.7362 | 326.7362
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 2.18 | 2.18
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2721.9922 | 2721.9922
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.34 | 1.34
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2648.6372 | 2648.6372
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.34 | 1.34
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 107.9986 | 107.9986
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 326.7362 | 326.7362
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2648.6372 | 2648.6372
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 114.8681 | 114.8681
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.26514 | 0.26514
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.6269 | 1.6269
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 86.6278 | 86.6278
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 86.628 | 86.628
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 86.628 | 86.628
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 6657.7983 | 6657.7983
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 6641.1538 | 6641.1538
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 16.6445 | 16.6445
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.34 | 1.34
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.34 | 1.34
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 107.9986 | 107.9986
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 307.5682 | 307.5682
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2648.6372 | 2648.6372
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 307.5682 | 307.5682
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.34 | 1.34
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2648.6372 | 2648.6372
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.4 | 0.4
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2484.623 | 2484.623
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.4 | 0.4
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 75.8568 | 75.8568
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 307.5682 | 307.5682
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2484.623 | 2484.623
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 318.8601 | 318.8601
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.3897 | 0.3897
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.35 | 3.35
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 88.0421 | 88.0421
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.8082 | 85.8082
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.8082 | 85.8082
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 14012.8779 | 14012.8779
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 13977.8457 | 13977.8457
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 35.0322 | 35.0322
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.4 | 0.4
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.4 | 0.4
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 75.8568 | 75.8568
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 293.6464 | 293.6464
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2484.623 | 2484.623
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 293.6464 | 293.6464
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.4 | 0.4
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2484.623 | 2484.623
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2325.2444 | 2325.2444
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 293.8842 | 293.8842
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2337.2493 | 2337.2493
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 1082.817 | 1082.817
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 5.9214 | 5.9214
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 182.864 | 182.864
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2429.6218 | 2429.6218
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 775.7797 | 775.7797
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 11.6521 | 11.6521
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 16.1448 | 16.1448
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 1.1407 | 1.1407
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 4.0609 | 4.0609
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 88.0245 | 88.0245
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.0904 | 76.0904
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 82.0921 | 82.0921
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 12050.0088 | 12050.0088
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 12019.8828 | 12019.8828
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 30.125 | 30.125
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 86.45 | 86.45
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 2.18 | 2.18
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 536.4592 | 536.4592
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 497.5313 | 497.5313
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 2.18 | 2.18
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 497.5313 | 497.5313
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.0556 | 497.0556
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 86.45 | 86.45
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 2.18 | 2.18
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 536.4592 | 536.4592
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 497.5313 | 497.5313
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 2.18 | 2.18
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 497.5313 | 497.5313
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.0556 | 497.0556
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.37875 | 0.37875
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3482.1716 | 3482.1716
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.099178 | 0.099178
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.23779 | 0.23779
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.24014 | 0.24014
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 92.5832 | 92.5832
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.8211 | 83.8211
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 309.1231 | 309.1231
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 341.4366 | 341.4366
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 73.3954 | 73.3954
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 286195.9062 | 286195.9062
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 88.0061 | 88.0061
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 537.116 | 537.116
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 408.2104 | 408.2104
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3482.1716 | 3482.1716
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 118.2992 | 118.2992
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 226.1392 | 226.1392
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 388.6693 | 388.6693
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 974.4664 | 974.4664
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 143.6583 | 143.6583
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 516.8241 | 516.8241
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 4.4783 | 4.4783
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 97.8019 | 97.8019
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 4.1638 | 4.1638
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.66494 | 0.66494
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 130.111 | 130.111
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.6375
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 105.237 | 105.237
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 178.2093 | 178.2093
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.80558 | 0.80558
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 65.91
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 2.9438
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 17.1003
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79282
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 3.5511
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 40.6977
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 109.9377 | 109.9377
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 40.3933
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 25.4101 | 25.4101
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2018
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 114.4249 | 114.4249
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 27.8128 | 27.8128
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 49.0609
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 114.4249 | 114.4249
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 28.3036
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 25.1944 | 25.1944
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.2616
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.825
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 281.8529 | 281.8529
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 516.8241 | 516.8241
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 4.4783 | 4.4783
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 233.9566 | 233.9566
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.98512 | 0.98512
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 286.5504 | 286.5504
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 105.237 | 105.237
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 234.3001 | 234.3001
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.61273 | 0.61273
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 65.91
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 3.5511
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99235
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 731.6876 | 731.6876
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 516.8241 | 516.8241
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 4.4783 | 4.4783
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 770.9417 | 770.9417
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.7073 | 1.7073
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 838.0667 | 838.0667
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 105.237 | 105.237
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 422.0713 | 422.0713
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34014 | 0.34014
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 65.91
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 524.1159 | 524.1159
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 516.8241 | 516.8241
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 4.4783 | 4.4783
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 512.7029 | 512.7029
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4158 | 1.4158
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 575.6496 | 575.6496
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.6375
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 105.237 | 105.237
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 335.7263 | 335.7263
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42762 | 0.42762
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 65.91
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 2.9438
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 17.1003
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79282
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 3.5511
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 223.0611
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 228.8499 | 228.8499
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.1335
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.68255
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 204.3276
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.10349 | 0.10349
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 78.7649 | 78.7649
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.80708
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 178998.5312 | 178998.5312
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 48.0609
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 228.8499 | 228.8499
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 29.6329
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.10349 | 0.10349
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 50.4456 | 50.4456
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2602
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 178998.5312 | 178998.5312
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 893.9999 | 893.9999
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 516.8241 | 516.8241
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 4.4783 | 4.4783
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 971.1801 | 971.1801
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.9033 | 1.9033
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1051.3622 | 1051.3622
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.6375
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 105.237 | 105.237
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 489.0205 | 489.0205
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.29357 | 0.29357
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 65.91
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 2.9438
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 17.1003
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79282
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.15857
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 3.5511
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 214.6979
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 219.8754 | 219.8754
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.14532
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.68683
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 195.5857
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.099433 | 0.099433
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 80.2754 | 80.2754
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76084
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.825
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 171978.9844 | 171978.9844
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 39.6977
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 219.8754 | 219.8754
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 42.4078
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.099433 | 0.099433
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 50.8902 | 50.8902
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2002
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.825
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 171978.9844 | 171978.9844
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.9668
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 142.4583 | 142.4583
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 516.8241 | 516.8241
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0097615 | 0.0097615
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 96.7169 | 96.7169
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 4.2694 | 4.2694
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.66416 | 0.66416
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 128.7773 | 128.7773
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.6375
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 105.237 | 105.237
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 179.1852 | 179.1852
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.8012 | 0.8012
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 65.91
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 2.9438
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 17.1003
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79282
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 3.5511
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 141.2583 | 141.2583
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 516.8241 | 516.8241
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0097615 | 0.0097615
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 95.6338 | 95.6338
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 4.3926 | 4.3926
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.66245 | 0.66245
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 127.444 | 127.444
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.6375
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 105.237 | 105.237
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 179.594 | 179.594
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.79937 | 0.79937
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 65.91
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 2.9438
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 17.1003
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79282
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 3.5511
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 148.239 | 148.239
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 516.8241 | 516.8241
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0097615 | 0.0097615
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 101.9602 | 101.9602
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 3.8139 | 3.8139
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.66614 | 0.66614
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 135.2057 | 135.2057
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.6375
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 105.237 | 105.237
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 173.4936 | 173.4936
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.82748 | 0.82748
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 65.91
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 2.9438
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.2498
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 17.1003
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79282
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0031714
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 3.5511
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 404524.75 | 404524.75
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 114.4249 | 114.4249
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 27.8128 | 27.8128
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 49.0609
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 114.4249 | 114.4249
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 28.3036
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.23262
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 24.6265
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 25.1944 | 25.1944
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.2616
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 40.6977
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 109.9377 | 109.9377
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 40.3933
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.22741
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 16.0649
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 25.4101 | 25.4101
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2018
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.825
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 32.1803
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 109.9377 | 109.9377
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 59.5589
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6575
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 26.7221 | 26.7221
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1428
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.8741
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3577
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.825
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91378
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 32.1803
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 109.9377 | 109.9377
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 59.5589
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.22184
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 7.3473
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6575
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 26.7221 | 26.7221
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1428
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.8741
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3577
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.825
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91378
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 109.9377 | 109.9377
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 25.4451 | 25.4451
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 39.6977
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 109.9377 | 109.9377
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 42.4078
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.22547
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 15.0413
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.049716 | 0.049716
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 25.4451 | 25.4451
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2002
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.825
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 85989.4922 | 85989.4922
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 114.4249 | 114.4249
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 25.2228 | 25.2228
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 48.0609
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 114.4249 | 114.4249
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 29.6329
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.23067
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 23.6026
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6575
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.051746 | 0.051746
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 25.2228 | 25.2228
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2602
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.8741
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3577
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029447
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.825
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91378
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 89499.2656 | 89499.2656
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 6.297 | 6.297
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 252.8501 | 252.8501
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.5596 | 1.5596
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.171 | 7.171
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2962.6248 | 2962.6248
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 415.1362 | 415.1362
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.0983 | 1.0983
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.6517 | 2.6517
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.1192 | 2.1192
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039327 | 0.039327
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8259e-05 | 1.8259e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 6.36 | 6.36
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.2648 | 226.2648
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.4037 | 1.4037
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.0559 | 7.0559
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2905.8972 | 2905.8972
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 358.4086 | 358.4086
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0708 | 1.0708
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.8369 | 2.8369
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1638 | 2.1638
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.03687 | 0.03687
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7141e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 96.1447 | 96.1447
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0033 | 436.0033
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 408.2104 | 408.2104
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.3927 | 6.3927
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3209.927 | 3209.927
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 662.4385 | 662.4385
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.356 | 1.356
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 33.0945 | 33.0945
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.7502 | 2.7502
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.068933 | 0.068933
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.6095e-05 | 2.6095e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 29.2416
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 7559.2622 | 7559.2622
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13137
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 995.916
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 108.5314 | 108.5314
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.015 | 303.015
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 388.6693 | 388.6693
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2745 | 3.2745
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1359.2158 | 1359.2158
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1188.2727 | -1188.2727
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.067129 | -0.067129
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 710.3107 | 710.3107
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 5.7521 | 5.7521
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.54437 | 0.54437
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.5499e-05 | 8.5499e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 7559.2622 | 7559.2622
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 29.2957
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 7559.2622 | 7559.2622
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20507
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 995.9927
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 118.2992 | 118.2992
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 226.1392 | 226.1392
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 388.6693 | 388.6693
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.5571 | 2.5571
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 974.4664 | 974.4664
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1573.0221 | -1573.0221
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.42326 | -0.42326
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 840.5917 | 840.5917
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5809 | 4.5809
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65273 | 0.65273
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.0001199 | 0.0001199
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 409.1796 | 409.1796
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.031068 | 0.031068
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 56.9378 | 56.9378
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 88.0061 | 88.0061
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 537.116 | 537.116
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 408.2104 | 408.2104
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.7896 | 6.7896
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.5289 | 1.5289
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 24.9721 | 24.9721
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.4395 | 2.4395
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.078328 | 0.078328
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.0414e-05 | 3.0414e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 120.3095 | 120.3095
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 158.077 | 158.077
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 388.6693 | 388.6693
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 673.9968 | 673.9968
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1873.4917 | -1873.4917
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.68654 | -0.68654
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.9666 | 915.9666
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 2.18 | 2.18
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 128.3819 | 128.3819
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 1.3769 | 1.3769
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.1277 | 7.1277
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2721.9922 | 2721.9922
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 174.5037 | 174.5037
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0054 | 1.0054
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 1.2053 | 1.2053
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027674 | 0.027674
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.3288e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 27.68 | 27.68
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 390.2057 | 390.2057
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 407.239 | 407.239
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 6.9316 | 6.9316
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3213.314 | 3213.314
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 665.8253 | 665.8253
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.226 | 1.226
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 9.4125 | 9.4125
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2522 | 2.2522
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.056038 | 0.056038
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3979e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 27.68 | 27.68
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 390.2057 | 390.2057
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 389.0559 | 389.0559
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 6.9316 | 6.9316
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3213.314 | 3213.314
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 665.8253 | 665.8253
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.226 | 1.226
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 9.4125 | 9.4125
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2522 | 2.2522
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.056038 | 0.056038
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3979e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 27.68 | 27.68
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 390.2057 | 390.2057
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 18.1831 | 18.1831
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 6.9316 | 6.9316
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3213.314 | 3213.314
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 665.8253 | 665.8253
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.226 | 1.226
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 9.4125 | 9.4125
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2522 | 2.2522
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.056038 | 0.056038
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3979e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 18.75 | 18.75
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 344.0994 | 344.0994
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 389.0559 | 389.0559
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 6.9701 | 6.9701
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3127.1702 | 3127.1702
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 579.6817 | 579.6817
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1735 | 1.1735
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 6.822 | 6.822
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.2172 | 2.2172
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.050151 | 0.050151
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.2027e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 18.75 | 18.75
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 344.0994 | 344.0994
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 30.6719 | 30.6719
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 6.9701 | 6.9701
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3127.1702 | 3127.1702
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 579.6817 | 579.6817
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1735 | 1.1735
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 6.822 | 6.822
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.2172 | 2.2172
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.050151 | 0.050151
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.2027e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 18.75 | 18.75
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 344.0994 | 344.0994
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 358.384 | 358.384
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 6.9701 | 6.9701
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3127.1702 | 3127.1702
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 579.6817 | 579.6817
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1735 | 1.1735
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 6.822 | 6.822
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.2172 | 2.2172
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.050151 | 0.050151
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.2027e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 29.2416
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 7559.2622 | 7559.2622
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13137
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 995.916
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 6.297 | 6.297
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 225.6743 | 225.6743
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.4037 | 1.4037
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.0583 | 7.0583
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2904.8972 | 2904.8972
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 357.4087 | 357.4087
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0705 | 1.0705
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.8117 | 2.8117
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1626 | 2.1626
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.036804 | 0.036804
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7117e-05 | 1.7117e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 6.36 | 6.36
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.2648 | 226.2648
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 356.9803 | 356.9803
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.0559 | 7.0559
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2905.8972 | 2905.8972
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 358.4086 | 358.4086
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0708 | 1.0708
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.8369 | 2.8369
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1638 | 2.1638
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.03687 | 0.03687
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7141e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 204.5898 | 204.5898
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.031068 | 0.031068
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 56.9378 | 56.9378
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 6.297 | 6.297
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 499.6052 | 499.6052
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.15596 | 0.15596
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 7.9802 | 7.9802
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.3481 | 1.3481
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.7742 | 1.7742
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1496 | 2.1496
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067265 | 0.067265
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8572e-05 | 2.8572e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.3137 | 1.3137
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 78.9798 | 78.9798
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 48.0353 | 48.0353
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.0632 | 1.0632
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 330.7401 | 330.7401
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2216.7485 | -2216.7485
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.053513 | -0.053513
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 972.4866 | 972.4866
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1953 | 4.1953
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66687 | 0.66687
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00035937 | 0.00035937
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.5519 | 6.5519
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 73.3808 | 73.3808
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 358.765 | 358.765
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.99568 | 0.99568
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 307.6902 | 307.6902
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2239.7983 | -2239.7983
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.18218 | -0.18218
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 976.0994 | 976.0994
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1903 | 4.1903
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.6631 | 0.6631
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00038637 | 0.00038637
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.031068 | 0.031068
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 56.9378 | 56.9378
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 16.894 | 16.894
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 164.6357 | 164.6357
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 48.855 | 48.855
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9877 | 1.9877
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 696.2256 | 696.2256
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1851.2629 | -1851.2629
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.09059 | -0.09059
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 903.515 | 903.515
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3491 | 4.3491
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68174 | 0.68174
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016472 | 0.00016472
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 5.5 | 5.5
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 211.9436 | 211.9436
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 356.9803 | 356.9803
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.0665 | 7.0665
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2879.03 | 2879.03
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 331.5415 | 331.5415
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0604 | 1.0604
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.5238 | 2.5238
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1585 | 2.1585
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035418 | 0.035418
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6561e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 5.5 | 5.5
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 211.9436 | 211.9436
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 19.3783 | 19.3783
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.0665 | 7.0665
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2879.03 | 2879.03
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 331.5415 | 331.5415
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0604 | 1.0604
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.5238 | 2.5238
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1585 | 2.1585
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035418 | 0.035418
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6561e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 5.5 | 5.5
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 211.9436 | 211.9436
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 337.602 | 337.602
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.0665 | 7.0665
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2879.03 | 2879.03
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 331.5415 | 331.5415
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0604 | 1.0604
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.5238 | 2.5238
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1585 | 2.1585
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035418 | 0.035418
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6561e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 2.18 | 2.18
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 128.3819 | 128.3819
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 337.602 | 337.602
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.1277 | 7.1277
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2721.9922 | 2721.9922
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 174.5037 | 174.5037
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0054 | 1.0054
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 1.2053 | 1.2053
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027674 | 0.027674
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.3288e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 2.18 | 2.18
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 128.3819 | 128.3819
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 9.4889 | 9.4889
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.1277 | 7.1277
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2721.9922 | 2721.9922
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 174.5037 | 174.5037
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0054 | 1.0054
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 1.2053 | 1.2053
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027674 | 0.027674
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.3288e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 2.1373 | 2.1373
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 111.026 | 111.026
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 28.8672 | 28.8672
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.4299 | 1.4299
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 465.7306 | 465.7306
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2081.7578 | -2081.7578
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.021831 | -0.021831
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 950.2326 | 950.2326
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2299 | 4.2299
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68216 | 0.68216
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00025247 | 0.00025247
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.1382 | 6.1382
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 105.4201 | 105.4201
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 358.765 | 358.765
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3675 | 1.3675
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 442.3387 | 442.3387
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2105.1499 | -2105.1499
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.11141 | -0.11141
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 954.6662 | 954.6662
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2211 | 4.2211
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68065 | 0.68065
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00026696 | 0.00026696
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.3108 | 5.3108
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 150.0223 | 150.0223
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 358.765 | 358.765
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8421 | 1.8421
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 632.2855 | 632.2855
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1915.203 | -1915.203
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.0084685 | -0.0084685
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 917.0516 | 917.0516
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3096 | 4.3096
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68443 | 0.68443
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018197 | 0.00018197
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 204.5898 | 204.5898
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.031068 | 0.031068
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 56.9378 | 56.9378
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.423 | 45.423
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 358.765 | 358.765
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64416 | 0.64416
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.1835 | 190.1835
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.3052 | -2357.3052
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061053 | -0.061053
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0591 | 990.0591
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63578 | 0.63578
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059101 | 0.00059101
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3792 | 7.3792
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5004 | 45.5004
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 358.765 | 358.765
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64488 | 0.64488
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1157 | 191.1157
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3728 | -2356.3728
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.25036 | -0.25036
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3279 | 990.3279
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63623 | 0.63623
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059029 | 0.00059029
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.3922 | 5.3922
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 211.2392 | 211.2392
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 19.3783 | 19.3783
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.0734 | 7.0734
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2878.03 | 2878.03
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 330.5416 | 330.5416
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0603 | 1.0603
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.4769 | 2.4769
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1553 | 2.1553
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.035331 | 0.035331
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6534e-05 | 1.6534e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 5.3922 | 5.3922
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 125.9456 | 125.9456
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 19.3783 | 19.3783
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5913 | 1.5913
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 529.2431 | 529.2431
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2018.2455 | -2018.2455
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.058768 | -0.058768
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 938.4268 | 938.4268
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2543 | 4.2543
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68518 | 0.68518
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00022034 | 0.00022034
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.7245 | 5.7245
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 120.3328 | 120.3328
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 358.765 | 358.765
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.5311 | 1.5311
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 505.418 | 505.418
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2042.0706 | -2042.0706
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.075135 | -0.075135
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 943.059 | 943.059
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.244 | 4.244
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68444 | 0.68444
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00023155 | 0.00023155
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 25.0205 | 25.0205
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 211.2493 | 211.2493
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 18.1831 | 18.1831
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.4355 | 2.4355
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 903.6204 | 903.6204
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1643.8682 | -1643.8682
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.031831 | -0.031831
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 851.6813 | 851.6813
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5541 | 4.5541
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.65634 | 0.65634
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012632 | 0.00012632
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 2.18 | 2.18
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 128.3819 | 128.3819
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 326.7362 | 326.7362
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.1277 | 7.1277
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2721.9922 | 2721.9922
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 174.5037 | 174.5037
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0054 | 1.0054
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 1.2053 | 1.2053
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.1223 | 2.1223
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027674 | 0.027674
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.3288e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 108.5314 | 108.5314
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 317.0735 | 317.0735
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 387.7 | 387.7
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.5635 | 5.5635
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2709.3022 | 2709.3022
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 161.8137 | 161.8137
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 61.459 | 61.459
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 7.3549 | 7.3549
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.083797 | 0.083797
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 2.071e-05 | 2.071e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.34 | 1.34
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 107.9986 | 107.9986
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 326.7362 | 326.7362
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.1574 | 7.1574
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2648.6372 | 2648.6372
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 101.1488 | 101.1488
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.98238 | 0.98238
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.79011 | 0.79011
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2257 | 4.2257
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025652 | 0.025652
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2556e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.34 | 1.34
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 107.9986 | 107.9986
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 19.168 | 19.168
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.1574 | 7.1574
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2648.6372 | 2648.6372
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 101.1488 | 101.1488
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.98238 | 0.98238
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.79011 | 0.79011
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2257 | 4.2257
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025652 | 0.025652
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2556e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.34 | 1.34
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 107.9986 | 107.9986
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 307.5682 | 307.5682
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.1574 | 7.1574
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2648.6372 | 2648.6372
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 101.1488 | 101.1488
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.98238 | 0.98238
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.79011 | 0.79011
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2257 | 4.2257
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025652 | 0.025652
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2556e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.4 | 0.4
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 75.8568 | 75.8568
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 307.5682 | 307.5682
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.2351 | 7.2351
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2484.623 | 2484.623
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -62.8655 | -62.8655
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.93469 | 0.93469
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.26794 | 0.26794
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1933 | 4.1933
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022502 | 0.022502
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.146e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.4 | 0.4
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 75.8568 | 75.8568
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 15.2987 | 15.2987
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.2963 | 7.2963
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2505.9863 | 2505.9863
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -41.5023 | -41.5023
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.9439 | 0.9439
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.26532 | 0.26532
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1933 | 4.1933
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022502 | 0.022502
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.146e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.4 | 0.4
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 75.8568 | 75.8568
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 293.6464 | 293.6464
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.2351 | 7.2351
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2484.623 | 2484.623
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -62.8655 | -62.8655
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.93469 | 0.93469
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.26794 | 0.26794
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1933 | 4.1933
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022502 | 0.022502
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.146e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 357.6548 | 357.6548
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 119.8959 | 119.8959
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 204.2087 | 204.2087
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 388.6693 | 388.6693
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.3541 | 2.3541
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 875.459 | 875.459
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1672.0295 | -1672.0295
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.51506 | -0.51506
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 867.5713 | 867.5713
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4589 | 4.4589
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.67012 | 0.67012
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013328 | 0.00013328
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 39.3118
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 15118.5244 | 15118.5244
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.56313
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 164.8359
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2382.6526
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.17681
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 992.599
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1779
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62836
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006607
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 29.2957
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 15118.5244 | 15118.5244
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.42698
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 122.9913
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2424.4973
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20507
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 995.9927
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.1777
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61462
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00080843
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 27.1373 | 27.1373
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 389.3419 | 389.3419
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 18.1831 | 18.1831
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 6.9389 | 6.9389
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3212.314 | 3212.314
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 664.8254 | 664.8254
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.225 | 1.225
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 9.2342 | 9.2342
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.2484 | 2.2484
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055887 | 0.055887
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3943e-05 | 2.3943e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 18.3824 | 18.3824
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 343.2908 | 343.2908
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 30.6719 | 30.6719
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 6.9773 | 6.9773
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3126.1704 | 3126.1704
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 578.6818 | 578.6818
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1729 | 1.1729
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 6.6933 | 6.6933
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.2138 | 2.2138
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.050024 | 0.050024
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1995e-05 | 2.1995e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 2.1373 | 2.1373
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 127.7141 | 127.7141
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 9.4889 | 9.4889
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.1341 | 7.1341
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2720.9922 | 2720.9922
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 173.5037 | 173.5037
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0053 | 1.0053
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 1.1832 | 1.1832
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.1192 | 2.1192
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027599 | 0.027599
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3264e-05 | 1.3264e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.3137 | 1.3137
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 107.4171 | 107.4171
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 19.168 | 19.168
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.1636 | 7.1636
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2647.6375 | 2647.6375
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 100.1488 | 100.1488
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98235 | 0.98235
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.77564 | 0.77564
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2249 | 4.2249
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.02559 | 0.02559
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2536e-05 | 1.2536e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.39216 | 0.39216
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 75.3816 | 75.3816
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 15.2987 | 15.2987
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.302 | 7.302
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2504.9863 | 2504.9863
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -42.5022 | -42.5022
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.94384 | 0.94384
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.26046 | 0.26046
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.193 | 4.193
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022459 | 0.022459
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1444e-05 | 1.1444e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 496.5145 | 496.5145
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.43663 | 0.43663
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6317 | 9.6317
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3714 | 1.3714
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049274 | 0.049274
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1272 | 2.1272
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066464 | 0.066464
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8439e-05 | 2.8439e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 120.3095 | 120.3095
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 158.077 | 158.077
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 204.5898 | 204.5898
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 673.9966 | 673.9966
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1873.4919 | -1873.4919
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.68654 | -0.68654
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.9666 | 915.9666
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 86.45 | 86.45
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 536.4592 | 536.4592
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 407.6178 | 407.6178
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.7974 | 6.7974
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.5235 | 1.5235
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 24.528 | 24.528
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.4341 | 2.4341
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.078111 | 0.078111
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.0377e-05 | 3.0377e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 120.3095 | 120.3095
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 158.077 | 158.077
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 20.5104 | 20.5104
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 673.9968 | 673.9968
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1873.4917 | -1873.4917
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.68654 | -0.68654
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.9666 | 915.9666
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9655 | 6.9655
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4533 | 46.4533
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 358.765 | 358.765
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65737 | 0.65737
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0623 | 195.0623
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.4263 | -2352.4263
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24257 | -0.24257
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9049 | 989.9049
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63733 | 0.63733
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058054 | 0.00058054
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 6.36 | 6.36
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.2648 | 226.2648
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 358.384 | 358.384
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.0559 | 7.0559
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2905.8972 | 2905.8972
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 358.4086 | 358.4086
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0708 | 1.0708
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.8369 | 2.8369
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1638 | 2.1638
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.03687 | 0.03687
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7141e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.1018 | 52.1018
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 63.7705 | 63.7705
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73089 | 0.73089
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.0898 | 218.0898
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.3987 | -2329.3987
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090313 | -0.0090313
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.084 | 987.084
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.64331 | 0.64331
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00052776 | 0.00052776
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.39216 | 0.39216
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.062 | 52.062
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 63.3339 | 63.3339
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73037 | 0.73037
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9421 | 217.9421
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5464 | -2329.5464
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.042088 | -0.042088
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1121 | 987.1121
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64327 | 0.64327
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052811 | 0.00052811
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 293.8842 | 293.8842
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.3819 | 7.3819
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2337.2493 | 2337.2493
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -210.2394 | -210.2394
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.89714 | 0.89714
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.074908 | 0.074908
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.4 | 0.4
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 75.8568 | 75.8568
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 13.9218 | 13.9218
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.2351 | 7.2351
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2484.623 | 2484.623
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -62.8655 | -62.8655
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.93469 | 0.93469
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.26794 | 0.26794
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1933 | 4.1933
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022502 | 0.022502
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.146e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.43663 | 0.43663
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 120.3095 | 120.3095
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 158.077 | 158.077
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 204.5898 | 204.5898
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 673.9966 | 673.9966
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1873.4919 | -1873.4919
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.68654 | -0.68654
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.9666 | 915.9666
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 120.3095 | 120.3095
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 158.077 | 158.077
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 10.2577 | 10.2577
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 673.9968 | 673.9968
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1873.4917 | -1873.4917
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.68654 | -0.68654
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.9666 | 915.9666
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 120.3095 | 120.3095
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 158.077 | 158.077
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 204.5898 | 204.5898
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 673.9966 | 673.9966
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1873.4919 | -1873.4919
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.68654 | -0.68654
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.9666 | 915.9666
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 120.3095 | 120.3095
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 158.077 | 158.077
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 409.1796 | 409.1796
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 673.9968 | 673.9968
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1873.4917 | -1873.4917
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.68654 | -0.68654
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.9666 | 915.9666
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 120.3095 | 120.3095
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 158.077 | 158.077
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 204.5898 | 204.5898
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 673.9966 | 673.9966
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1873.4919 | -1873.4919
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.68654 | -0.68654
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.9666 | 915.9666
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 120.3095 | 120.3095
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.1979 | 152.1979
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8515 | 1.8515
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.70767 | -0.70767
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 921.4484 | 921.4484
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.2799 | 4.2799
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.6917 | 0.6917
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018204 | 0.00018204
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 120.3095 | 120.3095
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.1979 | 152.1979
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8515 | 1.8515
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.70767 | -0.70767
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 921.4484 | 921.4484
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.2799 | 4.2799
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.6917 | 0.6917
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018204 | 0.00018204
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 96.1447 | 96.1447
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0024 | 460.0024
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 397.9526 | 397.9526
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.4834 | 6.4834
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3275.2939 | 3275.2939
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 727.8054 | 727.8054
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.4048 | 1.4048
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 31.4686 | 31.4686
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.6386 | 2.6386
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.071012 | 0.071012
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7152e-05 | 2.7152e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 204.5898 | 204.5898
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.031068 | 0.031068
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 56.9378 | 56.9378
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 204.5898 | 204.5898
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.031068 | 0.031068
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 56.9378 | 56.9378
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.031068 | 0.031068
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 56.9378 | 56.9378
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 29.2416
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 15118.5244 | 15118.5244
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.42629
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 122.5733
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2424.9153
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13137
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 995.916
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61443
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00080939
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 86.45 | 86.45
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 536.4592 | 536.4592
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 408.2104 | 408.2104
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.7974 | 6.7974
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.5235 | 1.5235
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 24.528 | 24.528
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.4341 | 2.4341
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.078111 | 0.078111
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.0377e-05 | 3.0377e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 119.4822 | 119.4822
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 228.0941 | 228.0941
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 388.6693 | 388.6693
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5748 | 2.5748
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 983.4664 | 983.4664
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1564.0221 | -1564.0221
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.42236 | -0.42236
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 838.1572 | 838.1572
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5927 | 4.5927
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65107 | 0.65107
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00011886 | 0.00011886
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 98.0676 | 98.0676
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5042 | 411.5042
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 397.9526 | 397.9526
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.2789 | 6.2789
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3136.2087 | 3136.2087
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 588.7203 | 588.7203
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.3063 | 1.3063
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 35.865 | 35.865
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.9442 | 2.9442
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.06752 | 0.06752
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.501e-05 | 2.501e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 120.3095 | 120.3095
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 158.077 | 158.077
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 10.2526 | 10.2526
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.9103 | 1.9103
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 673.9968 | 673.9968
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1873.4917 | -1873.4917
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.68654 | -0.68654
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.9666 | 915.9666
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2948 | 4.2948
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.69063 | 0.69063
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017476
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 106.4033 | 106.4033
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 338.9837 | 338.9837
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 387.7 | 387.7
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.806 | 5.806
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2851.1492 | 2851.1492
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 303.6606 | 303.6606
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1077 | 1.1077
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 51.2262 | 51.2262
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 4.8821 | 4.8821
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.073185 | 0.073185
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1709e-05 | 2.1709e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 108.5314 | 108.5314
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 317.0735 | 317.0735
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 387.7 | 387.7
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.5635 | 5.5635
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2709.3022 | 2709.3022
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 161.8137 | 161.8137
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 61.459 | 61.459
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 7.3549 | 7.3549
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.083797 | 0.083797
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.071e-05 | 2.071e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 98.0676 | 98.0676
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.1031 | 434.1031
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 387.7 | 387.7
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.3725 | 6.3725
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3201.3213 | 3201.3213
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 653.8326 | 653.8326
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3553 | 1.3553
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 33.9954 | 33.9954
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.7807 | 2.7807
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.06906 | 0.06906
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.602e-05 | 2.602e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 88.2061 | 88.2061
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 537.2003 | 537.2003
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 408.2104 | 408.2104
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.7886 | 6.7886
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3482.1716 | 3482.1716
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 934.6831 | 934.6831
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.5296 | 1.5296
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 25.0292 | 25.0292
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.4402 | 2.4402
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.078355 | 0.078355
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0418e-05 | 3.0418e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 118.2992 | 118.2992
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 226.1392 | 226.1392
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 388.6693 | 388.6693
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.5571 | 2.5571
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 974.4664 | 974.4664
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1573.0221 | -1573.0221
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.42326 | -0.42326
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 840.5917 | 840.5917
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5809 | 4.5809
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65273 | 0.65273
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.0001199 | 0.0001199
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 73.3954 | 73.3954
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15181.7607
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15162.0674
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 6.9687
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 309123.0938 | 309123.0938
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 341436.5625 | 341436.5625
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 40.05
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 10.41
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3

## Eng_Info
Power Out | 110 | MW
Turbine Pressure
Load | Power | Range | Elink | HP | 100% Case (bara) |  | 75% Case (bara) |  | 50% Case (bara) |  | Power (MW) | Ps (bara) | Ts ( C ) | Ms' ( tph ) | FEGT ( C ) | Stack ( C ) | 75% Case (bara)
50% | 55 | 55 - <70 | ELINK (3) | Main steam (1st stage) | 86.13 |  | 79.5825 |  | 71.3475 |  | 55 | 71.3475 | 530.798 | 200.5 | 857 | 149.3 | 86.15
75% | 82.5 | 70 - 93 | ELINK (2) | 2nd Stage | 27.68 | 0.32137 | 25.5758 | 0.32137 | 22.9293 | 0.32137 | 85 | 79.5825 | 533.906 |  |  |  | 20.83 | 0.24179
100% | 110 | >93 - 110 | ELINK | 3rd Stage | 18.48 | 0.21456 | 17.0752 | 0.21456 | 15.3083 | 0.21456 | 110 | 86.445 | 536.496 | 387.7 | 894 | 148.2 | 14.24 | 0.16529
Full Load | 110 | MW |  | 4th Stage | 6.36 | 0.073842 | 5.8765 | 0.073842 | 5.2684 | 0.073842 | [6 empty] | 5.244 | 0.060871
|  |  |  | 5th Stage | 5.5 | 0.063857 | 5.0819 | 0.063857 | 4.556 | 0.063857 | [6 empty] | 4.2 | 0.048752
|  | 61.5 |  | LP
|  |  |  | 6th Stage | 2.18 | 0.025311 | 2.0143 | 0.025311 | 1.8058 | 0.025311 | [6 empty] | 2.18 | 0.025305
|  | 55 |  | 7th Stage | 1.34 | 0.015558 | 1.2381 | 0.015558 | 1.11 | 0.015558 | [6 empty] | 1.34 | 0.015554
|  | 18.3333 |  | 8th Stage | 0.4 | 0.0046441 | 0.36959 | 0.0046441 | 0.33135 | 0.0046441 | [6 empty] | 0.4 | 0.0046431
[11 empty] | Pw | Ps
HHV Fuel | kJ/kg | [9 empty] | 55 | 71.35 |  | 85 | 79.5825
100% | 15026 | 3588.8984 | [8 empty] | 110 | 86.45
75% | 14599 | 3486.9112
50% | 15332 | 3661.9853
[11 empty] | Pw | Ts
| Trial Fuel | [9 empty] | 55 | 530.8 |  | 85 | 533.906
| 3600 | 15072.48 | [8 empty] | 110 | 536.5
| 4000 | 16747.2
[11 empty] | Pw | Ms | DSH
[11 empty] | 55 | 210 | 9.8 | 85 | 317.7795
[11 empty] | 110 | 407.6 | 20.5
[11 empty] | Pw | Ms'-20
[11 empty] | 55 | 200.5 |  | 85 | 302.606
[11 empty] | 110 | 387.7
[11 empty] | Pw | FEGT
[11 empty] | 55 | 857 |  | 85 | 877.1795
[11 empty] | 110 | 894

## input
Expected Output Power |  | 110 | MW
Group | Status | Parameters | Unit | short_name | Baris (New) | Notes | min | max | Value
Generator | view | Generator Power Factor |  | generator_power_factor | E388 |  | 0.75 | 0.95 | 0.9 | 1
Boiler | view | Desired Coal HHV (kJ/kg) | kcal/kg | desired_coal_hhv | E181 |  | 3375 | 4775 | 16747 | 1
Boiler | view | Total Moisture (% wg) | % | total_moisture | E173 |  | 25 | 45 | 30 | 1
Boiler | view | Main Steam Temp. | C | main_steam_temp | E296 |  | 510 | 538 | 537.196
Boiler | view | Saturated Steam Mass Flow | ton/h | sat_steam_mass_flow | E21 |  | 345 | 1175 | 387.696
Boiler | view | Main Steam Press. | bara | main_steam_press | E391 |  | 60 | 167 | 86.445
Boiler | view | Excess Air | % |  | E24 |  | 15 | 40 | 25 | 1
Ambient Condition | view | Ambient Temperature ( C ) | C |  | E17 |  | 25 | 33 | 30 | 1
Ambient Condition | view | Relative Humidity (%) | % |  | E18 |  | 60 | 80 | 75 | 1
Ambient Condition | view | Ambient Pressure (bar) | bar |  | E20 |  | 1.0123 | 1.0132 | 1.0124 | 1
Boiler | background input | FEGT | C | fegt | E23 | Korelasi formula dari main steam press |  |  | 893.997
Turbine | background input | 2nd Stage | bar | hp_turbine2_in | E400 | Korelasi formula dari main steam press |  |  | 27.7808
Turbine | background input | 3rd Stage | bar | hp_turbine3_in | E409 | Korelasi formula dari main steam press |  |  | 18.5476
Turbine | background input | 4th Stage | bar | hp_turbine4_in | E418 | Korelasi formula dari main steam press |  |  | 6.3831
Turbine | background input | 5th Stage | bar | hp_turbine5_in | E427 | Korelasi formula dari main steam press |  |  | 5.5195
Turbine | background input | 6th Stage | bar | lp_turbine1_in | E436 | Korelasi formula dari main steam press |  |  | 2.1879
Turbine | background input | 7th Stage | bar | lp_turbine2_in | E445 | Korelasi formula dari main steam press |  |  | 1.3449
Turbine | background input | 8th Stage | bar | lp_turbine3_in | E454 | Korelasi formula dari main steam press |  |  | 0.40145
Condenser | View | Water Coling Inlet Temp |  |  | E348 |  |  |  | 27.3 | 1
Condenser | View | Cooling Temp. Rise |  |  | E355 |  |  |  | 10 | 1
Note on F5: Adhy Marwanto: di konversi ke kJ/kg ketika di inject ke thermoflow. kali dengan 4.1868
Note on M5: Adhy Marwanto: input from what if sim. This default value is just tracing back value from the default modelling coal HHV.
Note on H8: Adhy Marwanto: steam production rate (from furnace / saturated steam)

## output
CODE | Drawing | Show at View | Param Type | Param Group |  | Unit |  | Ref | Value | Cell Address | Param Name | Baseline Value
1 | N/A |  | output | Generator | Generator Power Factor |  | generator_power_factor | E1610 | 0.9 |  | #REF! | #REF!
2 |  |  | output | Generator | Gross Power Output | kW | gross_power_output | E470 | 55563.4844 |  | #REF! | #REF!
3 | N/A |  | output | Generator | Auxiliary Power consumption | kW | auxiliary_power_consumption | E473 | 5227.2949 |  | #REF! | #REF!
4 | D31 |  | output | Boiler | Coal HHV | kJ/kg | desired_coal_hhv | E1019 | 16747 |  | #REF! | #REF!
5 | D53 | 1 | output | Generator | Gross Output | kW | gross_output | E470 | 55563.4844 |  | #REF! | #REF!
6 |  |  | output | Boiler | Boiler Efficiency | % | boiler_efficiency | E475 | 34.8285 |  | #REF! | #REF!
7 | N/A | 1 | output | Generator | Net Output | kW | net_output | E471 | 50058.3711 |  | #REF! | #REF!
8 | N/A | 1 | output | Boiler | Net Heatrate (HHV) | kcal/kWh | net_heatrate | E484 | 12672.4102 |  | #REF! | #REF!
9 | N/A | 1 | output | Plant | Gross Heatrate (LHV) | kcal/kWh | gross_heatrate | E476 | 10336.3652 |  | #REF! | #REF!
10 | N/A |  | output | Plant | Plant Efficiency (HHV) | kcal/kWh | plant_efficiency | E481 | 31.3778 |  | #REF! | #REF!
11 | N/A |  | output | Boiler | SSH Steam Outlet Temperature | C | ssh_steam_outlet_temperature | E1475 | 531.4 |  | #REF! | #REF!
12 | N/A |  | output | Boiler | SSH Steam Outlet Pressure | MPa | ssh_steam_outlet_pressure | E1474 | 7.2834 |  | #REF! | #REF!
13 | N/A |  | output | Boiler | SSH Steam Outlet Flow | t/h | ssh_steam_outlet_flow | E1473 | 210.3333 |  | #REF! | #REF!
14 | D41 |  | output | Boiler | Main Steam Inlet Temperature | C | main_steam_inlet_temperature | E3238 | 530.7554 |  | #REF! | #REF!
15 | D42 |  | output | Boiler | Main Steam Inlet Pressure | MPa | main_steam_inlet_pressure | E3237 | 7.135 |  | #REF! | #REF!
16 | D40 |  | output | Boiler | Main Steam Inlet Flow | t/h | main_steam_inlet_flow | E3239 | 209.9458 |  | #REF! | #REF!
17 | D51 |  | output | Turbine | LP ST Steam Inlet Temperature | C | lp_st_steam_inlet_temperature | E3029 | 129.6388 |  | #REF! | #REF!
18 | D52 |  | output | Turbine | LP ST Steam Inlet Pressure | MPa | lp_st_steam_inlet_pressure | E3028 | 0.1806 |  | #REF! | #REF!
19 | D50 |  | output | Turbine | LP ST Steam Inlet Flow | t/h | lp_st_steam_inlet_flow | E3030 | 168.5928 |  | #REF! | #REF!
20 | D20 |  | output | Condenser | Cond. CW Flow | t/h | cond_cw_flow | E3459 | 7987.0059 |  | #REF! | #REF!
21 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff1 | E1663 | 72.7786 |  | #REF! | #REF!
22 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff2 | E1690 | 77.431 |  | #REF! | #REF!
23 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff3 | E1717 | 81.94 |  | #REF! | #REF!
24 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff4 | E1744 | 82.971 |  | #REF! | #REF!
25 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff5 | E1771 | 85.2419 |  | #REF! | #REF!
26 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff1 | E1798 | 84.8771 |  | #REF! | #REF!
27 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff2 | E1825 | 86.8568 |  | #REF! | #REF!
28 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff3 | E1857 | 86.8102 |  | #REF! | #REF!
29 | D11 |  | output | FWH1 | FWH1 Terminal Temperature Difference | C | fwh1_terminal_temperature_difference | E997 | -3.7725 |  | #REF! | #REF!
30 | D09 |  | output | FWH2 | FWH2 Terminal Temperature Difference | C | fwh2_terminal_temperature_difference | E979 | -0.19001 |  | #REF! | #REF!
31 | D07 |  | output | Condensate | FWH4 Terminal Temperature Difference | C | fwh4_terminal_temperature_difference | E961 | 0.19775 |  | #REF! | #REF!
32 | D05 |  | output | Condensate | FWH5 Terminal Temperature Difference | C | fwh5_terminal_temperature_difference | E943 | 2 |  | #REF! | #REF!
33 | D03 |  | output | Condensate | FWH6 Terminal Temperature Difference | C | fwh6_terminal_temperature_difference | E926 | 2 |  | #REF! | #REF!
34 | D01 |  | output | Condensate | FWH7 Terminal Temperature Difference | C | fwh7_terminal_temperature_difference | E909 | 2 |  | #REF! | #REF!
35 | D12 |  | output | FWH1 | FWH1 Drain Cooler Approach | C | fwh1_drain_cooler_approach | E998 | 7.041 |  | #REF! | #REF!
36 | D10 |  | output | FWH2 | FWH2 Drain Cooler Approach | C | fwh2_drain_cooler_approach | E980 | 6.536 |  | #REF! | #REF!
37 | D08 |  | output | Condensate | FWH4 Drain Cooler Approach | C | fwh4_drain_cooler_approach | E962 | 5.6 |  | #REF! | #REF!
38 | D06 |  | output | Condensate | FWH5 Drain Cooler Approach | C | fwh5_drain_cooler_approach | E944 | 5.6 |  | #REF! | #REF!
39 | D04 |  | output | Condensate | FWH6 Drain Cooler Approach | C | fwh6_drain_cooler_approach | E927 | 5.6 |  | #REF! | #REF!
40 | D02 |  | output | Condensate | FWH7 Drain Cooler Approach | C | fwh7_drain_cooler_approach | E910 | 5.6 |  | #REF! | #REF!
41 | D18 |  | output | Condenser | Cond. Main Steam Inlet Pressure | MPa | cond_main_steam_inlet_pressure | E3303 | 0.00985 |  | #REF! | #REF!
42 | D19 |  | output | Condenser | Cond. Cooling Water Inlet Temperature | C | cond_cooling_water_inlet_temperature | E348 | 29.22 |  | #REF! | #REF!
43 | D21 |  | output | Condenser | Cond. Cooling Water Exit Temperature | C | cond_cooling_water_exit_temperature | E1593 | 39.3118 |  | #REF! | #REF!
44 | D20 |  | output | Condenser | Cond. Cooling Water Inlet Flow | t/h | cond_cooling_water_inlet_flow | E3459 | 7987.0059 |  | #REF! | #REF!
45 | D30 |  | output | Boiler | Coal Flow | t/h | coal_flow | E3569 | 37.8785 |  | #REF! | #REF!
46 | D39 |  | output | Boiler | Stack Temperature | C | stack_temperature | E2297 | 130.4938 |  | #REF! | #REF!
47 | N/A |  | output | Ambient Air | Ambient Pressure | MPa | ambient_pressure | E466 | 0.10124 |  | #REF! | #REF!
48 | N/A |  | output | Ambient Air | Ambient RH | % | ambient_rh | E468 | 59.56 |  | #REF! | #REF!
49 | N/A |  | output | Condenser | Cond. Condensate temperature | C | cond_condensate_temperature | E3117 | 45.5173 |  | #REF! | #REF!
50 | D32 |  | output | Air Preheater | APH Flue gas inlet temperature | C | aph_flue_gas_inlet_temperature | E2027 | 264.9479 |  | #REF! | #REF!
51 | D36 |  | output | Air Preheater | SA Outlet Temp. | C | sa_outlet_temp | E2189 | 214.6979 |  | #REF! | #REF!
52 | D34 |  | output | Air Preheater | PA Outlet Temp. | C | pa_outlet_temp | E2108 | 223.0611 |  | #REF! | #REF!
53 | D33 |  |  |  | Flue Gas Outlet Temp | C | flue_gas_outlet_temp | E1919 | 126.1789 |  | #REF! | #REF!
54 | D37 |  |  |  | SA Inlet Temp | C | sa_inlet_temp | E2216 | 39.6977 |  | #REF! | #REF!
55 | D35 |  |  |  | PA Inlet Temp | C | pa_inlet_temp | E2135 | 48.0609 |  | #REF! | #REF!
56 | D56 |  |  |  | LP Steam Efficiency | % | lp_steam_efficiency | AVERAGE(J25:J29) | 85.9465 |  | #REF! | #REF!
57 | D57 |  |  |  | HP Steam Efficiency | % | hp_steam_efficiency | AVERAGE(J30:J32) | 75.1048 |  | #REF! | #REF!
58 | D61 |  |  |  | Ambient Temperature | C | ambient_temperature | E17 | 32.18 |  | #REF! | #REF!
59 | D62 |  |  |  | Relative Humidity | % | relative_humidity | E18 | 59.56 |  | #REF! | #REF!
60 | D63 |  |  |  | Ambient Pressure | MPa | ambient_pressure | E2027 | 26.4948 |  | #REF! | #REF!
61 | D15 |  |  |  | Feedwater mass flow | t/h | feedwater_mass_flow | E3481 | 201.0013 |  | #REF! | #REF!
62 | D16 |  |  |  | Feedwater Temperature | C | feedwater_temperature | E3480 | 222.1428 |  | #REF! | #REF!
63 | D17 |  |  |  | Feedwater Pressure | MPa | feedwater_pressure | E3479 | 9.866 |  | #REF! | #REF!
Note on G6: Adhy Marwanto: Yang ditampilkan MW hasil kalkulasi oleh thermoflow, bukan expected. Tampilan dalam MW.
Note on C62: Adhy Marwanto: ketiga item ini tampilkan di drawing posisi di bawah Air Heater.