## ELINK (3)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTAW_What if_50%_RevD.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 6.9 | 6.9 | #N/A | 6.9
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 26.95 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 75.41 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 23.5477 | 23.5477 | #N/A | 23.5477
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
~31~1~7~~-27~ | Deaerator [31] - DAER : Deaerator design pressure | bar | 8.4382 | 8.4382 | #N/A | 8.4382
~31~1~8~~-27~ | Deaerator [31] - DAER : Deaerator outlet temperature @ design | C | 172.6372 | 172.6372 | #N/A | 172.6372
~31~1~5~~-27~ | Deaerator [31] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 12 | 12 | #N/A | 12
~31~1~6~~-27~ | Deaerator [31] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 11 | 11 | #N/A | 11
~67~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Specified outlet temperature | C | 325 | 325 | #N/A | 325
~67~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Specified outlet temperature | C | 418 | 418 | #N/A | 418
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~69~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Specified outlet temperature | C | 515 | 515 | #N/A | 515
~69~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed gas temperature drop | C | 1.1111 | 1.1111 | #N/A | 1.1111
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 317 | 317 | #N/A | 317
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.6181 | 99.6181 | #N/A | 99.6181
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.47994 | 0.47994 | #N/A | 0.47994
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 0 | 0 | #N/A | 0
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 38.6052 | 38.6052 | #N/A | 38.6052
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 14.8653 | 14.8653 | #N/A | 14.8653
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 309.1281 | 309.1281 | #N/A | 309.1281
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 57.2321 | 57.2321 | #N/A | 57.2321
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~66~1~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan design point overall pressure rise | millibar | 3.5334 | 3.5334 | #N/A | 3.5334
91¦~66~1~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~66~1~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~66~1~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~66~1~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~7~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~66~1~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~66~1~16~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss | kW | 0.66453 | 0.66453 | #N/A | 0.66453
91¦~66~1~13~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~66~1~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 149.0425 | 149.0425 | #N/A | 149.0425
91¦~66~1~12~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 3.608 | 3.608 | #N/A | 3.608
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan design point overall pressure rise | millibar | 24.9066 | 24.9066 | #N/A | 24.9066
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss | kW | 1.2618 | 1.2618 | #N/A | 1.2618
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan off-design control damper dP | millibar | 2.0531e-06 | 2.0531e-06 | #N/A | 2.0531e-06
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 40.4145 | 40.4145 | #N/A | 40.4145
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 23.5974 | 23.5974 | #N/A | 23.5974
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~16~1~2~~-38~ | Feedwater Heater [16] - HPH-1 : Design point FW temperature @ heater exit | C | 263.9052 | 263.9052 | #N/A | 263.9052
91¦~16~1~3~~-38~ | Feedwater Heater [16] - HPH-1 : Design point terminal difference | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~4~~-38~ | Feedwater Heater [16] - HPH-1 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~16~1~19~~-38~ | Feedwater Heater [16] - HPH-1 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~16~1~5~~-38~ | Feedwater Heater [16] - HPH-1 : Design point minimum pinch | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~6~~-38~ | Feedwater Heater [16] - HPH-1 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~16~2~2~~-38~ | Feedwater Heater [16] - HPH-1 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~16~1~16~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature @ heater exit at off-design | C | 263.9052 | 263.9052 | #N/A | 263.9052
91¦~16~1~8~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~16~1~9~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~16~1~10~~-38~ | Feedwater Heater [16] - HPH-1 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~16~1~11~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam mass flow | t/h | 35.4831 | 35.4831 | #N/A | 35.4831
91¦~16~1~12~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water mass flow | t/h | 546.162 | 546.162 | #N/A | 546.162
91¦~16~1~13~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of condensing section | kW/C | 2117.6506 | 2117.6506 | #N/A | 2117.6506
91¦~16~1~20~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of drain cooling section | kW/C | 119.951 | 119.951 | #N/A | 119.951
91¦~16~1~21~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~16~1~14~~-38~ | Feedwater Heater [16] - HPH-1 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~16~1~15~~-38~ | Feedwater Heater [16] - HPH-1 : Water-side flow resistance coefficient | m^-4 | 0.0459 | 0.0459 | #N/A | 0.0459
91¦~16~1~17~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~16~1~18~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~2~~-38~ | Feedwater Heater [17] - HPH-2 : Design point FW temperature @ heater exit | C | 234.7775 | 234.7775 | #N/A | 234.7775
91¦~17~1~3~~-38~ | Feedwater Heater [17] - HPH-2 : Design point terminal difference | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~4~~-38~ | Feedwater Heater [17] - HPH-2 : Design point drain cooler approach | C | 5.6 | 5.6 | #N/A | 5.6
91¦~17~1~19~~-38~ | Feedwater Heater [17] - HPH-2 : Design point residual superheat | C | 2.8 | 2.8 | #N/A | 2.8
91¦~17~1~5~~-38~ | Feedwater Heater [17] - HPH-2 : Design point minimum pinch | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~6~~-38~ | Feedwater Heater [17] - HPH-2 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~17~2~2~~-38~ | Feedwater Heater [17] - HPH-2 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~17~1~16~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature @ heater exit at off-design | C | 234.7775 | 234.7775 | #N/A | 234.7775
91¦~17~1~8~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~17~1~9~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~17~1~10~~-38~ | Feedwater Heater [17] - HPH-2 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~17~1~11~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam mass flow | t/h | 74.6765 | 74.6765 | #N/A | 74.6765
91¦~17~1~12~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water mass flow | t/h | 546.162 | 546.162 | #N/A | 546.162
91¦~17~1~13~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of condensing section | kW/C | 3256.9487 | 3256.9487 | #N/A | 3256.9487
91¦~17~1~20~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of drain cooling section | kW/C | 196.5388 | 196.5388 | #N/A | 196.5388
91¦~17~1~21~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~17~1~14~~-38~ | Feedwater Heater [17] - HPH-2 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~17~1~15~~-38~ | Feedwater Heater [17] - HPH-2 : Water-side flow resistance coefficient | m^-4 | 0.046819 | 0.046819 | #N/A | 0.046819
91¦~17~1~17~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~17~1~18~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~24~1~2~~-38~ | Feedwater Heater [24] - HPH-3 : Design point FW temperature @ heater exit | C | 197.7289 | 197.7289 | #N/A | 197.7289
91¦~24~1~3~~-38~ | Feedwater Heater [24] - HPH-3 : Design point terminal difference | C | 0.38 | 0.38 | #N/A | 0.38
91¦~24~1~4~~-38~ | Feedwater Heater [24] - HPH-3 : Design point drain cooler approach | C | 2.5 | 2.5 | #N/A | 2.5
91¦~24~1~19~~-38~ | Feedwater Heater [24] - HPH-3 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~24~1~5~~-38~ | Feedwater Heater [24] - HPH-3 : Design point minimum pinch | C | 0.3 | 0.3 | #N/A | 0.3
91¦~24~1~6~~-38~ | Feedwater Heater [24] - HPH-3 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~24~2~2~~-38~ | Feedwater Heater [24] - HPH-3 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~24~1~16~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature @ heater exit at off-design | C | 197.7289 | 197.7289 | #N/A | 197.7289
91¦~24~1~8~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~24~1~9~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~24~1~10~~-38~ | Feedwater Heater [24] - HPH-3 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~24~1~11~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam mass flow | t/h | 91.145 | 91.145 | #N/A | 91.145
91¦~24~1~12~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water mass flow | t/h | 546.162 | 546.162 | #N/A | 546.162
91¦~24~1~13~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of condensing section | kW/C | 2581.9404 | 2581.9404 | #N/A | 2581.9404
91¦~24~1~20~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of drain cooling section | kW/C | 272.9926 | 272.9926 | #N/A | 272.9926
91¦~24~1~21~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~24~1~14~~-38~ | Feedwater Heater [24] - HPH-3 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~24~1~15~~-38~ | Feedwater Heater [24] - HPH-3 : Water-side flow resistance coefficient | m^-4 | 0.047755 | 0.047755 | #N/A | 0.047755
91¦~24~1~17~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~24~1~18~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~53~1~2~~-38~ | Feedwater Heater [53] - LPH-8 : Design point FW temperature @ heater exit | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~3~~-38~ | Feedwater Heater [53] - LPH-8 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~53~1~4~~-38~ | Feedwater Heater [53] - LPH-8 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~53~1~19~~-38~ | Feedwater Heater [53] - LPH-8 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~53~1~5~~-38~ | Feedwater Heater [53] - LPH-8 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~53~1~6~~-38~ | Feedwater Heater [53] - LPH-8 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~53~2~2~~-38~ | Feedwater Heater [53] - LPH-8 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~53~1~16~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature @ heater exit at off-design | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~8~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~53~1~9~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~53~1~10~~-38~ | Feedwater Heater [53] - LPH-8 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~53~1~11~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam mass flow | t/h | 59.8899 | 59.8899 | #N/A | 59.8899
91¦~53~1~12~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water mass flow | t/h | 427.734 | 427.734 | #N/A | 427.734
91¦~53~1~13~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of condensing section | kW/C | 604.2064 | 604.2064 | #N/A | 604.2064
91¦~53~1~20~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of drain cooling section | kW/C | 154.513 | 154.513 | #N/A | 154.513
91¦~53~1~21~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~53~1~14~~-38~ | Feedwater Heater [53] - LPH-8 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~53~1~15~~-38~ | Feedwater Heater [53] - LPH-8 : Water-side flow resistance coefficient | m^-4 | 0.0049985 | 0.0049985 | #N/A | 0.0049985
91¦~53~1~17~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~53~1~18~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~54~1~2~~-38~ | Feedwater Heater [54] - LPH-7 : Design point FW temperature @ heater exit | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~3~~-38~ | Feedwater Heater [54] - LPH-7 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~54~1~4~~-38~ | Feedwater Heater [54] - LPH-7 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~54~1~19~~-38~ | Feedwater Heater [54] - LPH-7 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~54~1~5~~-38~ | Feedwater Heater [54] - LPH-7 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~54~1~6~~-38~ | Feedwater Heater [54] - LPH-7 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~54~2~2~~-38~ | Feedwater Heater [54] - LPH-7 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~54~1~16~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature @ heater exit at off-design | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~8~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~54~1~9~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~54~1~10~~-38~ | Feedwater Heater [54] - LPH-7 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~54~1~11~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam mass flow | t/h | 49.098 | 49.098 | #N/A | 49.098
91¦~54~1~12~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water mass flow | t/h | 427.734 | 427.734 | #N/A | 427.734
91¦~54~1~13~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of condensing section | kW/C | 753.3429 | 753.3429 | #N/A | 753.3429
91¦~54~1~20~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of drain cooling section | kW/C | 142.6287 | 142.6287 | #N/A | 142.6287
91¦~54~1~21~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~54~1~14~~-38~ | Feedwater Heater [54] - LPH-7 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~54~1~15~~-38~ | Feedwater Heater [54] - LPH-7 : Water-side flow resistance coefficient | m^-4 | 0.0049005 | 0.0049005 | #N/A | 0.0049005
91¦~54~1~17~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~54~1~18~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~55~1~2~~-38~ | Feedwater Heater [55] - LPH-6 : Design point FW temperature @ heater exit | C | 100.493 | 100.493 | #N/A | 100.493
91¦~55~1~3~~-38~ | Feedwater Heater [55] - LPH-6 : Design point terminal difference | C | 5.7 | 5.7 | #N/A | 5.7
91¦~55~1~4~~-38~ | Feedwater Heater [55] - LPH-6 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~55~1~19~~-38~ | Feedwater Heater [55] - LPH-6 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~55~1~5~~-38~ | Feedwater Heater [55] - LPH-6 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~55~1~6~~-38~ | Feedwater Heater [55] - LPH-6 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~55~2~2~~-38~ | Feedwater Heater [55] - LPH-6 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~55~1~16~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature @ heater exit at off-design | C | 100.493 | 100.493 | #N/A | 100.493
91¦~55~1~8~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~55~1~9~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~55~1~10~~-38~ | Feedwater Heater [55] - LPH-6 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~55~1~11~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam mass flow | t/h | 33.5367 | 33.5367 | #N/A | 33.5367
91¦~55~1~12~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water mass flow | t/h | 427.734 | 427.734 | #N/A | 427.734
91¦~55~1~13~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of condensing section | kW/C | 632.3135 | 632.3135 | #N/A | 632.3135
91¦~55~1~20~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of drain cooling section | kW/C | 84.1891 | 84.1891 | #N/A | 84.1891
91¦~55~1~21~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~55~1~14~~-38~ | Feedwater Heater [55] - LPH-6 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~55~1~15~~-38~ | Feedwater Heater [55] - LPH-6 : Water-side flow resistance coefficient | m^-4 | 0.0048044 | 0.0048044 | #N/A | 0.0048044
91¦~55~1~17~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~55~1~18~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~56~1~2~~-38~ | Feedwater Heater [56] - LPH-5 : Design point FW temperature @ heater exit | C | 131.4627 | 131.4627 | #N/A | 131.4627
91¦~56~1~3~~-38~ | Feedwater Heater [56] - LPH-5 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~56~1~4~~-38~ | Feedwater Heater [56] - LPH-5 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~56~1~19~~-38~ | Feedwater Heater [56] - LPH-5 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~56~1~5~~-38~ | Feedwater Heater [56] - LPH-5 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~56~1~6~~-38~ | Feedwater Heater [56] - LPH-5 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~56~2~2~~-38~ | Feedwater Heater [56] - LPH-5 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~56~1~16~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature @ heater exit at off-design | C | 131.4627 | 131.4627 | #N/A | 131.4627
91¦~56~1~8~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~56~1~9~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~56~1~10~~-38~ | Feedwater Heater [56] - LPH-5 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~56~1~11~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam mass flow | t/h | 22.2019 | 22.2019 | #N/A | 22.2019
91¦~56~1~12~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water mass flow | t/h | 427.734 | 427.734 | #N/A | 427.734
91¦~56~1~13~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of condensing section | kW/C | 920.1456 | 920.1456 | #N/A | 920.1456
91¦~56~1~20~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of drain cooling section | kW/C | 69.6455 | 69.6455 | #N/A | 69.6455
91¦~56~1~21~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~56~1~14~~-38~ | Feedwater Heater [56] - LPH-5 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~56~1~15~~-38~ | Feedwater Heater [56] - LPH-5 : Water-side flow resistance coefficient | m^-4 | 0.0047102 | 0.0047102 | #N/A | 0.0047102
91¦~56~1~17~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~56~1~18~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30 | #N/A | 30
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 215 | 215 | #N/A | 215
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100 | #N/A | TJA_Whatif100
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 27.99 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 5.36 | 5.36 | #N/A | 5.36
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 48.63 | 48.63 | #N/A | 48.63
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 3.99 | 3.99 | #N/A | 3.99
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.8 | 0.8 | #N/A | 0.8
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.19 | 0.19 | #N/A | 0.19
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 13.04 | 13.04 | #N/A | 13.04
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 4500 | 4500 | 4500
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 32.75 | 32.75 | #N/A | 32.75
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~7~1~10~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam production rate | t/h | 544.8 | 945.59 | 945.59 | 945.59
91¦~7~1~18~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1131.2 | 1145.33 | 1145.33 | 1145.33
91¦~7~1~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25 | 25 | 25
91¦~7~1~7~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Minor heat loss | % | 3.25 | 3.25 | #N/A | 3.25
91¦~7~1~8~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gage pressure | millibar | -0.62267 | -0.62267 | #N/A | -0.62267
91¦~7~1~6~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Secondary air pressure drop | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
91¦~7~1~39~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | % | 20 | 20 | #N/A | 20
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content (for emission level definition) | % | 5.3 | 5.3 | #N/A | 5.3
91¦~7~1~152~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
91¦~7~1~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit temperature @ design | C | 60.8 | 60.8 | #N/A | 60.8
91¦~7~1~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inlet air/fuel mass ratio in pulverizer @ design |  | 1.8 | 1.8 | #N/A | 1.8
91¦~7~1~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverized fuel fineness @ design | % | 65 | 65 | #N/A | 65
91¦~7~1~8~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Power consumption converted into heat in pulverizer @ design | % | 80 | 80 | #N/A | 80
91¦~7~1~7~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : % of as-received fuel moisture evaporated in pulverizer | % | 60 | 60 | #N/A | 60
91¦~7~1~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pressure drop in pulverizer | millibar | 20 | 20 | #N/A | 20
91¦~7~1~18~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit gauge pressure | millibar | 99.6264 | 99.6264 | #N/A | 99.6264
91¦~7~1~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer nameplate specific power | kWh/tonne | 22.0462 | 22.0462 | #N/A | 22.0462
91¦~3~1~2~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332 | #N/A | 1.0332
91¦~3~1~3~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~3~1~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 695.23 | 695.23 | #N/A | 695.23
91¦~3~1~5~~-1~ | Gas/Air Source [3] - Sec.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~3~1~18~~-1~ | Gas/Air Source [3] - Sec.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~3~1~21~~-1~ | Gas/Air Source [3] - Sec.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~3~1~22~~-1~ | Gas/Air Source [3] - Sec.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~11~1~2~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129 | #N/A | 1.1129
91¦~11~1~3~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~11~1~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 579.01 | 579.01 | #N/A | 579.01
91¦~11~1~5~~-1~ | Gas/Air Source [11] - Prim.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~11~1~18~~-1~ | Gas/Air Source [11] - Prim.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~11~1~21~~-1~ | Gas/Air Source [11] - Prim.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - Prim.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~40~1~12~~-168~ | General Pump [40] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Rating / design point load |  | 1.0212 | 1.0212 | #N/A | 1.0212
91¦~6~1~1~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25 | #N/A | 25
91¦~6~1~2~~-46~ | Makeup / Blowdown [6] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99 | #N/A | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01 | #N/A | 0.01
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3 | #N/A | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7 | #N/A | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989 | #N/A | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011 | #N/A | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761 | #N/A | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239 | #N/A | 0.79239
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~35~1~4~~-107~ | Pipe (PCE) [35] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~35~1~9~~-107~ | Pipe (PCE) [35] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~36~1~4~~-107~ | Pipe (PCE) [36] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~36~1~9~~-107~ | Pipe (PCE) [36] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~37~1~4~~-107~ | Pipe (PCE) [37] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~37~1~9~~-107~ | Pipe (PCE) [37] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~60~1~4~~-107~ | Pipe (PCE) [60] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~60~1~9~~-107~ | Pipe (PCE) [60] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~61~1~4~~-107~ | Pipe (PCE) [61] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~61~1~9~~-107~ | Pipe (PCE) [61] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~63~1~4~~-107~ | Pipe (PCE) [63] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~63~1~9~~-107~ | Pipe (PCE) [63] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~64~1~4~~-107~ | Pipe (PCE) [64] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~64~1~9~~-107~ | Pipe (PCE) [64] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~73~1~4~~-107~ | Pipe (PCE) [73] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~73~1~9~~-107~ | Pipe (PCE) [73] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~74~1~4~~-107~ | Pipe (PCE) [74] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~74~1~9~~-107~ | Pipe (PCE) [74] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~75~1~4~~-107~ | Pipe (PCE) [75] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~75~1~9~~-107~ | Pipe (PCE) [75] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~76~1~4~~-107~ | Pipe (PCE) [76] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~76~1~9~~-107~ | Pipe (PCE) [76] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
83¦91¦~82~1~12~~-100~ | Pump (PCE) [82] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~83~1~12~~-100~ | Pump (PCE) [83] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
91¦~8~1~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air outlet temperature | C | 273.8889 | 273.8889 | #N/A | 273.8889
91¦~8~1~3~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path cold end leakage | % | 7 | 7 | #N/A | 7
91¦~8~1~4~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path hot end leakage | % | 3 | 3 | #N/A | 3
91¦~8~1~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air outlet temperature | C | 343.3334 | 343.3334 | #N/A | 343.3334
91¦~8~1~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air cold end leakage | % | 10 | 10 | #N/A | 10
91¦~8~1~14~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air hot end leakage | % | 5 | 5 | #N/A | 5
91¦~1~1~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump design point overall pressure rise | bar | 152.6129 | 152.6129 | #N/A | 152.6129
91¦~1~1~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~1~1~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Flow margin | % | 10 | 10 | #N/A | 10
91¦~1~1~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~1~1~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Design point RPM |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~1~1~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~1~1~16~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss | kW | 56.4319 | 56.4319 | #N/A | 56.4319
91¦~1~1~13~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~1~1~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal RPM for off-design pump curve |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~11~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal rating flow for off-design pump curve | t/h | 305.0459 | 305.0459 | #N/A | 305.0459
91¦~1~1~12~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal pressure rise for off-design pump curve | bar | 144.5198 | 144.5198 | #N/A | 144.5198
91¦~1~1~2~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 8.607 | 8.607 | #N/A | 8.607
91¦~1~1~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~1~1~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~1~1~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~1~1~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~1~1~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~1~5~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~1~1~5~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~1~1~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~86~1~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump design point overall pressure rise | bar | 152.6129 | 152.6129 | #N/A | 152.6129
91¦~86~1~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~86~1~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Flow margin | % | 10 | 10 | #N/A | 10
91¦~86~1~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~86~1~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Design point RPM |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~86~1~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~86~1~16~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss | kW | 56.4319 | 56.4319 | #N/A | 56.4319
91¦~86~1~13~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~86~1~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal RPM for off-design pump curve |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~11~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal rating flow for off-design pump curve | t/h | 305.0459 | 305.0459 | #N/A | 305.0459
91¦~86~1~12~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal pressure rise for off-design pump curve | bar | 144.5198 | 144.5198 | #N/A | 144.5198
91¦~86~1~2~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 8.607 | 8.607 | #N/A | 8.607
91¦~86~1~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~86~1~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~86~1~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~86~1~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~86~1~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~86~5~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~86~1~5~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~86~1~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~34~1~84~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~34~1~72~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Assumed water-side pressure drop for TD mode | bar | 0.35 | 0.35 | #N/A | 0.35
91¦~34~1~34~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Min. pinch temp. difference | C | 2.5 | 2.5 | #N/A | 2.5
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998 | #N/A | 0.9998
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8 | #N/A | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195 | #N/A | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005 | #N/A | 0.005
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001 | #N/A | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057 | #N/A | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843 | #N/A | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668 | #N/A | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332 | #N/A | 0.0332
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417 | #N/A | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005 | #N/A | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578 | #N/A | 0.1578
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 532.1 | 534.17 | 534.17 | 534.17
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 420 | 420 | #N/A | 420
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~77~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Desired steam outlet temperature | C | 511 | 511 | #N/A | 511
~77~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~77~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~77~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~78~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Desired steam outlet temperature | C | 534.1 | 534.1 | #N/A | 534.1
~78~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~78~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~78~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~23~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Desired steam outlet temperature | C | 490 | 490 | #N/A | 490
~23~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~23~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~23~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~79~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Desired steam outlet temperature | C | 517 | 517 | #N/A | 517
~79~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~79~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~79~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
~14~2~2~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~14~1~5~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~14~1~6~~-32~ | Boiler Assembly [1]: Valve [14] : Upstream set point | bar | 36.6 | 36.6 | #N/A | 36.6
~14~1~8~~-32~ | Boiler Assembly [1]: Valve [14] : Downstream set point | bar | 36.6045 | 36.6045 | #N/A | 36.6045
~14~1~7~~-32~ | Boiler Assembly [1]: Valve [14] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~80~2~2~~-32~ | Valve [80] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~80~1~5~~-32~ | Valve [80] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~80~1~6~~-32~ | Valve [80] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~8~~-32~ | Valve [80] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~7~~-32~ | Valve [80] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~81~2~2~~-32~ | Valve [81] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~81~1~5~~-32~ | Valve [81] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~81~1~6~~-32~ | Valve [81] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~8~~-32~ | Valve [81] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~7~~-32~ | Valve [81] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~58~1~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5 | #N/A | 3.5
91¦~58~1~21~~-14~ | Water Sink [58] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~58~1~22~~-14~ | Water Sink [58] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~57~1~2~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~57~1~3~~-9~ | Water Source [57] : Temperature | C | 27.3 | 29 | 29 | 29
91¦~57~1~4~~-9~ | Water Source [57] : Steam quality |  | -2 | -2 | #N/A | -2
91¦~57~1~5~~-9~ | Water Source [57] : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~57~1~21~~-9~ | Water Source [57] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~57~1~22~~-9~ | Water Source [57] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~59~1~53~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975 | #N/A | 0.0975
~59~1~5~~-104~ | Water-cooled Condenser (PCE) [59] : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~59~1~9~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
~2~23~1~~-10100~ | Fix Pressure Stream 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 31.266 | 34.4868 | 34.4868 | 34.4868
~2~32~1~~-10100~ | Fix Pressure Stream 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 28.487 | 31.4223 | 31.4223 | 31.4223
~2~34~1~~-10100~ | Fix Pressure Stream 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 15.24 | 16.81 | 16.81 | 16.81
~2~41~1~~-10100~ | Fix Pressure Stream 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 8.607 | 9.4941 | 9.4941 | 9.4941
91¦~1~1~4~~-20000~ | Generator [1]: Design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~1~1~5~~-20000~ | Generator [1]: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~1~3~18~~-20000~ | Generator [1]: Generator mech loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~13~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [13] - G[1] |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~66~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [66] - SA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux |  | 1 | 1 | #N/A | 1
91¦~40~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [40] - CP |  | 1 | 1 | #N/A | 1
91¦~82~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [82] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~83~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [83] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~13~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~13~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~13~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~1~-4100~ | ST Assembly [1]: Leakage flow (HPT LP leak 1 to LPT crossover) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~13~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~13~1~2~~-11~ | ST Assembly [1]: ST Group [13] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 142.5 | 156.63 | 156.63 | 156.63
91¦~13~1~3~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry step efficiency | % | 85.1821 | 85.1821 | #N/A | 85.1821
91¦~13~1~7~~-11~ | ST Assembly [1]: ST Group [13] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~13~5~15~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~13~1~4~~-11~ | ST Assembly [1]: ST Group [13] : Reference pressure ratio for steam turbine expansion step |  | 1.1 | 1.1 | #N/A | 1.1
91¦~13~1~5~~-11~ | ST Assembly [1]: ST Group [13] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~13~1~6~~-11~ | ST Assembly [1]: ST Group [13] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~13~1~11~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~13~1~12~~-11~ | ST Assembly [1]: ST Group [13] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~15~1~2~~-11~ | ST Assembly [1]: ST Group [15] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 52.204 | 57.582 | 57.582 | 57.582
91¦~15~1~20~~-11~ | ST Assembly [1]: ST Group [15] : Outlet specific enthalpy (before exhaust loss if any) | kJ/kg | 3047.1499 | 3047.1499 | #N/A | 3047.1499
91¦~15~1~7~~-11~ | ST Assembly [1]: ST Group [15] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~15~5~15~~-11~ | ST Assembly [1]: ST Group [15] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~15~1~4~~-11~ | ST Assembly [1]: ST Group [15] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~15~1~5~~-11~ | ST Assembly [1]: ST Group [15] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~15~1~6~~-11~ | ST Assembly [1]: ST Group [15] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~15~1~11~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~15~1~12~~-11~ | ST Assembly [1]: ST Group [15] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~26~1~2~~-11~ | ST Assembly [1]: ST Group [26] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 28.487 | 31.4223 | 31.4223 | 31.4223
91¦~26~1~3~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry step efficiency | % | 88.6914 | 88.6914 | #N/A | 88.6914
91¦~26~1~7~~-11~ | ST Assembly [1]: ST Group [26] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~26~5~15~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~26~1~4~~-11~ | ST Assembly [1]: ST Group [26] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~26~1~5~~-11~ | ST Assembly [1]: ST Group [26] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~26~1~6~~-11~ | ST Assembly [1]: ST Group [26] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~26~1~11~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~26~1~12~~-11~ | ST Assembly [1]: ST Group [26] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~28~1~2~~-11~ | ST Assembly [1]: ST Group [28] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 15.24 | 16.81 | 16.81 | 16.81
91¦~28~1~3~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry step efficiency | % | 89.8737 | 89.8737 | #N/A | 89.8737
91¦~28~1~7~~-11~ | ST Assembly [1]: ST Group [28] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~28~5~15~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~28~1~4~~-11~ | ST Assembly [1]: ST Group [28] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~28~1~5~~-11~ | ST Assembly [1]: ST Group [28] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~6~~-11~ | ST Assembly [1]: ST Group [28] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~28~1~11~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~28~1~12~~-11~ | ST Assembly [1]: ST Group [28] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~44~1~2~~-11~ | ST Assembly [1]: ST Group [44] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 8.607 | 9.4941 | 9.4941 | 9.4941
91¦~44~1~3~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry step efficiency | % | 90.9151 | 90.9151 | #N/A | 90.9151
91¦~44~1~7~~-11~ | ST Assembly [1]: ST Group [44] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~44~5~15~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~44~1~4~~-11~ | ST Assembly [1]: ST Group [44] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~44~1~5~~-11~ | ST Assembly [1]: ST Group [44] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~44~1~6~~-11~ | ST Assembly [1]: ST Group [44] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~44~1~11~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~44~1~12~~-11~ | ST Assembly [1]: ST Group [44] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~45~1~2~~-11~ | ST Assembly [1]: ST Group [45] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 3.391 | 3.7398 | 3.7398 | 3.7398
91¦~45~1~3~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry step efficiency | % | 92.0601 | 92.0601 | #N/A | 92.0601
91¦~45~1~7~~-11~ | ST Assembly [1]: ST Group [45] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~45~5~15~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~45~1~4~~-11~ | ST Assembly [1]: ST Group [45] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~45~1~5~~-11~ | ST Assembly [1]: ST Group [45] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~45~1~6~~-11~ | ST Assembly [1]: ST Group [45] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~45~1~11~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~45~1~12~~-11~ | ST Assembly [1]: ST Group [45] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~46~1~2~~-11~ | ST Assembly [1]: ST Group [46] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.285 | 1.4169 | 1.4169 | 1.4169
91¦~46~1~3~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry step efficiency | % | 92.3209 | 92.3209 | #N/A | 92.3209
91¦~46~1~7~~-11~ | ST Assembly [1]: ST Group [46] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~46~5~15~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~46~1~4~~-11~ | ST Assembly [1]: ST Group [46] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~46~1~5~~-11~ | ST Assembly [1]: ST Group [46] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~46~1~6~~-11~ | ST Assembly [1]: ST Group [46] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~46~1~11~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~46~1~12~~-11~ | ST Assembly [1]: ST Group [46] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~47~1~2~~-11~ | ST Assembly [1]: ST Group [47] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.78 | 0.78 | #N/A | 0.78
91¦~47~1~3~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry step efficiency | % | 92.25 | 92.25 | #N/A | 92.25
91¦~47~1~7~~-11~ | ST Assembly [1]: ST Group [47] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~47~5~15~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~47~1~4~~-11~ | ST Assembly [1]: ST Group [47] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~47~1~5~~-11~ | ST Assembly [1]: ST Group [47] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~47~1~6~~-11~ | ST Assembly [1]: ST Group [47] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~47~1~11~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~47~1~12~~-11~ | ST Assembly [1]: ST Group [47] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~5~1~2~~-11~ | ST Assembly [1]: ST Group [5] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.283 | 0.283 | #N/A | 0.283
91¦~5~1~3~~-11~ | ST Assembly [1]: ST Group [5] : Design point dry step efficiency | % | 92.15 | 92.15 | #N/A | 92.15
91¦~5~1~7~~-11~ | ST Assembly [1]: ST Group [5] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~5~5~6~~-11~ | ST Assembly [1]: ST Group [5] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~5~1~4~~-11~ | ST Assembly [1]: ST Group [5] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~5~1~5~~-11~ | ST Assembly [1]: ST Group [5] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~5~1~6~~-11~ | ST Assembly [1]: ST Group [5] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~5~1~11~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~5~1~12~~-11~ | ST Assembly [1]: ST Group [5] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~2~1~~~-5007~ | HIP Turbin: Label 1 |  | BFPT-A | BFPT-A | #N/A | BFPT-A
~2~2~~~-5007~ | HIP Turbin: Label 2 |  | BFPT-B | BFPT-B | #N/A | BFPT-B
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 26.95 | 26.95
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 75.41 | 75.41
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 23.5477 | 23.5477
~~~4~~-5000~ | Plant Summary: Gross power | kW | 175000.875 | 175000.875
~~~7~~-5000~ | Plant Summary: Net power | kW | 164181.5938 | 164181.5938
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 10819.2725 | 10819.2725
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 9944.2686 | 9944.2686
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 875.0043 | 875.0043
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 39.2972 | 39.2972
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 9160.9619 | 9160.9619
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 36.8677 | 36.8677
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 9764.6523 | 9764.6523
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 445326.7188 | 445326.7188
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 36.8677 | 36.8677
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 36.8677 | 36.8677
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 33.8258 | 33.8258
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 10642.7539 | 10642.7539
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 485373.4062 | 485373.4062
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 445326.7188 | 445326.7188
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 36.8677 | 36.8677
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 1.5677 | 1.5677
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 1.362 | 1.362
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 445326.7188 | 445326.7188
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 485373.4062 | 485373.4062
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.362 | 2.362
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 3786.6589 | 3786.6589
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 42997264 | 42997264
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 54024212 | 54024212
~1~3~1~~-2005~ | Shaft 1: Shaft net power | kW | 177291.4531 | 177291.4531
~1~3~2~~-2005~ | Shaft 1: Shaft speed | RPM | 3000 | 3000
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 1329.8708 | 1329.8708
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 12985.7275 | 12985.7275
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 12.8449 | 12.8449
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 1334.0459 | 1334.0459
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 54024.2109 | 54024.2109
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 329.0516 | 329.0516
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 839702.5625 | 839702.5625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 16207.2617 | 16207.2617
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 64.9448 | 64.9448
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 191.8551 | 191.8551
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.52972 | 0.52972
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 436015.8125 | 436015.8125
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.03036 | 0.03036
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.9094 | 5.9094
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 42997264 | 42997264
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 42997264 | 42997264
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 7157194 | 7157194
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 50154456 | 50154456
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 54024212 | 54024212
~1~9~13~~-5003~ | Generator / Motor Power: Generator [1] of ST Assembly [1] power | kW | 175000.875 | 175000.875
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 604.0194 | 604.0194
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 1537.4357 | 1537.4357
~4~66~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [66] - SA Fan : aux | kW | 70.5806 | 70.5806
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan : aux | kW | 132.9526 | 132.9526
~4~7~158~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux | kW | 3099.7583 | 3099.7583
~4~40~168~~-5003~ | Generator / Motor Power: General Pump [40] - CP | kW | 178.5051 | 178.5051
~4~82~100~~-5003~ | Generator / Motor Power: Pump (PCE) [82] - CWP-1 | kW | 1101.7532 | 1101.7532
~4~83~100~~-5003~ | Generator / Motor Power: Pump (PCE) [83] - CWP-2 | kW | 1101.7532 | 1101.7532
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 367.5018 | 367.5018
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 1750.0087 | 1750.0087
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 875.0043 | 875.0043
~5~9~13~1~-5003~ | Generator / Motor Power: Shaft-1 net power | kW | 177291.4531 | 177291.4531
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 9944.2686 | 9944.2686
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 445326.7188 | 445326.7188
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~3~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer | kW | -200.9103 | -200.9103
91¦~3~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer | kW | -58.748 | -58.748
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air status |  | Ignored | Ignored
93¦~6~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer | kW | 45.6934 | 45.6934
91¦~6~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~57~3~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer | kW | 623814.125 | 623814.125
91¦~57~1~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer multiplier |  | 1 | 1
82¦71¦~57~5~10~1~-7000~ | Energy Inflow: Water Source [57] status |  | Ignored | Ignored
93¦~6~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer | kW | 0 | 0
91¦~6~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~58~3~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer | kW | 853781.5 | 853781.5
91¦~58~1~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer multiplier |  | 1 | 1
82¦71¦~58~5~10~2~-7000~ | Energy Outflow: Water Sink [58] status |  | Ignored | Ignored
93¦~13~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [13] shaft power | kW | 39501.2617 | 39501.2617
93¦~15~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [15] shaft power | kW | 14046.5234 | 14046.5234
93¦~26~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [26] shaft power | kW | 24441.8164 | 24441.8164
93¦~28~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [28] shaft power | kW | 19626.8613 | 19626.8613
93¦~44~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [44] shaft power | kW | 25009.209 | 25009.209
93¦~45~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [45] shaft power | kW | 20355.9414 | 20355.9414
93¦~46~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [46] shaft power | kW | 8669.1807 | 8669.1807
93¦~47~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [47] shaft power | kW | 14779.3516 | 14779.3516
93¦~5~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [5] shaft power | kW | 10861.3193 | 10861.3193
82¦71¦~5~5~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] power | kW | 175000.875 | 175000.875
91¦~5~1~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] multiplier |  | 1 | 1
93¦~5~3~3~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] efficiency | % | 98.708 | 98.708
82¦71¦~5~5~10~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] status |  | power producer | power producer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 604.0194 | 604.0194
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 1537.4357 | 1537.4357
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~66~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux power | kW | 70.5806 | 70.5806
91¦~66~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux multiplier |  | 1 | 1
82¦71¦~66~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux power | kW | 132.9526 | 132.9526
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux status |  | power consumer | power consumer
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux power | kW | 3099.7583 | 3099.7583
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux status |  | power consumer | power consumer
93¦~40~3~2~4~-7000~ | Auxiliary Device: General Pump [40] - CP power | kW | 178.5051 | 178.5051
91¦~40~1~1~4~-7000~ | Auxiliary Device: General Pump [40] - CP multiplier |  | 1 | 1
82¦71¦~40~5~10~4~-7000~ | Auxiliary Device: General Pump [40] - CP status |  | power consumer | power consumer
93¦~82~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 power | kW | 1101.7532 | 1101.7532
91¦~82~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 multiplier |  | 1 | 1
82¦71¦~82~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 status |  | power consumer | power consumer
93¦~83~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 power | kW | 1101.7532 | 1101.7532
91¦~83~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 multiplier |  | 1 | 1
82¦71¦~83~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 status |  | power consumer | power consumer
~31~6~1~~-27~ | Deaerator [31] - DAER : Mode |  | TD | TD
~31~6~3~~-27~ | Deaerator [31] - DAER : DA pressure specification |  | Specified by user | Specified by user
~31~4~4~~-27~ | Deaerator [31] - DAER : Operating pressure | bar | 8.4382 | 8.4382
~31~4~5~~-27~ | Deaerator [31] - DAER : Temperature | C | 172.6372 | 172.6372
93¦~31~4~7~~-27~ | Deaerator [31] - DAER : FW inlet pressure | bar | 9.6159 | 9.6159
93¦~31~4~8~~-27~ | Deaerator [31] - DAER : FW inlet temperature | C | 131.4777 | 131.4777
93¦~31~4~28~~-27~ | Deaerator [31] - DAER : FW inlet enthalpy | kJ/kg | 553.0932 | 553.0932
93¦~31~4~9~~-27~ | Deaerator [31] - DAER : FW inlet mass flow | t/h | 427.734 | 427.734
93¦~31~4~23~~-27~ | Deaerator [31] - DAER : Additional water head at inlet | bar | 1.1775 | 1.1775
93¦~31~4~10~~-27~ | Deaerator [31] - DAER : Heating stream pressure | bar | 8.4382 | 8.4382
93¦~31~4~12~~-27~ | Deaerator [31] - DAER : Heating stream temperature | C | 353.3496 | 353.3496
93¦~31~4~11~~-27~ | Deaerator [31] - DAER : Heating stream enthalpy | kJ/kg | 3168.3425 | 3168.3425
93¦~31~4~13~~-27~ | Deaerator [31] - DAER : Heating stream mass flow | t/h | 30.2036 | 30.2036
93¦~31~4~17~~-27~ | Deaerator [31] - DAER : Flash in pressure | bar | 14.9412 | 14.9412
93¦~31~4~18~~-27~ | Deaerator [31] - DAER : Flash in temperature | C | 178.5169 | 178.5169
93¦~31~4~19~~-27~ | Deaerator [31] - DAER : Flash in enthalpy | kJ/kg | 756.8219 | 756.8219
93¦~31~4~20~~-27~ | Deaerator [31] - DAER : Flash in mass flow | t/h | 91.145 | 91.145
93¦~31~4~14~~-27~ | Deaerator [31] - DAER : FW outlet pressure | bar | 9.5177 | 9.5177
93¦~31~4~15~~-27~ | Deaerator [31] - DAER : FW outlet temperature | C | 172.6459 | 172.6459
93¦~31~4~29~~-27~ | Deaerator [31] - DAER : FW outlet enthalpy | kJ/kg | 730.7693 | 730.7693
93¦~31~4~16~~-27~ | Deaerator [31] - DAER : FW outlet mass flow | t/h | 549.0826 | 549.0826
93¦~31~4~24~~-27~ | Deaerator [31] - DAER : Additional water head at outlet | bar | 1.0794 | 1.0794
~67~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Temperature drop | C | 0 | 0
~67~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet pressure | bar | 31.266 | 31.266
~67~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet temperature | C | 322.5885 | 322.5885
~67~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet mass flow | t/h | 468.5106 | 468.5106
~67~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet enthalpy | kJ/kg | 3047.1499 | 3047.1499
~67~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet pressure | bar | 31.266 | 31.266
~67~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet temperature | C | 322.5885 | 322.5885
~67~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet mass flow | t/h | 468.5106 | 468.5106
~67~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet enthalpy | kJ/kg | 3047.1499 | 3047.1499
~67~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray mass flow | t/h | 2.9419e-07 | 2.9419e-07
~67~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray water enthalpy | kJ/kg | 753.6763 | 753.6763
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Temperature drop | C | 2.0003 | 2.0003
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet pressure | bar | 148.2861 | 148.2861
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet temperature | C | 420.0042 | 420.0042
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet mass flow | t/h | 544.8 | 544.8
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet enthalpy | kJ/kg | 3057.8013 | 3057.8013
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet pressure | bar | 148.2861 | 148.2861
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet temperature | C | 418.004 | 418.004
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet mass flow | t/h | 546.5478 | 546.5478
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet enthalpy | kJ/kg | 3050.4329 | 3050.4329
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray mass flow | t/h | 1.7479 | 1.7479
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray water enthalpy | kJ/kg | 753.6763 | 753.6763
~69~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Temperature drop | C | 2.0003 | 2.0003
~69~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet pressure | bar | 145.3642 | 145.3642
~69~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet temperature | C | 516.9999 | 516.9999
~69~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet mass flow | t/h | 546.5478 | 546.5478
~69~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet enthalpy | kJ/kg | 3365.0205 | 3365.0205
~69~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet pressure | bar | 145.3642 | 145.3642
~69~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet temperature | C | 514.9996 | 514.9996
~69~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet mass flow | t/h | 547.7206 | 547.7206
~69~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet enthalpy | kJ/kg | 3359.4287 | 3359.4287
~69~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray mass flow | t/h | 1.1728 | 1.1728
~69~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray water enthalpy | kJ/kg | 753.6763 | 753.6763
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Heat loss | kW | 52.9728 | 52.9728
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Temperature drop | C | 1.1111 | 1.1111
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Heat loss | kW | 305.9263 | 305.9263
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Temperature drop | C | 0 | 0
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Heat loss | kW | 0 | 0
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 546.162 | 546.162
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 151.2666 | 151.2666
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 1151.7466 | 1151.7466
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 263.6848 | 263.6848
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 546.162 | 546.162
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 149.7689 | 149.7689
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 317 | 317
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1435.5515 | 1435.5515
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 837.5018 | 837.5018
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 4.1031 | 4.1031
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 510.2908 | 510.2908
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 352.4298 | 352.4298
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 51.0935 | 51.0935
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1691.4357 | 1691.4357
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 43057.1875 | 43057.1875
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 43057.1875 | 43057.1875
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 322.9289 | 322.9289
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 1.4977 | 1.4977
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.6181 | 99.6181
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 604.0194 | 604.0194
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.98686 | 0.98686
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 140.8226 | 140.8226
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 1101059.375 | 1101059.375
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 916.0822 | 916.0822
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 4.1031 | 4.1031
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 4.0874 | 4.0874
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.015669 | 0.015669
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 2348.208 | 2348.208
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 6546.439 | 6546.439
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 8.9675 | 8.9675
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 25 | 25
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 0 | 0
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2193 | 1.2193
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 1486.5293 | 1486.5293
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 1486.5293 | 1486.5293
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 1471.6641 | 1471.6641
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 309.1281 | 309.1281
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 38.6052 | 38.6052
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 38.6052 | 38.6052
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1 | 80.1
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 14.8653 | 14.8653
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 1614.3073 | 1614.3073
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.7054 | 96.7054
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 1537.4355 | 1537.4355
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 1486.5293 | 1486.5293
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.6889 | 96.6889
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 50.9062 | 50.9062
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 1560.8557 | 1560.8557
82¦71¦~66~5~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~66~5~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~66~1~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of existing units |  | 1 | 1
93¦~66~3~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1
93¦~66~3~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Total shaft power | kW | 66.4533 | 66.4533
93¦~66~3~1~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Shaft power per unit | kW | 66.4533 | 66.4533
93¦~66~3~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan compression power per unit | kW | 65.7887 | 65.7887
93¦~66~3~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan inlet volume flow per unit | m^3/s | 149.0425 | 149.0425
93¦~66~3~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure rise (before control damper) | millibar | 3.5334 | 3.5334
93¦~66~3~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan overall pressure rise | millibar | 3.5334 | 3.5334
93¦~66~3~6~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~66~3~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan polytropic efficiency | % | 80.0232 | 80.0232
93¦~66~3~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200
93¦~66~3~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss per unit | kW | 0.66453 | 0.66453
93¦~66~3~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~66~6~1~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Mode |  | Design | Design
91¦~66~1~7~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate power | kW | 74.1096 | 74.1096
91¦~66~1~19~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate efficiency | % | 94.1815 | 94.1815
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~66~2~8~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Number of operating units |  | 1 | 1
93¦~66~7~2~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electricity consumption | kW | 70.5806 | 70.5806
93¦~66~7~6~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Shaft power | kW | 66.4533 | 66.4533
93¦~66~7~4~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Efficiency | % | 94.1524 | 94.1524
93¦~66~7~3~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electrical loss | kW | 4.1273 | 4.1273
89¦~66~3~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate motor shaft power | kW | 69.7759 | 69.7759
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Total shaft power | kW | 126.1821 | 126.1821
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Shaft power per unit | kW | 126.1821 | 126.1821
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan compression power per unit | kW | 124.9203 | 124.9203
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan inlet volume flow per unit | m^3/s | 40.4145 | 40.4145
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure rise (before control damper) | millibar | 24.9066 | 24.9066
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan overall pressure rise | millibar | 24.9066 | 24.9066
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan polytropic efficiency | % | 80.0643 | 80.0643
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss per unit | kW | 1.2618 | 1.2618
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate power | kW | 139.6002 | 139.6002
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate efficiency | % | 94.9329 | 94.9329
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electricity consumption | kW | 132.9526 | 132.9526
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Shaft power | kW | 126.1821 | 126.1821
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Efficiency | % | 94.9076 | 94.9076
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electrical loss | kW | 6.7705 | 6.7705
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate motor shaft power | kW | 132.4912 | 132.4912
82¦71¦~16~5~1~~-38~ | Feedwater Heater [16] - HPH-1 : Mode |  | Design | Design
89¦~16~3~7~~-38~ | Feedwater Heater [16] - HPH-1 : Heat transfer | kW | 20886.1914 | 20886.1914
89¦~16~3~8~~-38~ | Feedwater Heater [16] - HPH-1 : Shell pressure | bar | 51.1804 | 51.1804
89¦~16~3~9~~-38~ | Feedwater Heater [16] - HPH-1 : Saturation temperature | C | 265.4052 | 265.4052
89¦~16~3~13~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature at heater exit | C | 263.9052 | 263.9052
89¦~16~3~11~~-38~ | Feedwater Heater [16] - HPH-1 : Terminal difference | C | 1.5 | 1.5
89¦~16~3~12~~-38~ | Feedwater Heater [16] - HPH-1 : Drain cooler approach | C | 2.8 | 2.8
89¦~16~3~3~~-38~ | Feedwater Heater [16] - HPH-1 : UA of drain cooler section | kW/C | 119.951 | 119.951
89¦~16~3~1~~-38~ | Feedwater Heater [16] - HPH-1 : UA of condensing section | kW/C | 2117.6506 | 2117.6506
82¦71¦~17~5~1~~-38~ | Feedwater Heater [17] - HPH-2 : Mode |  | Design | Design
89¦~17~3~7~~-38~ | Feedwater Heater [17] - HPH-2 : Heat transfer | kW | 25272.7305 | 25272.7305
89¦~17~3~8~~-38~ | Feedwater Heater [17] - HPH-2 : Shell pressure | bar | 30.6529 | 30.6529
89¦~17~3~9~~-38~ | Feedwater Heater [17] - HPH-2 : Saturation temperature | C | 235.0555 | 235.0555
89¦~17~3~13~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature at heater exit | C | 234.7775 | 234.7775
89¦~17~3~11~~-38~ | Feedwater Heater [17] - HPH-2 : Terminal difference | C | 0.27802 | 0.27802
89¦~17~3~12~~-38~ | Feedwater Heater [17] - HPH-2 : Drain cooler approach | C | 5.6 | 5.6
89¦~17~3~3~~-38~ | Feedwater Heater [17] - HPH-2 : UA of drain cooler section | kW/C | 196.5388 | 196.5388
89¦~17~3~1~~-38~ | Feedwater Heater [17] - HPH-2 : UA of condensing section | kW/C | 3256.9487 | 3256.9487
82¦71¦~24~5~1~~-38~ | Feedwater Heater [24] - HPH-3 : Mode |  | Design | Design
89¦~24~3~7~~-38~ | Feedwater Heater [24] - HPH-3 : Heat transfer | kW | 14385.6328 | 14385.6328
89¦~24~3~8~~-38~ | Feedwater Heater [24] - HPH-3 : Shell pressure | bar | 14.9412 | 14.9412
89¦~24~3~9~~-38~ | Feedwater Heater [24] - HPH-3 : Saturation temperature | C | 198.109 | 198.109
89¦~24~3~13~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature at heater exit | C | 197.7289 | 197.7289
89¦~24~3~11~~-38~ | Feedwater Heater [24] - HPH-3 : Terminal difference | C | 0.38001 | 0.38001
89¦~24~3~12~~-38~ | Feedwater Heater [24] - HPH-3 : Drain cooler approach | C | 2.5 | 2.5
89¦~24~3~3~~-38~ | Feedwater Heater [24] - HPH-3 : UA of drain cooler section | kW/C | 272.9926 | 272.9926
89¦~24~3~1~~-38~ | Feedwater Heater [24] - HPH-3 : UA of condensing section | kW/C | 2581.9404 | 2581.9404
82¦71¦~53~5~1~~-38~ | Feedwater Heater [53] - LPH-8 : Mode |  | Design | Design
89¦~53~3~7~~-38~ | Feedwater Heater [53] - LPH-8 : Heat transfer | kW | 7909.3164 | 7909.3164
89¦~53~3~8~~-38~ | Feedwater Heater [53] - LPH-8 : Shell pressure | bar | 0.27745 | 0.27745
89¦~53~3~9~~-38~ | Feedwater Heater [53] - LPH-8 : Saturation temperature | C | 67.3104 | 67.3104
89¦~53~3~13~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature at heater exit | C | 61.7104 | 61.7104
89¦~53~3~11~~-38~ | Feedwater Heater [53] - LPH-8 : Terminal difference | C | 5.6 | 5.6
89¦~53~3~12~~-38~ | Feedwater Heater [53] - LPH-8 : Drain cooler approach | C | 2.8 | 2.8
89¦~53~3~3~~-38~ | Feedwater Heater [53] - LPH-8 : UA of drain cooler section | kW/C | 154.513 | 154.513
89¦~53~3~1~~-38~ | Feedwater Heater [53] - LPH-8 : UA of condensing section | kW/C | 604.2064 | 604.2064
82¦71¦~54~5~1~~-38~ | Feedwater Heater [54] - LPH-7 : Mode |  | Design | Design
89¦~54~3~7~~-38~ | Feedwater Heater [54] - LPH-7 : Heat transfer | kW | 11340.0156 | 11340.0156
89¦~54~3~8~~-38~ | Feedwater Heater [54] - LPH-7 : Shell pressure | bar | 0.70449 | 0.70449
89¦~54~3~9~~-38~ | Feedwater Heater [54] - LPH-7 : Saturation temperature | C | 90.1 | 90.1
89¦~54~3~13~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature at heater exit | C | 84.5 | 84.5
89¦~54~3~11~~-38~ | Feedwater Heater [54] - LPH-7 : Terminal difference | C | 5.6 | 5.6
89¦~54~3~12~~-38~ | Feedwater Heater [54] - LPH-7 : Drain cooler approach | C | 2.8 | 2.8
89¦~54~3~3~~-38~ | Feedwater Heater [54] - LPH-7 : UA of drain cooler section | kW/C | 142.6287 | 142.6287
89¦~54~3~1~~-38~ | Feedwater Heater [54] - LPH-7 : UA of condensing section | kW/C | 753.3429 | 753.3429
82¦71¦~55~5~1~~-38~ | Feedwater Heater [55] - LPH-6 : Mode |  | Design | Design
89¦~55~3~7~~-38~ | Feedwater Heater [55] - LPH-6 : Heat transfer | kW | 7990.5054 | 7990.5054
89¦~55~3~8~~-38~ | Feedwater Heater [55] - LPH-6 : Shell pressure | bar | 1.2598 | 1.2598
89¦~55~3~9~~-38~ | Feedwater Heater [55] - LPH-6 : Saturation temperature | C | 106.193 | 106.193
89¦~55~3~13~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature at heater exit | C | 100.493 | 100.493
89¦~55~3~11~~-38~ | Feedwater Heater [55] - LPH-6 : Terminal difference | C | 5.7 | 5.7
89¦~55~3~12~~-38~ | Feedwater Heater [55] - LPH-6 : Drain cooler approach | C | 2.8 | 2.8
89¦~55~3~3~~-38~ | Feedwater Heater [55] - LPH-6 : UA of drain cooler section | kW/C | 84.1891 | 84.1891
89¦~55~3~1~~-38~ | Feedwater Heater [55] - LPH-6 : UA of condensing section | kW/C | 632.3135 | 632.3135
82¦71¦~56~5~1~~-38~ | Feedwater Heater [56] - LPH-5 : Mode |  | Design | Design
89¦~56~3~7~~-38~ | Feedwater Heater [56] - LPH-5 : Heat transfer | kW | 15595.376 | 15595.376
89¦~56~3~8~~-38~ | Feedwater Heater [56] - LPH-5 : Shell pressure | bar | 3.3245 | 3.3245
89¦~56~3~9~~-38~ | Feedwater Heater [56] - LPH-5 : Saturation temperature | C | 137.0627 | 137.0627
89¦~56~3~13~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature at heater exit | C | 131.4627 | 131.4627
89¦~56~3~11~~-38~ | Feedwater Heater [56] - LPH-5 : Terminal difference | C | 5.6 | 5.6
89¦~56~3~12~~-38~ | Feedwater Heater [56] - LPH-5 : Drain cooler approach | C | 2.8 | 2.8
89¦~56~3~3~~-38~ | Feedwater Heater [56] - LPH-5 : UA of drain cooler section | kW/C | 69.6455 | 69.6455
89¦~56~3~1~~-38~ | Feedwater Heater [56] - LPH-5 : UA of condensing section | kW/C | 920.1456 | 920.1456
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0135 | 1.0135
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 30 | 30
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 17296.6797 | 17296.6797
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 92.7421 | 92.7421
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 445326.7188 | 445326.7188
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 485373.4062 | 485373.4062
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.362 | 2.362
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 3786.6589 | 3786.6589
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 17286.1191 | 17286.1191
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 18840.5996
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 17296.6777 | 17296.6777
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 18922.1328 | 18922.1328
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 48.63 | 48.63
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 3.99 | 3.99
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 13.04 | 13.04
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.8 | 0.8
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.19 | 0.19
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 5.36 | 5.36
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 27.99 | 27.99
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9862 | 6.9862
93¦~7~4~57~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total steam produced | t/h | 544.8 | 544.8
93¦~7~4~54~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam pressure | bar | 149.7689 | 149.7689
93¦~7~4~55~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam temperature | C | 342.0345 | 342.0345
93¦~7~4~56~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam enthalpy | kJ/kg | 2611.5242 | 2611.5242
93¦~7~4~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Adiabatic temperature | C | 1707.4381 | 1707.4381
93¦~7~4~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Effective radiating temperature | C | 1421.6313 | 1421.6313
93¦~7~4~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1131.2021 | 1131.2021
93¦~7~4~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Waterwall surface temperature | C | 1047.5653 | 1047.5653
93¦~7~4~19~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25
82¦71¦~7~6~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas N2 mol% | % | 69.3633 | 69.3633
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas O2 mol% | % | 3.7173 | 3.7173
93¦~7~4~104~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas CO2 mol% | % | 13.0047 | 13.0047
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas H2O mol% | % | 13.0614 | 13.0614
93¦~7~4~191~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas SO2 mol% | % | 0.019061 | 0.019061
82¦71¦~7~6~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas Ar mol% | % | 0.83426 | 0.83426
93¦~7~4~289~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total heat transfer to water/steam side | kW | 178031.6875 | 178031.6875
93¦~7~4~5~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat transfer to waterwall | kW | 178031.6875 | 178031.6875
82¦71¦~7~6~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon in ash | kW | 1478.78 | 1478.78
93¦~7~4~13~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat losses | kW | 5784.2373 | 5784.2373
93¦~7~4~109~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | kW | 1676.8171 | 1676.8171
93¦~7~4~321~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash (bed drain) sensible heat | kW | 355.0224 | 355.0224
93¦~7~4~322~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash sensible heat | kW | 1420.0898 | 1420.0898
93¦~7~4~43~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat absorption rate | kW/m^2 | 103.751 | 103.751
93¦~7~4~41~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat release rate | kW/m^2 | 283.4951 | 283.4951
93¦~7~4~42~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Volumetric fuel release rate | kW/m^3 | 118.7654 | 118.7654
93¦~7~4~305~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : SO2 removal efficiency | % | 0 | 0
93¦~7~4~302~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Sulfur removed | t/h | 0 | 0
93¦~7~4~301~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reagent consumption | t/h | 0 | 0
93¦~7~4~32~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas mass flux @ aperture | t/h-m^2 | 10.6035 | 10.6035
93¦~7~4~46~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas velocity leaving aperture @ exit temperature | m/s | 11.7011 | 11.7011
93¦~7~4~247~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gas mass flux | t/h-m^2 | 7.2459 | 7.2459
93¦~7~4~33~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace velocity @ effective radiating temperature | m/s | 9.6496 | 9.6496
93¦~7~4~339~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel mass flow | t/h | 92.7421 | 92.7421
82¦71¦~7~6~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel consumption per day | tonne/day | 2225.8096 | 2225.8096
93¦~7~4~17~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (LHV) | kW | 445326.7188 | 445326.7188
93¦~7~4~49~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (HHV) | kW | 485373.4062 | 485373.4062
93¦~7~4~28~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel delivery power | kW | 2616.6575 | 2616.6575
93¦~7~4~246~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Ash handling power | kW | 226.1423 | 226.1423
93¦~7~4~47~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Forced circulation pump power | kW | 256.9583 | 256.9583
93¦~7~4~16~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel ash flow | t/h | 4.971 | 4.971
93¦~7~4~24~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon flow | t/h | 0.15785 | 0.15785
93¦~7~4~312~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solids added to ash due to reagent addition | t/h | 0 | 0
93¦~7~4~326~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inert bed material feed | t/h | 0 | 0
93¦~7~4~327~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solid produced from combustion | t/h | 5.1288 | 5.1288
93¦~7~4~314~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash flow | t/h | 1.0258 | 1.0258
93¦~7~4~317~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash flow | t/h | 4.1031 | 4.1031
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content | % | 5.3 | 5.3
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas O2 content | % | 3.7173 | 3.7173
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas H2O content | % | 13.0614 | 13.0614
93¦~7~4~431~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
76¦~7~2~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of existing pulverizers |  | 6 | 6
76¦~7~2~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of operating pulverizers |  | 5 | 5
91¦~7~1~92~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow | t/h | 92.7421 | 92.7421
93¦~7~3~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow (each) | t/h | 18.5484 | 18.5484
91¦~7~1~80~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel temperature | C | 30 | 30
91¦~7~1~89~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel moisture percent | % | 27.99 | 27.99
93¦~7~3~20~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel flow (each) | t/h | 15.4334 | 15.4334
93¦~7~3~19~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel moisture percent | % | 13.4558 | 13.4558
93¦~7~3~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet temperature | C | 60.8 | 60.8
93¦~7~3~33~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total moisture evaporated | t/h | 15.5751 | 15.5751
93¦~7~3~34~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percent of moisture evaporated | % | 60 | 60
82¦71¦~7~10~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow | t/h | 135.2475 | 135.2475
82¦71¦~7~10~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow (each) | t/h | 27.0495 | 27.0495
91¦~7~1~41~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet temperature | C | 320.7365 | 320.7365
82¦71¦~7~10~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow | t/h | 31.6883 | 31.6883
82¦71¦~7~10~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow (each) | t/h | 6.3377 | 6.3377
91¦~7~1~51~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air temperature | C | 27.2082 | 27.2082
82¦71¦~7~10~3~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow | t/h | 166.9358 | 166.9358
82¦71¦~7~10~13~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow (each) | t/h | 33.3872 | 33.3872
91¦~7~1~61~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air temperature | C | 266.1162 | 266.1162
91¦~7~1~60~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air pressure | bar | 1.1254 | 1.1254
93¦~7~3~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percentage of tempering air over total drying air | % | 18.9823 | 18.9823
93¦~7~3~35~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet air/fuel mass ratio |  | 1.8 | 1.8
82¦71¦~7~10~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow | t/h | 182.5109 | 182.5109
82¦71¦~7~10~14~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow (each) | t/h | 36.5022 | 36.5022
93¦~7~3~37~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas dew point | C | 55.521 | 55.521
93¦~7~3~38~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas relative humidity | % | 78.0768 | 78.0768
93¦~7~3~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer power (each) | kW | 515.3707 | 515.3707
82¦71¦~7~10~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exhaust fan power (each) | kW | 7.9608 | 7.9608
93¦~7~3~30~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total power consumption | kW | 2616.6575 | 2616.6575
93¦~3~3~1~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332
93¦~3~3~2~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85
93¦~3~3~3~~-1~ | Gas/Air Source [3] - Sec.Air : Enthalpy | kJ/kg | 0.86557 | 0.86557
93¦~3~3~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 641.2471 | 641.2471
93¦~3~3~5~~-1~ | Gas/Air Source [3] - Sec.Air : Molecular weight |  | 28.7578 | 28.7578
93¦~3~3~11~~-1~ | Gas/Air Source [3] - Sec.Air : N2 mole percent | % | 76.5891 | 76.5891
93¦~3~3~12~~-1~ | Gas/Air Source [3] - Sec.Air : O2 mole percent | % | 20.5495 | 20.5495
93¦~3~3~13~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mole percent | % | 0.029724 | 0.029724
93¦~3~3~14~~-1~ | Gas/Air Source [3] - Sec.Air : H2O mole percent | % | 1.9093 | 1.9093
93¦~3~3~15~~-1~ | Gas/Air Source [3] - Sec.Air : SO2 mole percent | % | 0 | 0
93¦~3~3~16~~-1~ | Gas/Air Source [3] - Sec.Air : Ar mole percent | % | 0.92239 | 0.92239
93¦~3~3~20~~-1~ | Gas/Air Source [3] - Sec.Air : Liquid H2O mole percent | % | 0 | 0
93¦~3~3~21~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mass flow | t/h | 0.2917 | 0.2917
93¦~11~3~1~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129
93¦~11~3~2~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85
93¦~11~3~3~~-1~ | Gas/Air Source [11] - Prim.Air : Enthalpy | kJ/kg | 0.86495 | 0.86495
93¦~11~3~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 187.4026 | 187.4026
93¦~11~3~5~~-1~ | Gas/Air Source [11] - Prim.Air : Molecular weight |  | 28.7728 | 28.7728
93¦~11~3~11~~-1~ | Gas/Air Source [11] - Prim.Air : N2 mole percent | % | 76.6959 | 76.6959
93¦~11~3~12~~-1~ | Gas/Air Source [11] - Prim.Air : O2 mole percent | % | 20.5782 | 20.5782
93¦~11~3~13~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mole percent | % | 0.029766 | 0.029766
93¦~11~3~14~~-1~ | Gas/Air Source [11] - Prim.Air : H2O mole percent | % | 1.7725 | 1.7725
93¦~11~3~15~~-1~ | Gas/Air Source [11] - Prim.Air : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - Prim.Air : Ar mole percent | % | 0.92367 | 0.92367
93¦~11~3~20~~-1~ | Gas/Air Source [11] - Prim.Air : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mass flow | t/h | 0.085323 | 0.085323
82¦71¦~40~10~3~~-168~ | General Pump [40] - CP : Mode |  | TD | TD
82¦71¦~40~10~7~~-168~ | General Pump [40] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~40~10~6~~-168~ | General Pump [40] - CP : Pump head | m | 106.101 | 106.101
83¦93¦~40~3~15~~-168~ | General Pump [40] - CP : Pressure rise before control valve | bar | 10.3021 | 10.3021
83¦93¦~40~3~18~~-168~ | General Pump [40] - CP : Pressure rise after valve pressure drop | bar | 10.3021 | 10.3021
83¦93¦~40~3~16~~-168~ | General Pump [40] - CP : Pressure drop across valve | bar | 2.6301e-07 | 2.6301e-07
83¦93¦~40~3~12~~-168~ | General Pump [40] - CP : Apparent isentropic efficiency | % | 74.9998 | 74.9998
83¦93¦~40~3~13~~-168~ | General Pump [40] - CP : Shaft work per station | kW | 169.9272 | 169.9272
82¦71¦~40~10~1~~-168~ | General Pump [40] - CP : Hydraulic work per station | kW | 164.8294 | 164.8294
82¦71¦~40~10~2~~-168~ | General Pump [40] - CP : Electricity consumption per station | kW | 178.5051 | 178.5051
83¦93¦~40~3~5~~-168~ | General Pump [40] - CP : Suction flow | t/h | 427.734 | 427.734
83¦93¦~40~3~27~~-168~ | General Pump [40] - CP : Suction pressure | bar | 0.45641 | 0.45641
83¦93¦~40~3~28~~-168~ | General Pump [40] - CP : Suction temperature | C | 45.2441 | 45.2441
83¦93¦~40~3~4~~-168~ | General Pump [40] - CP : Suction enthalpy | kJ/kg | 189.4355 | 189.4355
83¦93¦~40~3~8~~-168~ | General Pump [40] - CP : Discharge flow | t/h | 427.734 | 427.734
83¦93¦~40~3~29~~-168~ | General Pump [40] - CP : Discharge pressure | bar | 10.7585 | 10.7585
83¦93¦~40~3~6~~-168~ | General Pump [40] - CP : Discharge temperature | C | 45.3593 | 45.3593
83¦93¦~40~3~7~~-168~ | General Pump [40] - CP : Discharge enthalpy | kJ/kg | 190.8228 | 190.8228
82¦71¦~40~6~1~1000~-168~ | General Pump [40] - CP : Motor: Mode |  | Design | Design
91¦~40~1~7~1000~-168~ | General Pump [40] - CP : Motor: Nameplate power | kW | 182.2935 | 182.2935
91¦~40~1~19~1000~-168~ | General Pump [40] - CP : Motor: Nameplate efficiency | % | 95.2048 | 95.2048
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate / Design point load |  | 1.0212 | 1.0212
76¦~40~2~8~1000~-168~ | General Pump [40] - CP : Motor: Number of operating units |  | 1 | 1
93¦~40~7~2~1000~-168~ | General Pump [40] - CP : Motor: Electricity consumption | kW | 178.5051 | 178.5051
93¦~40~7~6~1000~-168~ | General Pump [40] - CP : Motor: Shaft power | kW | 169.9272 | 169.9272
93¦~40~7~4~1000~-168~ | General Pump [40] - CP : Motor: Efficiency | % | 95.1946 | 95.1946
93¦~40~7~3~1000~-168~ | General Pump [40] - CP : Motor: Electrical loss | kW | 8.5779 | 8.5779
89¦~40~3~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate motor shaft power | kW | 173.5336 | 173.5336
93¦~6~3~1~~-46~ | Makeup / Blowdown [6] : Makeup flow | t/h | 1.5677 | 1.5677
93¦~6~3~3~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25
93¦~6~3~2~~-46~ | Makeup / Blowdown [6] : Makeup enthalpy | kJ/kg | 104.9292 | 104.9292
93¦~6~3~4~~-46~ | Makeup / Blowdown [6] : Blowdown flow | t/h | 0 | 0
93¦~6~3~6~~-46~ | Makeup / Blowdown [6] : Blowdown temperature | C | 45.3184 | 45.3184
93¦~6~3~5~~-46~ | Makeup / Blowdown [6] : Blowdown enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~11~~-46~ | Makeup / Blowdown [6] : Inlet pressure | bar | 0.45641 | 0.45641
93¦~6~3~12~~-46~ | Makeup / Blowdown [6] : Inlet flow | t/h | 426.1664 | 426.1664
93¦~6~3~14~~-46~ | Makeup / Blowdown [6] : Inlet temperature | C | 45.3184 | 45.3184
93¦~6~3~13~~-46~ | Makeup / Blowdown [6] : Inlet enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~22~~-46~ | Makeup / Blowdown [6] : Outlet flow | t/h | 427.734 | 427.734
93¦~6~3~24~~-46~ | Makeup / Blowdown [6] : Outlet temperature | C | 45.2441 | 45.2441
93¦~6~3~23~~-46~ | Makeup / Blowdown [6] : Outlet enthalpy | kJ/kg | 189.4355 | 189.4355
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~21~3~1~~-6~ | Mixer [21] : Actual mass flow fraction of 1st clockwise inlet |  | 6.2793e-10 | 6.2793e-10
93¦~21~3~3~~-6~ | Mixer [21] : Actual mass flow fraction of 3rd clockwise inlet |  | 1 | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01
93¦~25~3~1~~-6~ | Mixer [25] : Actual mass flow fraction of 1st clockwise inlet |  | 1 | 1
93¦~25~3~3~~-6~ | Mixer [25] : Actual mass flow fraction of 3rd clockwise inlet |  | 6.3462e-10 | 6.3462e-10
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7
93¦~30~3~1~~-6~ | Mixer [30] : Actual mass flow fraction of 1st clockwise inlet |  | 0.3 | 0.3
93¦~30~3~3~~-6~ | Mixer [30] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.7 | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011
93¦~33~3~1~~-6~ | Mixer [33] : Actual mass flow fraction of 1st clockwise inlet |  | 0.10989 | 0.10989
93¦~33~3~2~~-6~ | Mixer [33] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.89011 | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~39~3~2~~-6~ | Mixer [39] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99555 | 0.99555
93¦~39~3~3~~-6~ | Mixer [39] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.0044462 | 0.0044462
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.95026 | 0.95026
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.0012821 | 0.0012821
93¦~62~3~3~~-6~ | Mixer [62] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.048456 | 0.048456
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~85~3~1~~-6~ | Mixer [85] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~85~3~3~~-6~ | Mixer [85] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~90~3~1~~-6~ | Mixer [90] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~90~3~3~~-6~ | Mixer [90] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
~35~6~5~~-107~ | Pipe (PCE) [35] : Mode |  | TD | TD
~35~6~1~~-107~ | Pipe (PCE) [35] : Pressure drop from inlet to exit | bar | 1.0236 | 1.0236
~35~6~2~~-107~ | Pipe (PCE) [35] : Pressure drop as percent of exit pressure | % | 2 | 2
~35~6~4~~-107~ | Pipe (PCE) [35] : Heat loss | kW | 9.8561 | 9.8561
~36~6~5~~-107~ | Pipe (PCE) [36] : Mode |  | TD | TD
~36~6~1~~-107~ | Pipe (PCE) [36] : Pressure drop from inlet to exit | bar | 0.61306 | 0.61306
~36~6~2~~-107~ | Pipe (PCE) [36] : Pressure drop as percent of exit pressure | % | 2 | 2
~36~6~4~~-107~ | Pipe (PCE) [36] : Heat loss | kW | 10.8868 | 10.8868
~37~6~5~~-107~ | Pipe (PCE) [37] : Mode |  | TD | TD
~37~6~1~~-107~ | Pipe (PCE) [37] : Pressure drop from inlet to exit | bar | 0.29882 | 0.29882
~37~6~2~~-107~ | Pipe (PCE) [37] : Pressure drop as percent of exit pressure | % | 2 | 2
~37~6~4~~-107~ | Pipe (PCE) [37] : Heat loss | kW | 4.5745 | 4.5745
~60~6~5~~-107~ | Pipe (PCE) [60] : Mode |  | TD | TD
~60~6~1~~-107~ | Pipe (PCE) [60] : Pressure drop from inlet to exit | bar | 0.06649 | 0.06649
~60~6~2~~-107~ | Pipe (PCE) [60] : Pressure drop as percent of exit pressure | % | 2 | 2
~60~6~4~~-107~ | Pipe (PCE) [60] : Heat loss | kW | 6.167 | 6.167
~61~6~5~~-107~ | Pipe (PCE) [61] : Mode |  | TD | TD
~61~6~1~~-107~ | Pipe (PCE) [61] : Pressure drop from inlet to exit | bar | 0.025196 | 0.025196
~61~6~2~~-107~ | Pipe (PCE) [61] : Pressure drop as percent of exit pressure | % | 2 | 2
~61~6~4~~-107~ | Pipe (PCE) [61] : Heat loss | kW | 3.1485 | 3.1485
~63~6~5~~-107~ | Pipe (PCE) [63] : Mode |  | TD | TD
~63~6~1~~-107~ | Pipe (PCE) [63] : Pressure drop from inlet to exit | bar | 0.015294 | 0.015294
~63~6~2~~-107~ | Pipe (PCE) [63] : Pressure drop as percent of exit pressure | % | 2 | 2
~63~6~4~~-107~ | Pipe (PCE) [63] : Heat loss | kW | 4.3224 | 4.3224
~64~6~5~~-107~ | Pipe (PCE) [64] : Mode |  | TD | TD
~64~6~1~~-107~ | Pipe (PCE) [64] : Pressure drop from inlet to exit | bar | 0.005549 | 0.005549
~64~6~2~~-107~ | Pipe (PCE) [64] : Pressure drop as percent of exit pressure | % | 2 | 2
~64~6~4~~-107~ | Pipe (PCE) [64] : Heat loss | kW | 2.9977 | 2.9977
~73~6~5~~-107~ | Pipe (PCE) [73] : Mode |  | TD | TD
~73~6~1~~-107~ | Pipe (PCE) [73] : Pressure drop from inlet to exit | bar | 0.16876 | 0.16876
~73~6~2~~-107~ | Pipe (PCE) [73] : Pressure drop as percent of exit pressure | % | 2 | 2
~73~6~4~~-107~ | Pipe (PCE) [73] : Heat loss | kW | 8.3897 | 8.3897
~74~6~5~~-107~ | Pipe (PCE) [74] : Mode |  | TD | TD
~74~6~1~~-107~ | Pipe (PCE) [74] : Pressure drop from inlet to exit | bar | 1.425 | 1.425
~74~6~2~~-107~ | Pipe (PCE) [74] : Pressure drop as percent of exit pressure | % | 1 | 1
~74~6~4~~-107~ | Pipe (PCE) [74] : Heat loss | kW | 258.6647 | 258.6647
~75~6~5~~-107~ | Pipe (PCE) [75] : Mode |  | TD | TD
~75~6~1~~-107~ | Pipe (PCE) [75] : Pressure drop from inlet to exit | bar | 0.28487 | 0.28487
~75~6~2~~-107~ | Pipe (PCE) [75] : Pressure drop as percent of exit pressure | % | 1 | 1
~75~6~4~~-107~ | Pipe (PCE) [75] : Heat loss | kW | 221.2572 | 221.2572
~76~6~5~~-107~ | Pipe (PCE) [76] : Mode |  | TD | TD
~76~6~1~~-107~ | Pipe (PCE) [76] : Pressure drop from inlet to exit | bar | 1.5127 | 1.5127
~76~6~2~~-107~ | Pipe (PCE) [76] : Pressure drop as percent of exit pressure | % | 1 | 1
~76~6~4~~-107~ | Pipe (PCE) [76] : Heat loss | kW | 151.7183 | 151.7183
82¦71¦~82~10~3~~-100~ | Pump (PCE) [82] - CWP-1 : Mode |  | TD | TD
82¦71¦~82~10~7~~-100~ | Pump (PCE) [82] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~82~10~6~~-100~ | Pump (PCE) [82] - CWP-1 : Pump head | m | 28.9733 | 28.9733
83¦93¦~82~3~15~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~82~3~18~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~82~3~16~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~82~3~12~~-100~ | Pump (PCE) [82] - CWP-1 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~82~3~13~~-100~ | Pump (PCE) [82] - CWP-1 : Shaft work per station | kW | 1063.4344 | 1063.4344
82¦71¦~82~10~1~~-100~ | Pump (PCE) [82] - CWP-1 : Hydraulic work per station | kW | 1031.5314 | 1031.5314
82¦71¦~82~10~2~~-100~ | Pump (PCE) [82] - CWP-1 : Electricity consumption per station | kW | 1101.7532 | 1101.7532
83¦93¦~82~3~5~~-100~ | Pump (PCE) [82] - CWP-1 : Suction flow | t/h | 9802.543 | 9802.543
83¦93¦~82~3~27~~-100~ | Pump (PCE) [82] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~82~3~28~~-100~ | Pump (PCE) [82] - CWP-1 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~82~3~4~~-100~ | Pump (PCE) [82] - CWP-1 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~82~3~8~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge flow | t/h | 9802.543 | 9802.543
83¦93¦~82~3~29~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~82~3~6~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~82~3~7~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~82~6~1~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Mode |  | Design | Design
91¦~82~1~7~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate power | kW | 1140.2465 | 1140.2465
91¦~82~1~19~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate efficiency | % | 96.5341 | 96.5341
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~82~2~8~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~82~7~2~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electricity consumption | kW | 1101.7532 | 1101.7532
93¦~82~7~6~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Shaft power | kW | 1063.4344 | 1063.4344
93¦~82~7~4~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Efficiency | % | 96.522 | 96.522
93¦~82~7~3~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electrical loss | kW | 38.3188 | 38.3188
89¦~82~3~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate motor shaft power | kW | 1100.5889 | 1100.5889
82¦71¦~83~10~3~~-100~ | Pump (PCE) [83] - CWP-2 : Mode |  | TD | TD
82¦71¦~83~10~7~~-100~ | Pump (PCE) [83] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~83~10~6~~-100~ | Pump (PCE) [83] - CWP-2 : Pump head | m | 28.9733 | 28.9733
83¦93¦~83~3~15~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~83~3~18~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~83~3~16~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~83~3~12~~-100~ | Pump (PCE) [83] - CWP-2 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~83~3~13~~-100~ | Pump (PCE) [83] - CWP-2 : Shaft work per station | kW | 1063.4344 | 1063.4344
82¦71¦~83~10~1~~-100~ | Pump (PCE) [83] - CWP-2 : Hydraulic work per station | kW | 1031.5314 | 1031.5314
82¦71¦~83~10~2~~-100~ | Pump (PCE) [83] - CWP-2 : Electricity consumption per station | kW | 1101.7532 | 1101.7532
83¦93¦~83~3~5~~-100~ | Pump (PCE) [83] - CWP-2 : Suction flow | t/h | 9802.543 | 9802.543
83¦93¦~83~3~27~~-100~ | Pump (PCE) [83] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~83~3~28~~-100~ | Pump (PCE) [83] - CWP-2 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~83~3~4~~-100~ | Pump (PCE) [83] - CWP-2 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~83~3~8~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge flow | t/h | 9802.543 | 9802.543
83¦93¦~83~3~29~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~83~3~6~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~83~3~7~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~83~6~1~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Mode |  | Design | Design
91¦~83~1~7~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate power | kW | 1140.2465 | 1140.2465
91¦~83~1~19~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate efficiency | % | 96.5341 | 96.5341
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~83~2~8~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~83~7~2~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electricity consumption | kW | 1101.7532 | 1101.7532
93¦~83~7~6~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Shaft power | kW | 1063.4344 | 1063.4344
93¦~83~7~4~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Efficiency | % | 96.522 | 96.522
93¦~83~7~3~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electrical loss | kW | 38.3188 | 38.3188
89¦~83~3~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate motor shaft power | kW | 1100.5889 | 1100.5889
93¦~8~3~64~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air path heat transfer | kW | 11970.7734 | 11970.7734
93¦~8~3~44~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Secondary air path heat transfer | kW | 42570.0469 | 42570.0469
82¦71¦~8~5~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Total heat transfer | kW | 54540.8203 | 54540.8203
93¦~8~3~69~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Heat transfer duty ratio (Qpa / Qsa) | % | 28.1202 | 28.1202
93¦~8~3~24~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Average cold end temperature (ACET) | C | 86.9033 | 86.9033
93¦~8~3~191~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O dew point temperature | C | 49.3361 | 49.3361
93¦~8~3~138~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit sulfur dew point temperature | C | -273.15 | -273.15
93¦~8~3~139~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas sulfur dew point temperature within air heater | C | -273.15 | -273.15
93¦~8~3~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit O2 mol% | % | 5.1747 | 5.1747
93¦~8~3~12~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit CO2 mol% | % | 11.8817 | 11.8817
93¦~8~3~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O mol% | % | 12.0932 | 12.0932
82¦71¦~8~5~2~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit N2 mol% | % | 69.9911 | 69.9911
93¦~8~3~132~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit Ar mol% | % | 0.84192 | 0.84192
93¦~8~3~131~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit SO2 mol% | % | 0.017412 | 0.017412
82¦71¦~1~5~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~1~5~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~1~1~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of existing units |  | 1 | 1
93¦~1~3~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1
93¦~1~3~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Total shaft power | kW | 1803.3745 | 1803.3745
93¦~1~3~1~~-85~ | ST-Driven Pump [1] - BFPT-A : Shaft power per unit | kW | 1803.3745 | 1803.3745
93¦~1~3~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping power per unit | kW | 1746.9426 | 1746.9426
93¦~1~3~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping flow per unit | t/h | 274.5413 | 274.5413
93¦~1~3~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump pressure rise (before control valve) | bar | 152.6129 | 152.6129
93¦~1~3~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall pressure rise | bar | 152.6129 | 152.6129
93¦~1~3~6~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~1~3~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall apparent isentropic efficiency | % | 74.4501 | 74.4501
93¦~1~3~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600 | 3600
93¦~1~3~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss per unit | kW | 56.4319 | 56.4319
93¦~1~3~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~1~10~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Type of inlet control |  | Sliding | Sliding
93¦~1~3~29~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Steam supply pressure | bar | 8.607 | 8.607
93¦~1~3~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet pressure | bar | 8.607 | 8.607
93¦~1~3~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet temperature | C | 361.1295 | 361.1295
93¦~1~3~14~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet flow per unit | t/h | 8.8676 | 8.8676
93¦~1~3~13~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~1~3~16~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion massflow per unit | t/h | 8.8676 | 8.8676
93¦~1~3~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial pressure | bar | 8.607 | 8.607
93¦~1~3~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~1~3~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~1~3~25~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2450.488 | 2450.488
93¦~1~3~21~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~1~3~22~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~1~3~24~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet flow per unit | t/h | 8.8676 | 8.8676
93¦~1~3~23~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet enthalpy | kJ/kg | 2450.488 | 2450.488
72¦79¦93¦~1~7~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust volume flow per unit | m^3/s | 34.9577 | 34.9577
72¦79¦93¦~1~7~18~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~1~7~17~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~1~3~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual flow function | m^2 | 0.0023021 | 0.0023021
93¦~1~3~10~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual pressure ratio (blading) |  | 88.2769 | 88.2769
93¦~1~3~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry step efficiency | % | 85 | 85
93¦~1~3~1~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group overall efficiency | % | 87.5096 | 87.5096
93¦~1~3~30~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group blading efficiency | % | 87.5096 | 87.5096
93¦~1~3~50~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion power per unit | kW | 1807.8938 | 1807.8938
93¦~1~3~9~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical loss per unit | kW | 4.5197 | 4.5197
82¦71¦~86~5~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~86~5~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~86~1~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of existing units |  | 1 | 1
93¦~86~3~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1
93¦~86~3~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Total shaft power | kW | 1803.3745 | 1803.3745
93¦~86~3~1~~-85~ | ST-Driven Pump [86] - BFPT-B : Shaft power per unit | kW | 1803.3745 | 1803.3745
93¦~86~3~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping power per unit | kW | 1746.9426 | 1746.9426
93¦~86~3~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping flow per unit | t/h | 274.5413 | 274.5413
93¦~86~3~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump pressure rise (before control valve) | bar | 152.6129 | 152.6129
93¦~86~3~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall pressure rise | bar | 152.6129 | 152.6129
93¦~86~3~6~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~86~3~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall apparent isentropic efficiency | % | 74.4501 | 74.4501
93¦~86~3~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000 | 3000
93¦~86~3~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss per unit | kW | 56.4319 | 56.4319
93¦~86~3~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~86~10~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Type of inlet control |  | Sliding | Sliding
93¦~86~3~29~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Steam supply pressure | bar | 8.607 | 8.607
93¦~86~3~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet pressure | bar | 8.607 | 8.607
93¦~86~3~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet temperature | C | 361.1295 | 361.1295
93¦~86~3~14~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet flow per unit | t/h | 8.8676 | 8.8676
93¦~86~3~13~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~86~3~16~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion massflow per unit | t/h | 8.8676 | 8.8676
93¦~86~3~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial pressure | bar | 8.607 | 8.607
93¦~86~3~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~86~3~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~86~3~25~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2450.488 | 2450.488
93¦~86~3~21~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~86~3~22~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~86~3~24~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet flow per unit | t/h | 8.8676 | 8.8676
93¦~86~3~23~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet enthalpy | kJ/kg | 2450.488 | 2450.488
72¦79¦93¦~86~7~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust volume flow per unit | m^3/s | 34.9577 | 34.9577
72¦79¦93¦~86~7~18~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~86~7~17~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~86~3~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual flow function | m^2 | 0.0023021 | 0.0023021
93¦~86~3~10~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual pressure ratio (blading) |  | 88.2769 | 88.2769
93¦~86~3~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry step efficiency | % | 85 | 85
93¦~86~3~1~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group overall efficiency | % | 87.5096 | 87.5096
93¦~86~3~30~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group blading efficiency | % | 87.5096 | 87.5096
93¦~86~3~50~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion power per unit | kW | 1807.8938 | 1807.8938
93¦~86~3~9~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical loss per unit | kW | 4.5197 | 4.5197
91¦~34~1~13~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~34~1~71~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~34~3~7~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer | kW | 208.6087 | 208.6087
91¦~34~1~101~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Feedwater temperature rise (overall) | C | 0.42747 | 0.42747
82¦71¦~34~5~2~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Terminal difference | C | 11.4139 | 11.4139
91¦~34~1~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer area | m^2 | 65.2424 | 65.2424
91¦~34~1~82~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~34~3~52~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell length | m | 0 | 0
89¦~34~3~53~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell inner diameter | m | 1.1308 | 1.1308
89¦~34~3~56~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall length | m | 0 | 0
89¦~34~3~27~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall outer diameter | m | 0 | 0
89¦~34~3~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total dry weight | kg | 0 | 0
89¦~34~3~57~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~34~5~5~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total estimated installed cost | USD | 0 | 0
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~4~3~1~~-7~ | Splitter [4] : Actual flow fraction of 1st clockwise outlet |  | 0.96988 | 0.96988
93¦~4~3~3~~-7~ | Splitter [4] : Actual flow fraction of 3rd clockwise outlet |  | 0.030118 | 0.030118
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~9~3~1~~-7~ | Splitter [9] : Actual flow fraction of 1st clockwise outlet |  | 0.82992 | 0.82992
93¦~9~3~3~~-7~ | Splitter [9] : Actual flow fraction of 3rd clockwise outlet |  | 0.17008 | 0.17008
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998
93¦~18~3~1~~-7~ | Splitter [18] : Actual flow fraction of 1st clockwise outlet |  | 5.3712e-10 | 5.3712e-10
93¦~18~3~2~~-7~ | Splitter [18] : Actual flow fraction of 2nd clockwise outlet |  | 5.3712e-10 | 5.3712e-10
93¦~18~3~3~~-7~ | Splitter [18] : Actual flow fraction of 3rd clockwise outlet |  | 1 | 1
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~19~3~1~~-7~ | Splitter [19] : Actual flow fraction of 1st clockwise outlet |  | 0.93516 | 0.93516
93¦~19~3~3~~-7~ | Splitter [19] : Actual flow fraction of 3rd clockwise outlet |  | 0.06484 | 0.06484
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005
93¦~20~3~1~~-7~ | Splitter [20] : Actual flow fraction of 1st clockwise outlet |  | 0.91693 | 0.91693
93¦~20~3~2~~-7~ | Splitter [20] : Actual flow fraction of 2nd clockwise outlet |  | 0.076586 | 0.076586
93¦~20~3~3~~-7~ | Splitter [20] : Actual flow fraction of 3rd clockwise outlet |  | 0.0064856 | 0.0064856
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843
93¦~22~3~1~~-7~ | Splitter [22] : Actual flow fraction of 1st clockwise outlet |  | 0.001 | 0.001
93¦~22~3~2~~-7~ | Splitter [22] : Actual flow fraction of 2nd clockwise outlet |  | 0.00057 | 0.00057
93¦~22~3~3~~-7~ | Splitter [22] : Actual flow fraction of 3rd clockwise outlet |  | 0.99843 | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~27~3~1~~-7~ | Splitter [27] : Actual flow fraction of 1st clockwise outlet |  | 0.98945 | 0.98945
93¦~27~3~3~~-7~ | Splitter [27] : Actual flow fraction of 3rd clockwise outlet |  | 0.010545 | 0.010545
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.97513 | 0.97513
93¦~29~3~3~~-7~ | Splitter [29] : Actual flow fraction of 3rd clockwise outlet |  | 0.024868 | 0.024868
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578
93¦~32~3~1~~-7~ | Splitter [32] : Actual flow fraction of 1st clockwise outlet |  | 0.039234 | 0.039234
93¦~32~3~2~~-7~ | Splitter [32] : Actual flow fraction of 2nd clockwise outlet |  | 0.90129 | 0.90129
93¦~32~3~3~~-7~ | Splitter [32] : Actual flow fraction of 3rd clockwise outlet |  | 0.059474 | 0.059474
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.94551 | 0.94551
93¦~49~3~3~~-7~ | Splitter [49] : Actual flow fraction of 3rd clockwise outlet |  | 0.054493 | 0.054493
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~50~3~1~~-7~ | Splitter [50] : Actual flow fraction of 1st clockwise outlet |  | 0.97058 | 0.97058
93¦~50~3~3~~-7~ | Splitter [50] : Actual flow fraction of 3rd clockwise outlet |  | 0.029424 | 0.029424
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~51~3~1~~-7~ | Splitter [51] : Actual flow fraction of 1st clockwise outlet |  | 0.95838 | 0.95838
93¦~51~3~3~~-7~ | Splitter [51] : Actual flow fraction of 3rd clockwise outlet |  | 0.04162 | 0.04162
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~70~3~1~~-7~ | Splitter [70] : Actual flow fraction of 1st clockwise outlet |  | 0.40156 | 0.40156
93¦~70~3~3~~-7~ | Splitter [70] : Actual flow fraction of 3rd clockwise outlet |  | 0.59844 | 0.59844
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~71~3~1~~-7~ | Splitter [71] : Actual flow fraction of 1st clockwise outlet |  | 5.3578e-10 | 5.3578e-10
93¦~71~3~2~~-7~ | Splitter [71] : Actual flow fraction of 2nd clockwise outlet |  | 0.0053192 | 0.0053192
93¦~71~3~3~~-7~ | Splitter [71] : Actual flow fraction of 3rd clockwise outlet |  | 0.99468 | 0.99468
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~84~3~1~~-7~ | Splitter [84] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~84~3~3~~-7~ | Splitter [84] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~88~3~1~~-7~ | Splitter [88] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~88~3~3~~-7~ | Splitter [88] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~89~3~1~~-7~ | Splitter [89] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~89~3~3~~-7~ | Splitter [89] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 145.0539 | 145.0539
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 49.8498 | 49.8498
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 143.5012 | 143.5012
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 3961.7773 | 3961.7773
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 5.1747 | 5.1747
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 11.8817 | 11.8817
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 12.0932 | 12.0932
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 69.9911 | 69.9911
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.84192 | 0.84192
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.017412 | 0.017412
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 201.5122 | 201.5122
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 561.7842 | 561.7842
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 196.5543 | 196.5543
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.015669 | 0.015669
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 8.9675 | 8.9675
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9999 | 24.9999
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 5.1747 | 5.1747
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 12.0932 | 12.0932
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~23~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Mode |  | TD | TD
~23~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet mass flow | t/h | 546.5478 | 546.5478
~23~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet pressure | bar | 148.2861 | 148.2861
~23~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet enthalpy | kJ/kg | 3050.4329 | 3050.4329
~23~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet temperature | C | 418.004 | 418.004
~23~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit mass flow | t/h | 546.5478 | 546.5478
~23~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit pressure | bar | 146.8179 | 146.8179
~23~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit temperature | C | 490 | 490
~23~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit enthalpy | kJ/kg | 3286.0432 | 3286.0432
~23~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas mass flow | t/h | 837.5018 | 837.5018
~23~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Flyash mass flow | t/h | 4.1031 | 4.1031
~23~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas inlet temperature | C | 1131.2001 | 1131.2001
~23~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas exit temperature | C | 1020.9855 | 1020.9855
~23~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat transfer to steam | kW | 35770.6328 | 35770.6328
~23~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss | kW | 268.2798 | 268.2798
~23~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Radiant heat influx | kW | 1676.8239 | 1676.8239
~23~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~23~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam side pressure drop | bar | 1.4682 | 1.4682
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 547.7206 | 547.7206
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 145.3643 | 145.3643
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3359.4287 | 3359.4287
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 514.9995 | 514.9995
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 547.7206 | 547.7206
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 143.925 | 143.925
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 532.1 | 532.1
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3408.4106 | 3408.4106
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 837.5018 | 837.5018
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 4.1031 | 4.1031
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 771.387 | 771.387
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 746.0795 | 746.0795
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 7452.4644 | 7452.4644
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 55.8935 | 55.8935
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 1.4393 | 1.4393
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 544.8 | 544.8
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 149.7689 | 149.7689
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2611.5242 | 2611.5242
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 342.0345 | 342.0345
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 544.8 | 544.8
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 148.2861 | 148.2861
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 420 | 420
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3057.8013 | 3057.8013
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 837.5018 | 837.5018
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 4.1031 | 4.1031
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 746.0813 | 746.0813
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 510.2856 | 510.2856
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 67537.6406 | 67537.6406
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 506.5323 | 506.5323
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 1.4829 | 1.4829
~77~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Mode |  | TD | TD
~77~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet mass flow | t/h | 468.5106 | 468.5106
~77~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet pressure | bar | 31.266 | 31.266
~77~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet enthalpy | kJ/kg | 3047.1499 | 3047.1499
~77~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet temperature | C | 322.5885 | 322.5885
~77~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit mass flow | t/h | 468.5106 | 468.5106
~77~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit pressure | bar | 30.9564 | 30.9564
~77~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit temperature | C | 511 | 511
~77~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit enthalpy | kJ/kg | 3480.7429 | 3480.7429
~77~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas mass flow | t/h | 837.5018 | 837.5018
~77~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Flyash mass flow | t/h | 4.1031 | 4.1031
~77~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas inlet temperature | C | 981.8358 | 981.8358
~77~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas exit temperature | C | 794.4238 | 794.4238
~77~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat transfer to steam | kW | 56429.4648 | 56429.4648
~77~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss | kW | 423.221 | 423.221
~77~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Radiant heat influx | kW | 0 | 0
~77~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~77~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam side pressure drop | bar | 0.30956 | 0.30956
~78~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Mode |  | TD | TD
~78~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet mass flow | t/h | 468.5106 | 468.5106
~78~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet pressure | bar | 30.9564 | 30.9564
~78~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet enthalpy | kJ/kg | 3480.7429 | 3480.7429
~78~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet temperature | C | 511.002 | 511.002
~78~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit mass flow | t/h | 468.5106 | 468.5106
~78~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit pressure | bar | 30.6499 | 30.6499
~78~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit temperature | C | 534.1 | 534.1
~78~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit enthalpy | kJ/kg | 3533.1067 | 3533.1067
~78~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas mass flow | t/h | 837.5018 | 837.5018
~78~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Flyash mass flow | t/h | 4.1031 | 4.1031
~78~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas inlet temperature | C | 794.424 | 794.424
~78~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas exit temperature | C | 771.3864 | 771.3864
~78~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat transfer to steam | kW | 6814.8193 | 6814.8193
~78~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss | kW | 51.1111 | 51.1111
~78~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Radiant heat influx | kW | 0 | 0
~78~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~78~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam side pressure drop | bar | 0.3065 | 0.3065
~79~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Mode |  | TD | TD
~79~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet mass flow | t/h | 546.5478 | 546.5478
~79~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet pressure | bar | 146.8179 | 146.8179
~79~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet enthalpy | kJ/kg | 3286.0432 | 3286.0432
~79~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet temperature | C | 489.9973 | 489.9973
~79~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit mass flow | t/h | 546.5478 | 546.5478
~79~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit pressure | bar | 145.3642 | 145.3642
~79~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit temperature | C | 517 | 517
~79~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit enthalpy | kJ/kg | 3365.0205 | 3365.0205
~79~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas mass flow | t/h | 837.5018 | 837.5018
~79~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Flyash mass flow | t/h | 4.1031 | 4.1031
~79~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas inlet temperature | C | 1020.9857 | 1020.9857
~79~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas exit temperature | C | 981.8359 | 981.8359
~79~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat transfer to steam | kW | 11990.4297 | 11990.4297
~79~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss | kW | 89.9282 | 89.9282
~79~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Radiant heat influx | kW | 0 | 0
~79~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~79~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam side pressure drop | bar | 1.4537 | 1.4537
~14~5~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control mode |  | Down set point | Down set point
~14~5~2~~-32~ | Boiler Assembly [1]: Valve [14] : Valve current status |  | Wide open | Wide open
~14~3~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop @ VWO | bar | 0 | 0
~14~3~10~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop | bar | 1.8781 | 1.8781
~14~3~3~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet pressure | bar | 30.6499 | 30.6499
~14~3~4~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet temperature | C | 534.1028 | 534.1028
~14~3~5~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet enthalpy | kJ/kg | 3533.1067 | 3533.1067
~14~3~6~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet mass flow | t/h | 468.5106 | 468.5106
~14~3~7~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet pressure | bar | 28.7719 | 28.7719
~14~3~8~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet temperature | C | 533.2796 | 533.2796
~14~3~9~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet enthalpy | kJ/kg | 3533.1067 | 3533.1067
~80~5~1~~-32~ | Valve [80] : Pressure control mode |  | Closed | Closed
~80~5~2~~-32~ | Valve [80] : Valve current status |  | Closed | Closed
~80~3~1~~-32~ | Valve [80] : Pressure drop @ VWO | bar | 0 | 0
~80~3~10~~-32~ | Valve [80] : Pressure drop | bar | 0 | 0
~80~3~3~~-32~ | Valve [80] : Inlet pressure | bar | 31.266 | 31.266
~80~3~4~~-32~ | Valve [80] : Inlet temperature | C | 478.2809 | 478.2809
~80~3~5~~-32~ | Valve [80] : Inlet enthalpy | kJ/kg | 3406.7107 | 3406.7107
~80~3~6~~-32~ | Valve [80] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~80~3~7~~-32~ | Valve [80] : Outlet pressure | bar | 31.266 | 31.266
~80~3~8~~-32~ | Valve [80] : Outlet temperature | C | 478.2809 | 478.2809
~80~3~9~~-32~ | Valve [80] : Outlet enthalpy | kJ/kg | 3406.7107 | 3406.7107
~81~5~1~~-32~ | Valve [81] : Pressure control mode |  | Closed | Closed
~81~5~2~~-32~ | Valve [81] : Valve current status |  | Closed | Closed
~81~3~1~~-32~ | Valve [81] : Pressure drop @ VWO | bar | 0 | 0
~81~3~10~~-32~ | Valve [81] : Pressure drop | bar | 0 | 0
~81~3~3~~-32~ | Valve [81] : Inlet pressure | bar | 28.487 | 28.487
~81~3~4~~-32~ | Valve [81] : Inlet temperature | C | 476.7819 | 476.7819
~81~3~5~~-32~ | Valve [81] : Inlet enthalpy | kJ/kg | 3406.7107 | 3406.7107
~81~3~6~~-32~ | Valve [81] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~81~3~7~~-32~ | Valve [81] : Outlet pressure | bar | 28.487 | 28.487
~81~3~8~~-32~ | Valve [81] : Outlet temperature | C | 476.7819 | 476.7819
~81~3~9~~-32~ | Valve [81] : Outlet enthalpy | kJ/kg | 3406.7107 | 3406.7107
93¦~58~3~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5
93¦~58~3~2~~-14~ | Water Sink [58] : Temperature | C | 37.3673 | 37.3673
93¦~58~3~3~~-14~ | Water Sink [58] : Enthalpy | kJ/kg | 156.7739 | 156.7739
93¦~58~3~4~~-14~ | Water Sink [58] : Mass flow | t/h | 19605.0859 | 19605.0859
93¦~57~3~1~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135
93¦~57~3~2~~-9~ | Water Source [57] : Temperature | C | 27.3223 | 27.3223
93¦~57~3~3~~-9~ | Water Source [57] : Enthalpy | kJ/kg | 114.5466 | 114.5466
93¦~57~3~4~~-9~ | Water Source [57] : Mass flow | t/h | 19605.0859 | 19605.0859
~59~10~1~~-104~ | Water-cooled Condenser (PCE) [59] : Mode |  | TD | TD
~59~3~27~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975
~59~3~26~~-104~ | Water-cooled Condenser (PCE) [59] : Saturation temperature | C | 45.3132 | 45.3132
~59~3~21~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser heat rejection (per unit) | kW | 227904.375 | 227904.375
~59~3~23~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
82¦71¦~1~6~1~~-20000~ | Generator [1]: Mode |  | Design | Design
91¦~1~1~7~~-20000~ | Generator [1]: Nameplate power | kW | 183750.9062 | 183750.9062
91¦~1~1~19~~-20000~ | Generator [1]: Nameplate efficiency | % | 98.7256 | 98.7256
91¦~1~1~5~~-20000~ | Generator [1]: Nameplate / Design point load |  | 1.05 | 1.05
76¦~1~2~8~~-20000~ | Generator [1]: Number of operating units |  | 1 | 1
93¦~1~7~2~~-20000~ | Generator [1]: Generator power output | kW | 175000.875 | 175000.875
93¦~1~7~6~~-20000~ | Generator [1]: Shaft power | kW | 177291.4531 | 177291.4531
93¦~1~7~4~~-20000~ | Generator [1]: Generator efficiency | % | 98.708 | 98.708
93¦~1~7~3~~-20000~ | Generator [1]: Total loss | kW | 2290.5732 | 2290.5732
93¦~1~7~28~~-20000~ | Generator [1]: Electrical & Windage loss | kW | 2009.573 | 2009.573
93¦~1~7~29~~-20000~ | Generator [1]: Mechanical loss | kW | 281.0002 | 281.0002
86¦87¦68¦86¦86¦~13~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 175000.875 | 175000.875
86¦87¦68¦86¦86¦~13~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.708 | 98.708
86¦87¦68¦86¦86¦~13~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 275.6264 | 275.6264
86¦87¦68¦86¦86¦~13~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 91.8755 | 91.8755
86¦87¦68¦86¦86¦~13~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 204.1677 | 204.1677
86¦87¦68¦86¦86¦~13~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~13~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.7256 | 98.7256
86¦87¦68¦86¦86¦~13~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 149.625 | 149.625
86¦87¦68¦86¦86¦~13~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 530.8859 | 530.8859
86¦87¦68¦86¦86¦~13~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 547.7206 | 547.7206
86¦87¦68¦86¦86¦~13~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~13~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 6 | 6
86¦87¦68¦86¦86¦~13~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~13~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~13~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 183750.9062 | 183750.9062
91¦~13~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.7256 | 98.7256
91¦~13~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~13~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~13~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 175000.875 | 175000.875
93¦~13~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 177291.4531 | 177291.4531
93¦~13~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.708 | 98.708
93¦~13~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 2290.5732 | 2290.5732
93¦~13~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 2009.573 | 2009.573
93¦~13~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 281.0002 | 281.0002
86¦87¦68¦86¦86¦~13~3~30~~-4100~ | ST Assembly [1]: Steam turbine length (including gear box) | m | 19.7652 | 19.7652
86¦87¦68¦86¦86¦~13~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.4396 | 4.4396
86¦87¦68¦86¦86¦~13~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight (including weight of gear box) | kg | 287790.3438 | 287790.3438
86¦87¦68¦86¦86¦~13~3~33~~-4100~ | ST Assembly [1]: Gear box length | m | 0 | 0
86¦87¦68¦86¦86¦~13~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 11.4655 | 11.4655
86¦87¦68¦86¦86¦~13~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.733 | 3.733
86¦87¦68¦86¦86¦~13~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 236733.875 | 236733.875
86¦87¦68¦86¦86¦~13~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 31.2307 | 31.2307
86¦87¦68¦86¦86¦~13~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.4396 | 4.4396
86¦87¦68¦86¦86¦~13~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 524524.1875 | 524524.1875
86¦87¦68¦86¦86¦~13~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 33.347 | 33.347
86¦87¦68¦86¦86¦~13~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.3275 | 5.3275
86¦87¦68¦86¦86¦~13~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 37296480 | 37296480
86¦87¦68¦86¦86¦~13~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 42997264 | 42997264
82¦71¦~13~10~3~~-11~ | ST Assembly [1]: ST Group [13] : Mode |  | Design | Design
82¦71¦~13~10~4~~-11~ | ST Assembly [1]: ST Group [13] : Type of inlet control |  | Sliding | Sliding
93¦~13~3~29~~-11~ | ST Assembly [1]: ST Group [13] : Steam supply pressure | bar | 142.5 | 142.5
93¦~13~3~11~~-11~ | ST Assembly [1]: ST Group [13] : Inlet pressure | bar | 142.5 | 142.5
93¦~13~3~12~~-11~ | ST Assembly [1]: ST Group [13] : Inlet temperature | C | 530.8859 | 530.8859
93¦~13~3~14~~-11~ | ST Assembly [1]: ST Group [13] : Inlet flow | t/h | 547.7206 | 547.7206
93¦~13~3~13~~-11~ | ST Assembly [1]: ST Group [13] : Inlet enthalpy | kJ/kg | 3406.7107 | 3406.7107
93¦~13~3~16~~-11~ | ST Assembly [1]: ST Group [13] : Expansion massflow | t/h | 547.2429 | 547.2429
93¦~13~3~4~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial pressure | bar | 142.5 | 142.5
93¦~13~3~15~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial enthalpy | kJ/kg | 3406.7107 | 3406.7107
93¦~13~3~6~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end pressure (before Exhaust Loss) | bar | 52.204 | 52.204
93¦~13~3~25~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3146.207 | 3146.207
93¦~13~3~21~~-11~ | ST Assembly [1]: ST Group [13] : Outlet pressure | bar | 52.204 | 52.204
93¦~13~3~22~~-11~ | ST Assembly [1]: ST Group [13] : Outlet temperature | C | 381.5247 | 381.5247
93¦~13~3~24~~-11~ | ST Assembly [1]: ST Group [13] : Outlet flow | t/h | 547.2429 | 547.2429
93¦~13~3~23~~-11~ | ST Assembly [1]: ST Group [13] : Outlet enthalpy | kJ/kg | 3146.207 | 3146.207
72¦79¦93¦~13~7~15~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust volume flow | m^3/s | 8.0807 | 8.0807
72¦79¦93¦~13~7~18~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~13~7~17~~-11~ | ST Assembly [1]: ST Group [13] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~13~3~7~~-11~ | ST Assembly [1]: ST Group [13] : Actual flow function | m^2 | 0.0092373 | 0.0092373
93¦~13~3~10~~-11~ | ST Assembly [1]: ST Group [13] : Actual pressure ratio (blading) |  | 2.7297 | 2.7297
93¦~13~3~3~~-11~ | ST Assembly [1]: ST Group [13] : Dry step efficiency | % | 85.1821 | 85.1821
93¦~13~3~1~~-11~ | ST Assembly [1]: ST Group [13] : Group overall efficiency | % | 86.4442 | 86.4442
93¦~13~3~30~~-11~ | ST Assembly [1]: ST Group [13] : Group blading efficiency | % | 86.4442 | 86.4442
93¦~13~3~50~~-11~ | ST Assembly [1]: ST Group [13] : Expansion power | kW | 39600.2656 | 39600.2656
93¦~13~3~8~~-11~ | ST Assembly [1]: ST Group [13] : Shaft power | kW | 39501.2617 | 39501.2617
93¦~13~3~9~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical loss | kW | 99.0006 | 99.0006
82¦71¦~15~10~3~~-11~ | ST Assembly [1]: ST Group [15] : Mode |  | Design | Design
82¦71¦~15~10~4~~-11~ | ST Assembly [1]: ST Group [15] : Type of inlet control |  | Sliding | Sliding
93¦~15~3~29~~-11~ | ST Assembly [1]: ST Group [15] : Steam supply pressure | bar | 52.204 | 52.204
93¦~15~3~11~~-11~ | ST Assembly [1]: ST Group [15] : Inlet pressure | bar | 52.204 | 52.204
93¦~15~3~12~~-11~ | ST Assembly [1]: ST Group [15] : Inlet temperature | C | 381.5247 | 381.5247
93¦~15~3~14~~-11~ | ST Assembly [1]: ST Group [15] : Inlet flow | t/h | 511.7598 | 511.7598
93¦~15~3~13~~-11~ | ST Assembly [1]: ST Group [15] : Inlet enthalpy | kJ/kg | 3146.207 | 3146.207
93¦~15~3~16~~-11~ | ST Assembly [1]: ST Group [15] : Expansion massflow | t/h | 511.7598 | 511.7598
93¦~15~3~4~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial pressure | bar | 52.204 | 52.204
93¦~15~3~15~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial enthalpy | kJ/kg | 3146.207 | 3146.207
93¦~15~3~6~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end pressure (before Exhaust Loss) | bar | 31.266 | 31.266
93¦~15~3~25~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3047.1499 | 3047.1499
93¦~15~3~21~~-11~ | ST Assembly [1]: ST Group [15] : Outlet pressure | bar | 31.266 | 31.266
93¦~15~3~22~~-11~ | ST Assembly [1]: ST Group [15] : Outlet temperature | C | 322.5885 | 322.5885
93¦~15~3~24~~-11~ | ST Assembly [1]: ST Group [15] : Outlet flow | t/h | 511.7598 | 511.7598
93¦~15~3~23~~-11~ | ST Assembly [1]: ST Group [15] : Outlet enthalpy | kJ/kg | 3047.1499 | 3047.1499
72¦79¦93¦~15~7~15~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust volume flow | m^3/s | 11.6242 | 11.6242
72¦79¦93¦~15~7~18~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~15~7~17~~-11~ | ST Assembly [1]: ST Group [15] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~15~3~7~~-11~ | ST Assembly [1]: ST Group [15] : Actual flow function | m^2 | 0.021481 | 0.021481
93¦~15~3~10~~-11~ | ST Assembly [1]: ST Group [15] : Actual pressure ratio (blading) |  | 1.6697 | 1.6697
93¦~15~3~3~~-11~ | ST Assembly [1]: ST Group [15] : Dry step efficiency | % | 72.8201 | 72.8201
93¦~15~3~1~~-11~ | ST Assembly [1]: ST Group [15] : Group overall efficiency | % | 73.6887 | 73.6887
93¦~15~3~30~~-11~ | ST Assembly [1]: ST Group [15] : Group blading efficiency | % | 73.6887 | 73.6887
93¦~15~3~50~~-11~ | ST Assembly [1]: ST Group [15] : Expansion power | kW | 14081.7285 | 14081.7285
93¦~15~3~8~~-11~ | ST Assembly [1]: ST Group [15] : Shaft power | kW | 14046.5234 | 14046.5234
93¦~15~3~9~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical loss | kW | 35.2043 | 35.2043
82¦71¦~26~10~3~~-11~ | ST Assembly [1]: ST Group [26] : Mode |  | Design | Design
82¦71¦~26~10~4~~-11~ | ST Assembly [1]: ST Group [26] : Type of inlet control |  | Sliding | Sliding
93¦~26~3~29~~-11~ | ST Assembly [1]: ST Group [26] : Steam supply pressure | bar | 28.487 | 28.487
93¦~26~3~11~~-11~ | ST Assembly [1]: ST Group [26] : Inlet pressure | bar | 28.487 | 28.487
93¦~26~3~12~~-11~ | ST Assembly [1]: ST Group [26] : Inlet temperature | C | 532.3978 | 532.3978
93¦~26~3~14~~-11~ | ST Assembly [1]: ST Group [26] : Inlet flow | t/h | 463.57 | 463.57
93¦~26~3~13~~-11~ | ST Assembly [1]: ST Group [26] : Inlet enthalpy | kJ/kg | 3531.4065 | 3531.4065
93¦~26~3~16~~-11~ | ST Assembly [1]: ST Group [26] : Expansion massflow | t/h | 463.57 | 463.57
93¦~26~3~4~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial pressure | bar | 28.487 | 28.487
93¦~26~3~15~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial enthalpy | kJ/kg | 3531.4065 | 3531.4065
93¦~26~3~6~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end pressure (before Exhaust Loss) | bar | 15.24 | 15.24
93¦~26~3~25~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3341.123 | 3341.123
93¦~26~3~21~~-11~ | ST Assembly [1]: ST Group [26] : Outlet pressure | bar | 15.24 | 15.24
93¦~26~3~22~~-11~ | ST Assembly [1]: ST Group [26] : Outlet temperature | C | 439.2987 | 439.2987
93¦~26~3~24~~-11~ | ST Assembly [1]: ST Group [26] : Outlet flow | t/h | 463.57 | 463.57
93¦~26~3~23~~-11~ | ST Assembly [1]: ST Group [26] : Outlet enthalpy | kJ/kg | 3341.123 | 3341.123
72¦79¦93¦~26~7~15~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust volume flow | m^3/s | 27.3343 | 27.3343
72¦79¦93¦~26~7~18~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~26~7~17~~-11~ | ST Assembly [1]: ST Group [26] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~26~3~7~~-11~ | ST Assembly [1]: ST Group [26] : Actual flow function | m^2 | 0.040887 | 0.040887
93¦~26~3~10~~-11~ | ST Assembly [1]: ST Group [26] : Actual pressure ratio (blading) |  | 1.8692 | 1.8692
93¦~26~3~3~~-11~ | ST Assembly [1]: ST Group [26] : Dry step efficiency | % | 88.6914 | 88.6914
93¦~26~3~1~~-11~ | ST Assembly [1]: ST Group [26] : Group overall efficiency | % | 89.1568 | 89.1568
93¦~26~3~30~~-11~ | ST Assembly [1]: ST Group [26] : Group blading efficiency | % | 89.1568 | 89.1568
93¦~26~3~50~~-11~ | ST Assembly [1]: ST Group [26] : Expansion power | kW | 24503.0762 | 24503.0762
93¦~26~3~8~~-11~ | ST Assembly [1]: ST Group [26] : Shaft power | kW | 24441.8164 | 24441.8164
93¦~26~3~9~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical loss | kW | 61.2576 | 61.2576
82¦71¦~28~10~3~~-11~ | ST Assembly [1]: ST Group [28] : Mode |  | Design | Design
82¦71¦~28~10~4~~-11~ | ST Assembly [1]: ST Group [28] : Type of inlet control |  | Sliding | Sliding
93¦~28~3~29~~-11~ | ST Assembly [1]: ST Group [28] : Steam supply pressure | bar | 15.24 | 15.24
93¦~28~3~11~~-11~ | ST Assembly [1]: ST Group [28] : Inlet pressure | bar | 15.24 | 15.24
93¦~28~3~12~~-11~ | ST Assembly [1]: ST Group [28] : Inlet temperature | C | 439.2987 | 439.2987
93¦~28~3~14~~-11~ | ST Assembly [1]: ST Group [28] : Inlet flow | t/h | 452.0421 | 452.0421
93¦~28~3~13~~-11~ | ST Assembly [1]: ST Group [28] : Inlet enthalpy | kJ/kg | 3341.123 | 3341.123
93¦~28~3~16~~-11~ | ST Assembly [1]: ST Group [28] : Expansion massflow | t/h | 452.0421 | 452.0421
93¦~28~3~4~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial pressure | bar | 15.24 | 15.24
93¦~28~3~15~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial enthalpy | kJ/kg | 3341.123 | 3341.123
93¦~28~3~6~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end pressure (before Exhaust Loss) | bar | 8.607 | 8.607
93¦~28~3~25~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3184.4282 | 3184.4282
93¦~28~3~21~~-11~ | ST Assembly [1]: ST Group [28] : Outlet pressure | bar | 8.607 | 8.607
93¦~28~3~22~~-11~ | ST Assembly [1]: ST Group [28] : Outlet temperature | C | 361.1295 | 361.1295
93¦~28~3~24~~-11~ | ST Assembly [1]: ST Group [28] : Outlet flow | t/h | 452.0421 | 452.0421
93¦~28~3~23~~-11~ | ST Assembly [1]: ST Group [28] : Outlet enthalpy | kJ/kg | 3184.4282 | 3184.4282
72¦79¦93¦~28~7~15~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust volume flow | m^3/s | 42.0979 | 42.0979
72¦79¦93¦~28~7~18~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~28~7~17~~-11~ | ST Assembly [1]: ST Group [28] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~28~3~7~~-11~ | ST Assembly [1]: ST Group [28] : Actual flow function | m^2 | 0.070175 | 0.070175
93¦~28~3~10~~-11~ | ST Assembly [1]: ST Group [28] : Actual pressure ratio (blading) |  | 1.7707 | 1.7707
93¦~28~3~3~~-11~ | ST Assembly [1]: ST Group [28] : Dry step efficiency | % | 89.8737 | 89.8737
93¦~28~3~1~~-11~ | ST Assembly [1]: ST Group [28] : Group overall efficiency | % | 90.2717 | 90.2717
93¦~28~3~30~~-11~ | ST Assembly [1]: ST Group [28] : Group blading efficiency | % | 90.2717 | 90.2717
93¦~28~3~50~~-11~ | ST Assembly [1]: ST Group [28] : Expansion power | kW | 19676.0508 | 19676.0508
93¦~28~3~8~~-11~ | ST Assembly [1]: ST Group [28] : Shaft power | kW | 19626.8613 | 19626.8613
93¦~28~3~9~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical loss | kW | 49.1901 | 49.1901
82¦71¦~44~10~3~~-11~ | ST Assembly [1]: ST Group [44] : Mode |  | Design | Design
82¦71¦~44~10~4~~-11~ | ST Assembly [1]: ST Group [44] : Type of inlet control |  | Sliding | Sliding
93¦~44~3~29~~-11~ | ST Assembly [1]: ST Group [44] : Steam supply pressure | bar | 8.607 | 8.607
93¦~44~3~11~~-11~ | ST Assembly [1]: ST Group [44] : Inlet pressure | bar | 8.607 | 8.607
93¦~44~3~12~~-11~ | ST Assembly [1]: ST Group [44] : Inlet temperature | C | 361.1295 | 361.1295
93¦~44~3~14~~-11~ | ST Assembly [1]: ST Group [44] : Inlet flow | t/h | 407.4222 | 407.4222
93¦~44~3~13~~-11~ | ST Assembly [1]: ST Group [44] : Inlet enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~44~3~16~~-11~ | ST Assembly [1]: ST Group [44] : Expansion massflow | t/h | 407.4222 | 407.4222
93¦~44~3~4~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial pressure | bar | 8.607 | 8.607
93¦~44~3~15~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial enthalpy | kJ/kg | 3184.4282 | 3184.4282
93¦~44~3~6~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end pressure (before Exhaust Loss) | bar | 3.391 | 3.391
93¦~44~3~25~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2962.8953 | 2962.8953
93¦~44~3~21~~-11~ | ST Assembly [1]: ST Group [44] : Outlet pressure | bar | 3.391 | 3.391
93¦~44~3~22~~-11~ | ST Assembly [1]: ST Group [44] : Outlet temperature | C | 248.1745 | 248.1745
93¦~44~3~24~~-11~ | ST Assembly [1]: ST Group [44] : Outlet flow | t/h | 407.4222 | 407.4222
93¦~44~3~23~~-11~ | ST Assembly [1]: ST Group [44] : Outlet enthalpy | kJ/kg | 2962.8953 | 2962.8953
72¦79¦93¦~44~7~15~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust volume flow | m^3/s | 79.338 | 79.338
72¦79¦93¦~44~7~18~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~44~7~17~~-11~ | ST Assembly [1]: ST Group [44] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~44~3~7~~-11~ | ST Assembly [1]: ST Group [44] : Actual flow function | m^2 | 0.10577 | 0.10577
93¦~44~3~10~~-11~ | ST Assembly [1]: ST Group [44] : Actual pressure ratio (blading) |  | 2.5382 | 2.5382
93¦~44~3~3~~-11~ | ST Assembly [1]: ST Group [44] : Dry step efficiency | % | 90.9151 | 90.9151
93¦~44~3~1~~-11~ | ST Assembly [1]: ST Group [44] : Group overall efficiency | % | 91.5075 | 91.5075
93¦~44~3~30~~-11~ | ST Assembly [1]: ST Group [44] : Group blading efficiency | % | 91.5075 | 91.5075
93¦~44~3~50~~-11~ | ST Assembly [1]: ST Group [44] : Expansion power | kW | 25071.8887 | 25071.8887
93¦~44~3~8~~-11~ | ST Assembly [1]: ST Group [44] : Shaft power | kW | 25009.209 | 25009.209
93¦~44~3~9~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical loss | kW | 62.6797 | 62.6797
82¦71¦~45~10~3~~-11~ | ST Assembly [1]: ST Group [45] : Mode |  | Design | Design
82¦71¦~45~10~4~~-11~ | ST Assembly [1]: ST Group [45] : Type of inlet control |  | Sliding | Sliding
93¦~45~3~29~~-11~ | ST Assembly [1]: ST Group [45] : Steam supply pressure | bar | 3.391 | 3.391
93¦~45~3~11~~-11~ | ST Assembly [1]: ST Group [45] : Inlet pressure | bar | 3.391 | 3.391
93¦~45~3~12~~-11~ | ST Assembly [1]: ST Group [45] : Inlet temperature | C | 248.1745 | 248.1745
93¦~45~3~14~~-11~ | ST Assembly [1]: ST Group [45] : Inlet flow | t/h | 385.2204 | 385.2204
93¦~45~3~13~~-11~ | ST Assembly [1]: ST Group [45] : Inlet enthalpy | kJ/kg | 2962.8953 | 2962.8953
93¦~45~3~16~~-11~ | ST Assembly [1]: ST Group [45] : Expansion massflow | t/h | 385.2204 | 385.2204
93¦~45~3~4~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial pressure | bar | 3.391 | 3.391
93¦~45~3~15~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial enthalpy | kJ/kg | 2962.8953 | 2962.8953
93¦~45~3~6~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end pressure (before Exhaust Loss) | bar | 1.285 | 1.285
93¦~45~3~25~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2772.1892 | 2772.1892
93¦~45~3~21~~-11~ | ST Assembly [1]: ST Group [45] : Outlet pressure | bar | 1.285 | 1.285
93¦~45~3~22~~-11~ | ST Assembly [1]: ST Group [45] : Outlet temperature | C | 148.8532 | 148.8532
93¦~45~3~24~~-11~ | ST Assembly [1]: ST Group [45] : Outlet flow | t/h | 385.2204 | 385.2204
93¦~45~3~23~~-11~ | ST Assembly [1]: ST Group [45] : Outlet enthalpy | kJ/kg | 2772.1892 | 2772.1892
72¦79¦93¦~45~7~15~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust volume flow | m^3/s | 160.4174 | 160.4174
72¦79¦93¦~45~7~18~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~45~7~17~~-11~ | ST Assembly [1]: ST Group [45] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~45~3~7~~-11~ | ST Assembly [1]: ST Group [45] : Actual flow function | m^2 | 0.23039 | 0.23039
93¦~45~3~10~~-11~ | ST Assembly [1]: ST Group [45] : Actual pressure ratio (blading) |  | 2.6389 | 2.6389
93¦~45~3~3~~-11~ | ST Assembly [1]: ST Group [45] : Dry step efficiency | % | 92.0601 | 92.0601
93¦~45~3~1~~-11~ | ST Assembly [1]: ST Group [45] : Group overall efficiency | % | 92.4762 | 92.4762
93¦~45~3~30~~-11~ | ST Assembly [1]: ST Group [45] : Group blading efficiency | % | 92.4762 | 92.4762
93¦~45~3~50~~-11~ | ST Assembly [1]: ST Group [45] : Expansion power | kW | 20406.959 | 20406.959
93¦~45~3~8~~-11~ | ST Assembly [1]: ST Group [45] : Shaft power | kW | 20355.9414 | 20355.9414
93¦~45~3~9~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical loss | kW | 51.0173 | 51.0173
82¦71¦~46~10~3~~-11~ | ST Assembly [1]: ST Group [46] : Mode |  | Design | Design
82¦71¦~46~10~4~~-11~ | ST Assembly [1]: ST Group [46] : Type of inlet control |  | Sliding | Sliding
93¦~46~3~29~~-11~ | ST Assembly [1]: ST Group [46] : Steam supply pressure | bar | 1.285 | 1.285
93¦~46~3~11~~-11~ | ST Assembly [1]: ST Group [46] : Inlet pressure | bar | 1.285 | 1.285
93¦~46~3~12~~-11~ | ST Assembly [1]: ST Group [46] : Inlet temperature | C | 148.8532 | 148.8532
93¦~46~3~14~~-11~ | ST Assembly [1]: ST Group [46] : Inlet flow | t/h | 373.8855 | 373.8855
93¦~46~3~13~~-11~ | ST Assembly [1]: ST Group [46] : Inlet enthalpy | kJ/kg | 2772.1892 | 2772.1892
93¦~46~3~16~~-11~ | ST Assembly [1]: ST Group [46] : Expansion massflow | t/h | 373.8855 | 373.8855
93¦~46~3~4~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial pressure | bar | 1.285 | 1.285
93¦~46~3~15~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial enthalpy | kJ/kg | 2772.1892 | 2772.1892
93¦~46~3~6~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end pressure (before Exhaust Loss) | bar | 0.78 | 0.78
93¦~46~3~25~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2688.509 | 2688.509
93¦~46~3~21~~-11~ | ST Assembly [1]: ST Group [46] : Outlet pressure | bar | 0.78 | 0.78
93¦~46~3~22~~-11~ | ST Assembly [1]: ST Group [46] : Outlet temperature | C | 104.8294 | 104.8294
93¦~46~3~24~~-11~ | ST Assembly [1]: ST Group [46] : Outlet flow | t/h | 373.8855 | 373.8855
93¦~46~3~23~~-11~ | ST Assembly [1]: ST Group [46] : Outlet enthalpy | kJ/kg | 2688.509 | 2688.509
72¦79¦93¦~46~7~15~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust volume flow | m^3/s | 229.7126 | 229.7126
72¦79¦93¦~46~7~18~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~46~7~17~~-11~ | ST Assembly [1]: ST Group [46] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~46~3~7~~-11~ | ST Assembly [1]: ST Group [46] : Actual flow function | m^2 | 0.5312 | 0.5312
93¦~46~3~10~~-11~ | ST Assembly [1]: ST Group [46] : Actual pressure ratio (blading) |  | 1.6474 | 1.6474
93¦~46~3~3~~-11~ | ST Assembly [1]: ST Group [46] : Dry step efficiency | % | 92.3209 | 92.3209
93¦~46~3~1~~-11~ | ST Assembly [1]: ST Group [46] : Group overall efficiency | % | 92.321 | 92.321
93¦~46~3~30~~-11~ | ST Assembly [1]: ST Group [46] : Group blading efficiency | % | 92.321 | 92.321
93¦~46~3~50~~-11~ | ST Assembly [1]: ST Group [46] : Expansion power | kW | 8690.9082 | 8690.9082
93¦~46~3~8~~-11~ | ST Assembly [1]: ST Group [46] : Shaft power | kW | 8669.1807 | 8669.1807
93¦~46~3~9~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical loss | kW | 21.7273 | 21.7273
82¦71¦~47~10~3~~-11~ | ST Assembly [1]: ST Group [47] : Mode |  | Design | Design
82¦71¦~47~10~4~~-11~ | ST Assembly [1]: ST Group [47] : Type of inlet control |  | Sliding | Sliding
93¦~47~3~29~~-11~ | ST Assembly [1]: ST Group [47] : Steam supply pressure | bar | 0.78 | 0.78
93¦~47~3~11~~-11~ | ST Assembly [1]: ST Group [47] : Inlet pressure | bar | 0.78 | 0.78
93¦~47~3~12~~-11~ | ST Assembly [1]: ST Group [47] : Inlet temperature | C | 104.8294 | 104.8294
93¦~47~3~14~~-11~ | ST Assembly [1]: ST Group [47] : Inlet flow | t/h | 358.3243 | 358.3243
93¦~47~3~13~~-11~ | ST Assembly [1]: ST Group [47] : Inlet enthalpy | kJ/kg | 2688.509 | 2688.509
93¦~47~3~16~~-11~ | ST Assembly [1]: ST Group [47] : Expansion massflow | t/h | 358.3243 | 358.3243
93¦~47~3~4~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial pressure | bar | 0.78 | 0.78
93¦~47~3~15~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial enthalpy | kJ/kg | 2688.509 | 2688.509
93¦~47~3~6~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end pressure (before Exhaust Loss) | bar | 0.283 | 0.283
93¦~47~3~25~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2539.6545 | 2539.6545
93¦~47~3~21~~-11~ | ST Assembly [1]: ST Group [47] : Outlet pressure | bar | 0.283 | 0.283
93¦~47~3~22~~-11~ | ST Assembly [1]: ST Group [47] : Outlet temperature | C | 67.7608 | 67.7608
93¦~47~3~24~~-11~ | ST Assembly [1]: ST Group [47] : Outlet flow | t/h | 358.3243 | 358.3243
93¦~47~3~23~~-11~ | ST Assembly [1]: ST Group [47] : Outlet enthalpy | kJ/kg | 2539.6545 | 2539.6545
72¦79¦93¦~47~7~15~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust volume flow | m^3/s | 530.2402 | 530.2402
72¦79¦93¦~47~7~18~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~47~7~17~~-11~ | ST Assembly [1]: ST Group [47] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~47~3~7~~-11~ | ST Assembly [1]: ST Group [47] : Actual flow function | m^2 | 0.7937 | 0.7937
93¦~47~3~10~~-11~ | ST Assembly [1]: ST Group [47] : Actual pressure ratio (blading) |  | 2.7562 | 2.7562
93¦~47~3~3~~-11~ | ST Assembly [1]: ST Group [47] : Dry step efficiency | % | 92.25 | 92.25
93¦~47~3~1~~-11~ | ST Assembly [1]: ST Group [47] : Group overall efficiency | % | 92.1687 | 92.1687
93¦~47~3~30~~-11~ | ST Assembly [1]: ST Group [47] : Group blading efficiency | % | 92.1687 | 92.1687
93¦~47~3~50~~-11~ | ST Assembly [1]: ST Group [47] : Expansion power | kW | 14816.3926 | 14816.3926
93¦~47~3~8~~-11~ | ST Assembly [1]: ST Group [47] : Shaft power | kW | 14779.3516 | 14779.3516
93¦~47~3~9~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical loss | kW | 37.0409 | 37.0409
82¦71¦~5~10~3~~-11~ | ST Assembly [1]: ST Group [5] : Mode |  | Design | Design
82¦71¦~5~10~4~~-11~ | ST Assembly [1]: ST Group [5] : Type of inlet control |  | Sliding | Sliding
93¦~5~3~29~~-11~ | ST Assembly [1]: ST Group [5] : Steam supply pressure | bar | 0.283 | 0.283
93¦~5~3~11~~-11~ | ST Assembly [1]: ST Group [5] : Inlet pressure | bar | 0.283 | 0.283
93¦~5~3~12~~-11~ | ST Assembly [1]: ST Group [5] : Inlet temperature | C | 67.7608 | 67.7608
93¦~5~3~14~~-11~ | ST Assembly [1]: ST Group [5] : Inlet flow | t/h | 347.5323 | 347.5323
93¦~5~3~13~~-11~ | ST Assembly [1]: ST Group [5] : Inlet enthalpy | kJ/kg | 2539.6545 | 2539.6545
93¦~5~3~16~~-11~ | ST Assembly [1]: ST Group [5] : Expansion massflow | t/h | 347.5323 | 347.5323
93¦~5~3~4~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial pressure | bar | 0.283 | 0.283
93¦~5~3~15~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial enthalpy | kJ/kg | 2539.6545 | 2539.6545
93¦~5~3~6~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~5~3~25~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2405.5776 | 2405.5776
93¦~5~3~21~~-11~ | ST Assembly [1]: ST Group [5] : Outlet pressure | bar | 0.0975 | 0.0975
93¦~5~3~22~~-11~ | ST Assembly [1]: ST Group [5] : Outlet temperature | C | 45.3132 | 45.3132
93¦~5~3~24~~-11~ | ST Assembly [1]: ST Group [5] : Outlet flow | t/h | 347.8045 | 347.8045
93¦~5~3~23~~-11~ | ST Assembly [1]: ST Group [5] : Outlet enthalpy | kJ/kg | 2427.1348 | 2427.1348
72¦79¦76¦~5~6~2~~-11~ | ST Assembly [1]: ST Group [5] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~5~7~15~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust volume flow per end | m^3/s | 1342.8129 | 1342.8129
72¦79¦91¦~5~5~3~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus area | m^2 | 6.8352 | 6.8352
72¦79¦93¦~5~7~16~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus velocity | m/s | 196.4563 | 196.4563
72¦79¦91¦~5~5~1~~-11~ | ST Assembly [1]: ST Group [5] : Last stage pitch diameter | mm | 2567.7771 | 2567.7771
72¦79¦91¦~5~5~2~~-11~ | ST Assembly [1]: ST Group [5] : Last stage blade length | mm | 847.3102 | 847.3102
72¦79¦93¦~5~7~18~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust loss | kJ/kg | 21.287 | 21.287
72¦79¦93¦~5~7~17~~-11~ | ST Assembly [1]: ST Group [5] : Dry exhaust loss | kJ/kg | 21.287 | 21.287
93¦~5~3~7~~-11~ | ST Assembly [1]: ST Group [5] : Actual flow function | m^2 | 1.948 | 1.948
93¦~5~3~10~~-11~ | ST Assembly [1]: ST Group [5] : Actual pressure ratio (blading) |  | 2.9026 | 2.9026
93¦~5~3~3~~-11~ | ST Assembly [1]: ST Group [5] : Dry step efficiency | % | 92.15 | 92.15
93¦~5~3~1~~-11~ | ST Assembly [1]: ST Group [5] : Group overall efficiency | % | 74.332 | 74.332
93¦~5~3~30~~-11~ | ST Assembly [1]: ST Group [5] : Group blading efficiency | % | 88.3608 | 88.3608
93¦~5~3~50~~-11~ | ST Assembly [1]: ST Group [5] : Expansion power | kW | 10888.541 | 10888.541
93¦~5~3~8~~-11~ | ST Assembly [1]: ST Group [5] : Shaft power | kW | 10861.3193 | 10861.3193
93¦~5~3~9~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical loss | kW | 27.2213 | 27.2213
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (source) | bar | 142.5 | 142.5
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (sink) | bar | 28.487 | 28.487
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (source) | C | 530.8859 | 530.8859
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (sink) | C | 476.7819 | 476.7819
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (source) | bar | 109.6154 | 109.6154
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (sink) | bar | 28.487 | 28.487
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (source) | C | 516.6677 | 516.6677
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (sink) | C | 476.7819 | 476.7819
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~1~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (source) | bar | 31.266 | 31.266
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~5~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (sink) | bar | 8.607 | 8.607
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (source) | C | 322.5885 | 322.5885
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (sink) | C | 296.1311 | 296.1311
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~2~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 91.4125 | 91.4125
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.8703 | 83.8703
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 445.3267 | 445.3267
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 485.3734 | 485.3734
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 92.7421 | 92.7421
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 407084.3438 | 407084.3438
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 143.925 | 143.925
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 532.1 | 532.1
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 547.7206 | 547.7206
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3408.4106 | 3408.4106
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 151.2666 | 151.2666
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 263.6848 | 263.6848
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 546.162 | 546.162
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 1151.7466 | 1151.7466
93¦~7~3~165~~-4200~ | Boiler Assembly [1]: Hot reheat pressure | bar | 28.7719 | 28.7719
93¦~7~3~166~~-4200~ | Boiler Assembly [1]: Hot reheat temperature | C | 533.2796 | 533.2796
93¦~7~3~167~~-4200~ | Boiler Assembly [1]: Hot reheat massflow | t/h | 468.5106 | 468.5106
93¦~7~3~168~~-4200~ | Boiler Assembly [1]: Hot reheat enthalpy | kJ/kg | 3533.1067 | 3533.1067
93¦~7~3~161~~-4200~ | Boiler Assembly [1]: Cold reheat pressure | bar | 31.266 | 31.266
93¦~7~3~162~~-4200~ | Boiler Assembly [1]: Cold reheat temperature | C | 322.5885 | 322.5885
93¦~7~3~163~~-4200~ | Boiler Assembly [1]: Cold reheat massflow | t/h | 468.5106 | 468.5106
93¦~7~3~164~~-4200~ | Boiler Assembly [1]: Cold reheat enthalpy | kJ/kg | 3047.1499 | 3047.1499
~1~1~0~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Pressure | bar | 1.0332 | 1.0332
~1~1~1~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Temperature | C | 25.85 | 25.85
~1~1~2~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mass flow | t/h | 641.2471 | 641.2471
~1~1~22~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash flow | t/h | 0 | 0
~1~1~16~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~1~18~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Relative humidity | % | 59.24 | 59.24
~1~1~20~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Entropy | kJ/kg-C | 0.18546 | 0.18546
~1~1~3~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Enthalpy | kJ/kg | 0.86557 | 0.86557
~1~1~19~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Molecular weight | M.W. | 28.7578 | 28.7578
~1~1~4~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO2 mass flow | t/h | 0.2917 | 0.2917
~1~1~5~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Volume flow | m^3/s | 149.0425 | 149.0425
~1~1~101~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Density | kg/m^3 | 1.1951 | 1.1951
~1~1~6~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of N2 | % | 76.5891 | 76.5891
~1~1~7~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of O2 | % | 20.5495 | 20.5495
~1~1~8~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~1~9~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O | % | 1.9093 | 1.9093
~1~1~10~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~1~11~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of Ar | % | 0.92239 | 0.92239
~1~1~12~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of SO2 | % | 0 | 0
~1~1~14~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~1~23~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: HCl mass flow | kg/hr | 0 | 0
~1~1~24~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: NOx mass flow | kg/hr | 0 | 0
~1~1~25~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO mass flow | kg/hr | 0 | 0
~1~1~26~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: UHC mass flow | kg/hr | 0 | 0
~1~1~29~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Hg mass flow | kg/hr | 0 | 0
~1~1~32~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~1~31~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Normal volume flow | Nm^3/hr | 499812.5312 | 499812.5312
~1~2~0~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1254 | 1.1254
~1~2~1~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 320.7365 | 320.7365
~1~2~2~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 135.2439 | 135.2439
~1~2~22~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~2~16~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~2~18~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~2~20~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.86707 | 0.86707
~1~2~3~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 305.7197 | 305.7197
~1~2~19~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~2~4~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.061575 | 0.061575
~1~2~5~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 57.2895 | 57.2895
~1~2~101~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.65575 | 0.65575
~1~2~6~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~2~7~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~2~8~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~2~9~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~2~10~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~2~12~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~2~14~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~2~23~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~2~31~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 105359.3359 | 105359.3359
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Pressure | bar | 1.1379 | 1.1379
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Temperature | C | 28.2082 | 28.2082
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mass flow | t/h | 187.4026 | 187.4026
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Relative humidity | % | 52.7378 | 52.7378
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Entropy | kJ/kg-C | 0.16412 | 0.16412
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Enthalpy | kJ/kg | 3.2646 | 3.2646
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Molecular weight | M.W. | 28.7728 | 28.7728
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO2 mass flow | t/h | 0.085323 | 0.085323
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Volume flow | m^3/s | 39.8409 | 39.8409
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Density | kg/m^3 | 1.3066 | 1.3066
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of N2 | % | 76.6959 | 76.6959
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of O2 | % | 20.5782 | 20.5782
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O | % | 1.7725 | 1.7725
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of Ar | % | 0.92367 | 0.92367
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Normal volume flow | Nm^3/hr | 145992.6875 | 145992.6875
~1~13~0~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 1.0118 | 1.0118
~1~13~1~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 1131.2 | 1131.2
~1~13~2~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 837.5011 | 837.5011
~1~13~22~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash flow | t/h | 4.1031 | 4.1031
~1~13~16~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash enthalpy | kJ/kg | 1245.9578 | 1245.9578
~1~13~18~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 2.092 | 2.092
~1~13~3~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 1341.037 | 1341.037
~1~13~19~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~13~4~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~13~5~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Volume flow | m^3/s | 924.4099 | 924.4099
~1~13~101~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 0.25166 | 0.25166
~1~13~6~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~13~7~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~13~8~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~13~9~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~13~10~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~13~12~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~13~14~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~13~23~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~13~31~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99933 | 0.99933
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 746.08 | 746.08
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 837.5011 | 837.5011
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 4.1031 | 4.1031
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 788.9393 | 788.9393
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6771 | 1.6771
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 837.4841 | 837.4841
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 679.2729 | 679.2729
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34248 | 0.34248
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.99683 | 0.99683
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 510.2871 | 510.2871
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 837.5011 | 837.5011
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 4.1031 | 4.1031
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 495.8652 | 495.8652
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.3534 | 1.3534
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 546.4401 | 546.4401
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 29.0436 | 29.0436
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 523.4327 | 523.4327
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.44445 | 0.44445
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 69.3633 | 69.3633
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 3.7173 | 3.7173
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 13.0614 | 13.0614
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.83426 | 0.83426
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 4.2757 | 4.2757
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~16~0~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 0.99434 | 0.99434
~1~16~1~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 352.4337 | 352.4337
~1~16~2~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 837.5011 | 837.5011
~1~16~22~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 4.1031 | 4.1031
~1~16~16~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 310.8754 | 310.8754
~1~16~18~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 0 | 0
~1~16~20~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 1.0898 | 1.0898
~1~16~3~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 360.8888 | 360.8888
~1~16~19~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 29.0436 | 29.0436
~1~16~4~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~16~5~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 419.0149 | 419.0149
~1~16~101~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 0.55521 | 0.55521
~1~16~6~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 69.3633 | 69.3633
~1~16~7~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 3.7173 | 3.7173
~1~16~8~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~16~9~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 13.0614 | 13.0614
~1~16~10~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.83426 | 0.83426
~1~16~12~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~16~14~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~16~23~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 4.2757 | 4.2757
~1~16~31~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~83~0~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 1.0093 | 1.0093
~1~83~1~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 1020.9855 | 1020.9855
~1~83~2~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 837.5011 | 837.5011
~1~83~22~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash flow | t/h | 4.1031 | 4.1031
~1~83~16~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash enthalpy | kJ/kg | 1119.7618 | 1119.7618
~1~83~18~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Relative humidity | % | 0 | 0
~1~83~20~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 1.9836 | 1.9836
~1~83~3~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 1193.9524 | 1193.9524
~1~83~19~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~83~4~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~83~5~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Volume flow | m^3/s | 853.9653 | 853.9653
~1~83~101~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 0.27242 | 0.27242
~1~83~6~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~83~7~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~83~8~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~83~9~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~83~10~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O liquid | % | 0 | 0
~1~83~11~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~83~12~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~83~14~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~83~23~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: HCl mass flow | kg/hr | 0 | 0
~1~83~24~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: NOx mass flow | kg/hr | 0 | 0
~1~83~25~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO mass flow | kg/hr | 0 | 0
~1~83~26~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: UHC mass flow | kg/hr | 0 | 0
~1~83~29~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Hg mass flow | kg/hr | 0 | 0
~1~83~32~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~83~31~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~89~0~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1329 | 1.1329
~1~89~1~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 27.2082 | 27.2082
~1~89~2~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 31.8729 | 31.8729
~1~89~22~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 55.664 | 55.664
~1~89~20~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~89~3~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~89~19~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~89~4~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.014511 | 0.014511
~1~89~5~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 6.7833 | 6.7833
~1~89~101~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 1.3052 | 1.3052
~1~89~6~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~89~7~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~89~8~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~89~9~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~89~10~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~89~12~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 24830.0527 | 24830.0527
~1~90~0~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.1329 | 1.1329
~1~90~1~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 27.2082 | 27.2082
~1~90~2~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 155.5296 | 155.5296
~1~90~22~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~90~16~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~90~18~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 55.664 | 55.664
~1~90~20~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.162 | 0.162
~1~90~3~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 2.247 | 2.247
~1~90~19~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7728 | 28.7728
~1~90~4~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.070811 | 0.070811
~1~90~5~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 33.1002 | 33.1002
~1~90~101~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.3052 | 1.3052
~1~90~6~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.6959 | 76.6959
~1~90~7~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5782 | 20.5782
~1~90~8~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~90~9~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.7725 | 1.7725
~1~90~10~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~90~11~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92367 | 0.92367
~1~90~12~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~90~14~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~90~23~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~90~24~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~90~25~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~90~26~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~90~29~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~90~32~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~90~31~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 121162.625 | 121162.625
~1~91~0~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.98686 | 0.98686
~1~91~1~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 140.8226 | 140.8226
~1~91~2~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 916.0822 | 916.0822
~1~91~22~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 4.1031 | 4.1031
~1~91~16~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 95.241 | 95.241
~1~91~18~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 3.2267 | 3.2267
~1~91~20~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.6314 | 0.6314
~1~91~3~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 123.8154 | 123.8154
~1~91~19~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 29.0192 | 29.0192
~1~91~4~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 165.074 | 165.074
~1~91~5~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 305.8499 | 305.8499
~1~91~101~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.832 | 0.832
~1~91~6~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 69.9911 | 69.9911
~1~91~7~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 5.1747 | 5.1747
~1~91~8~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 11.8817 | 11.8817
~1~91~9~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 12.0932 | 12.0932
~1~91~10~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~91~11~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.84192 | 0.84192
~1~91~12~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.017412 | 0.017412
~1~91~14~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.87058 | 0.87058
~1~91~23~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~91~24~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~91~25~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~91~26~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~91~29~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~91~32~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 5.8866 | 5.8866
~1~91~31~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 707597.0625 | 707597.0625
~1~92~0~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0243 | 1.0243
~1~92~1~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 273.8889 | 273.8889
~1~92~2~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 582.9519 | 582.9519
~1~92~22~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~92~16~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~92~18~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~92~20~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.80947 | 0.80947
~1~92~3~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 256.4639 | 256.4639
~1~92~19~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7578 | 28.7578
~1~92~4~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.26518 | 0.26518
~1~92~5~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 250.0536 | 250.0536
~1~92~101~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.64759 | 0.64759
~1~92~6~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.5891 | 76.5891
~1~92~7~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5495 | 20.5495
~1~92~8~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~92~9~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.9093 | 1.9093
~1~92~10~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~92~11~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92239 | 0.92239
~1~92~12~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~92~14~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~92~23~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~92~24~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~92~25~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~92~26~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~92~29~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~92~32~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~92~31~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 454375.0312 | 454375.0312
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Pressure | bar | 0.97876 | 0.97876
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Temperature | C | 140.8226 | 140.8226
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mass flow | t/h | 916.0822 | 916.0822
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash flow | t/h | 0.015669 | 0.015669
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash enthalpy | kJ/kg | 95.241 | 95.241
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Relative humidity | % | 3.2002 | 3.2002
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Entropy | kJ/kg-C | 0.63376 | 0.63376
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Enthalpy | kJ/kg | 123.8154 | 123.8154
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Molecular weight | M.W. | 29.0192 | 29.0192
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO2 mass flow | t/h | 165.0742 | 165.0742
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Volume flow | m^3/s | 308.3813 | 308.3813
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Density | kg/m^3 | 0.82517 | 0.82517
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of N2 | % | 69.9911 | 69.9911
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of O2 | % | 5.1747 | 5.1747
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of CO2 | % | 11.8817 | 11.8817
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O | % | 12.0932 | 12.0932
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of Ar | % | 0.84192 | 0.84192
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of SO2 | % | 0.017412 | 0.017412
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Dry Oxygen | % | 5.8865 | 5.8865
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Normal volume flow | Nm^3/hr | 707597.0625 | 707597.0625
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.97378 | 0.97378
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 139.7115 | 139.7115
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 916.0822 | 916.0822
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.015669 | 0.015669
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 94.2404 | 94.2404
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 3.2854 | 3.2854
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.63231 | 0.63231
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 122.6132 | 122.6132
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 29.0192 | 29.0192
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 165.0742 | 165.0742
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 309.1282 | 309.1282
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.82318 | 0.82318
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 69.9911 | 69.9911
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 5.1747 | 5.1747
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 11.8817 | 11.8817
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 12.0932 | 12.0932
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.84192 | 0.84192
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.017412 | 0.017412
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 5.8865 | 5.8865
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 707597.0625 | 707597.0625
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 145.0539 | 145.0539
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 916.0822 | 916.0822
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.015669 | 0.015669
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 99.066 | 99.066
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 2.9422 | 2.9422
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.63508 | 0.63508
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 128.3963 | 128.3963
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 29.0192 | 29.0192
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 165.0742 | 165.0742
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 301.1786 | 301.1786
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.84491 | 0.84491
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 69.9911 | 69.9911
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 5.1747 | 5.1747
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 11.8817 | 11.8817
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 12.0932 | 12.0932
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.84192 | 0.84192
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.017412 | 0.017412
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 5.8865 | 5.8865
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 707597.0625 | 707597.0625
~1~96~0~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.0317 | 1.0317
~1~96~1~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 26.2127 | 26.2127
~1~96~2~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 641.2471 | 641.2471
~1~96~22~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~96~16~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~96~18~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 57.9016 | 57.9016
~1~96~20~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.1871 | 0.1871
~1~96~3~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~96~19~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7578 | 28.7578
~1~96~4~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.2917 | 0.2917
~1~96~5~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 149.4328 | 149.4328
~1~96~101~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.192 | 1.192
~1~96~6~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.5891 | 76.5891
~1~96~7~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5495 | 20.5495
~1~96~8~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~96~9~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.9093 | 1.9093
~1~96~10~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~96~11~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92239 | 0.92239
~1~96~12~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~96~14~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~96~23~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~96~24~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~96~25~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~96~26~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~96~29~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~96~32~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~96~31~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 499812.5312 | 499812.5312
~1~97~0~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Pressure | bar | 1.0367 | 1.0367
~1~97~1~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Temperature | C | 26.2127 | 26.2127
~1~97~2~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mass flow | t/h | 641.2471 | 641.2471
~1~97~22~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash flow | t/h | 0 | 0
~1~97~16~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~97~18~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Relative humidity | % | 58.1814 | 58.1814
~1~97~20~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Entropy | kJ/kg-C | 0.18571 | 0.18571
~1~97~3~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~97~19~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Molecular weight | M.W. | 28.7578 | 28.7578
~1~97~4~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO2 mass flow | t/h | 0.2917 | 0.2917
~1~97~5~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Volume flow | m^3/s | 148.7143 | 148.7143
~1~97~101~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Density | kg/m^3 | 1.1978 | 1.1978
~1~97~6~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of N2 | % | 76.5891 | 76.5891
~1~97~7~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of O2 | % | 20.5495 | 20.5495
~1~97~8~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~97~9~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O | % | 1.9093 | 1.9093
~1~97~10~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~97~11~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of Ar | % | 0.92239 | 0.92239
~1~97~12~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of SO2 | % | 0 | 0
~1~97~14~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~97~23~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: HCl mass flow | kg/hr | 0 | 0
~1~97~24~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: NOx mass flow | kg/hr | 0 | 0
~1~97~25~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO mass flow | kg/hr | 0 | 0
~1~97~26~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: UHC mass flow | kg/hr | 0 | 0
~1~97~29~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Hg mass flow | kg/hr | 0 | 0
~1~97~32~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~97~31~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Normal volume flow | Nm^3/hr | 499812.5312 | 499812.5312
~1~98~0~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Pressure | bar | 1.1329 | 1.1329
~1~98~1~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Temperature | C | 27.2082 | 27.2082
~1~98~2~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mass flow | t/h | 187.4026 | 187.4026
~1~98~22~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash flow | t/h | 0 | 0
~1~98~16~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~98~18~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Relative humidity | % | 55.664 | 55.664
~1~98~20~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~98~3~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~98~19~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~98~4~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO2 mass flow | t/h | 0.085323 | 0.085323
~1~98~5~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Volume flow | m^3/s | 39.8834 | 39.8834
~1~98~101~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Density | kg/m^3 | 1.3052 | 1.3052
~1~98~6~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~98~7~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~98~8~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~98~9~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~98~10~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O liquid | % | 0 | 0
~1~98~11~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~98~12~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of SO2 | % | 0 | 0
~1~98~14~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~98~23~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: HCl mass flow | kg/hr | 0 | 0
~1~98~24~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: NOx mass flow | kg/hr | 0 | 0
~1~98~25~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO mass flow | kg/hr | 0 | 0
~1~98~26~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: UHC mass flow | kg/hr | 0 | 0
~1~98~29~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Hg mass flow | kg/hr | 0 | 0
~1~98~32~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Dry Oxygen | % | 20.9495 | 20.9495
~1~98~31~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Normal volume flow | Nm^3/hr | 145992.6875 | 145992.6875
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Pressure | bar | 1.1129 | 1.1129
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Temperature | C | 25.85 | 25.85
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mass flow | t/h | 187.4026 | 187.4026
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Relative humidity | % | 59.24 | 59.24
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Entropy | kJ/kg-C | 0.16252 | 0.16252
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Enthalpy | kJ/kg | 0.86495 | 0.86495
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Molecular weight | M.W. | 28.7728 | 28.7728
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO2 mass flow | t/h | 0.085323 | 0.085323
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Volume flow | m^3/s | 40.4145 | 40.4145
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Density | kg/m^3 | 1.2881 | 1.2881
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of N2 | % | 76.6959 | 76.6959
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of O2 | % | 20.5782 | 20.5782
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O | % | 1.7725 | 1.7725
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of Ar | % | 0.92367 | 0.92367
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Normal volume flow | Nm^3/hr | 145992.6875 | 145992.6875
~1~113~0~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 1.0043 | 1.0043
~1~113~1~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 794.4239 | 794.4239
~1~113~2~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 837.5011 | 837.5011
~1~113~22~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash flow | t/h | 4.1031 | 4.1031
~1~113~16~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash enthalpy | kJ/kg | 849.1645 | 849.1645
~1~113~18~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Relative humidity | % | 0 | 0
~1~113~20~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 1.7346 | 1.7346
~1~113~3~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 898.9742 | 898.9742
~1~113~19~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Molecular weight | M.W. | 29.0436 | 29.0436
~1~113~4~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~113~5~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Volume flow | m^3/s | 707.9603 | 707.9603
~1~113~101~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 0.32861 | 0.32861
~1~113~6~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of N2 | % | 69.3633 | 69.3633
~1~113~7~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of O2 | % | 3.7173 | 3.7173
~1~113~8~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~113~9~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O | % | 13.0614 | 13.0614
~1~113~10~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of Ar | % | 0.83426 | 0.83426
~1~113~12~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~113~14~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~113~23~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dry Oxygen | % | 4.2757 | 4.2757
~1~113~31~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~114~0~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 1.0018 | 1.0018
~1~114~1~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 771.3865 | 771.3865
~1~114~2~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 837.5011 | 837.5011
~1~114~22~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 4.1031 | 4.1031
~1~114~16~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 820.5182 | 820.5182
~1~114~18~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~114~20~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.7075 | 1.7075
~1~114~3~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 869.6024 | 869.6024
~1~114~19~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~114~4~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~114~5~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 694.4066 | 694.4066
~1~114~101~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.33502 | 0.33502
~1~114~6~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~114~7~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~114~8~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~114~9~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~114~10~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~114~12~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~114~14~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~114~23~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~114~31~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~1~116~0~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 1.0068 | 1.0068
~1~116~1~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 981.8359 | 981.8359
~1~116~2~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 837.5011 | 837.5011
~1~116~22~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash flow | t/h | 4.1031 | 4.1031
~1~116~16~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash enthalpy | kJ/kg | 1075.0419 | 1075.0419
~1~116~18~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Relative humidity | % | 0 | 0
~1~116~20~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 1.9437 | 1.9437
~1~116~3~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 1142.2451 | 1142.2451
~1~116~19~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Molecular weight | M.W. | 29.0436 | 29.0436
~1~116~4~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO2 mass flow | t/h | 165.0382 | 165.0382
~1~116~5~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Volume flow | m^3/s | 830.1819 | 830.1819
~1~116~101~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 0.28023 | 0.28023
~1~116~6~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of N2 | % | 69.3633 | 69.3633
~1~116~7~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of O2 | % | 3.7173 | 3.7173
~1~116~8~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~116~9~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O | % | 13.0614 | 13.0614
~1~116~10~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of Ar | % | 0.83426 | 0.83426
~1~116~12~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~116~14~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~116~23~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dry Oxygen | % | 4.2757 | 4.2757
~1~116~31~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Normal volume flow | Nm^3/hr | 646356.1875 | 646356.1875
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 0.175 | 0.175
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 285.2767 | 285.2767
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 0.26747 | 0.26747
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 8.9722 | 8.9722
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | 1.1874 | 1.1874
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 0.067935 | 0.067935
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 1.9906 | 1.9906
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.041888 | 0.041888
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 1.9696e-05 | 1.9696e-05
~2~4~0~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~4~1~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Temperature | C | 285.1745 | 285.1745
~2~4~2~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 0.46925 | 0.46925
~2~4~20~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 9.242 | 9.242
~2~4~4~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~4~3~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~4~5~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Steam quality |  | 1.1939 | 1.1939
~2~4~10~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.037849 | 0.037849
~2~4~11~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 1.9894 | 1.9894
~2~4~12~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.04187 | 0.04187
~2~4~13~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.9693e-05 | 1.9693e-05
~2~5~0~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 155.8349 | 155.8349
~2~5~1~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 234.7722 | 234.7722
~2~5~2~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 546.162 | 546.162
~2~5~20~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 2.6288 | 2.6288
~2~5~4~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 1015.0786 | 1015.0786
~2~5~3~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | -1532.41 | -1532.41
~2~5~5~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | -0.64346 | -0.64346
~2~5~10~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 832.6238 | 832.6238
~2~5~11~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 4.6091 | 4.6091
~2~5~12~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.64851 | 0.64851
~2~5~13~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 0.00011628 | 0.00011628
~2~6~0~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Pressure | bar | 9.6159 | 9.6159
~2~6~1~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Temperature | C | 131.4777 | 131.4777
~2~6~2~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Mass flow | t/h | 427.734 | 427.734
~2~6~20~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 1.6496 | 1.6496
~2~6~4~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 553.0933 | 553.0933
~2~6~3~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1994.3953 | -1994.3953
~2~6~5~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Steam quality |  | -0.10003 | -0.10003
~2~6~10~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Density | kg/m^3 | 933.9633 | 933.9633
~2~6~11~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.2642 | 4.2642
~2~6~12~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.68584 | 0.68584
~2~6~13~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00021035 | 0.00021035
~2~7~0~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Pressure | bar | 8.607 | 8.607
~2~7~1~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Temperature | C | 361.1295 | 361.1295
~2~7~2~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Mass flow | t/h | 17.7353 | 17.7353
~2~7~20~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~7~4~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~7~3~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~7~5~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Steam quality |  | 1.2028 | 1.2028
~2~7~10~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Density | kg/m^3 | 2.9827 | 2.9827
~2~7~11~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~7~12~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~7~13~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~9~0~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 31.266 | 31.266
~2~9~1~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 322.5885 | 322.5885
~2~9~2~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 468.5106 | 468.5106
~2~9~20~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~9~4~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~9~3~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~9~5~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | 1.1367 | 1.1367
~2~9~10~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 12.2292 | 12.2292
~2~9~11~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~9~12~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~9~13~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~10~0~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Pressure | bar | 30.6499 | 30.6499
~2~10~1~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Temperature | C | 534.1028 | 534.1028
~2~10~2~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Mass flow | t/h | 468.5106 | 468.5106
~2~10~20~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Entropy | kJ/kg-C | 7.3222 | 7.3222
~2~10~4~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy | kJ/kg | 3533.1067 | 3533.1067
~2~10~3~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy H* | kJ/kg | 985.618 | 985.618
~2~10~5~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Steam quality |  | 1.4079 | 1.4079
~2~10~10~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Density | kg/m^3 | 8.3934 | 8.3934
~2~10~11~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Specific heat | kJ/kg-C | 2.2433 | 2.2433
~2~10~12~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Thermal conductivity | W/m-C | 0.073319 | 0.073319
~2~10~13~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Dynamic viscosity | kg/m-s | 3.0044e-05 | 3.0044e-05
~2~11~0~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Pressure | bar | 0.45641 | 0.45641
~2~11~1~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Temperature | C | 45.3184 | 45.3184
~2~11~2~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Mass flow | t/h | 426.1664 | 426.1664
~2~11~20~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Entropy | kJ/kg-C | 0.64279 | 0.64279
~2~11~4~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy | kJ/kg | 189.7462 | 189.7462
~2~11~3~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy H* | kJ/kg | -2357.7424 | -2357.7424
~2~11~5~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Steam quality |  | -0.061141 | -0.061141
~2~11~10~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Density | kg/m^3 | 990.103 | 990.103
~2~11~11~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~11~12~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Thermal conductivity | W/m-C | 0.63566 | 0.63566
~2~11~13~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Dynamic viscosity | kg/m-s | 0.0005921 | 0.0005921
~2~12~0~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Pressure | bar | 51.1804 | 51.1804
~2~12~1~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Temperature | C | 237.5539 | 237.5539
~2~12~2~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 35.4831 | 35.4831
~2~12~20~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.6754 | 2.6754
~2~12~4~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 1026.1935 | 1026.1935
~2~12~3~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1521.295 | -1521.295
~2~12~5~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Steam quality |  | -0.083152 | -0.083152
~2~12~10~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 818.7884 | 818.7884
~2~12~11~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.7264 | 4.7264
~2~12~12~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.63423 | 0.63423
~2~12~13~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.00011217 | 0.00011217
~2~17~0~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Pressure | bar | 152.7793 | 152.7793
~2~17~1~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Temperature | C | 263.8929 | 263.8929
~2~17~2~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Mass flow | t/h | 546.162 | 546.162
~2~17~20~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Entropy | kJ/kg-C | 2.893 | 2.893
~2~17~4~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy | kJ/kg | 1152.7467 | 1152.7467
~2~17~3~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy H* | kJ/kg | -1394.7418 | -1394.7418
~2~17~5~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Steam quality |  | -0.47706 | -0.47706
~2~17~10~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Density | kg/m^3 | 790.5403 | 790.5403
~2~17~11~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Specific heat | kJ/kg-C | 4.8669 | 4.8669
~2~17~12~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Thermal conductivity | W/m-C | 0.61545 | 0.61545
~2~17~13~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Dynamic viscosity | kg/m-s | 0.00010281 | 0.00010281
~2~18~0~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Pressure | bar | 142.5 | 142.5
~2~18~1~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Temperature | C | 530.8859 | 530.8859
~2~18~2~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Mass flow | t/h | 547.7206 | 547.7206
~2~18~20~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Entropy | kJ/kg-C | 6.4906 | 6.4906
~2~18~4~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~18~3~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~18~5~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Steam quality |  | 1.7377 | 1.7377
~2~18~10~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Density | kg/m^3 | 42.6145 | 42.6145
~2~18~11~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Specific heat | kJ/kg-C | 2.6912 | 2.6912
~2~18~12~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Thermal conductivity | W/m-C | 0.083219 | 0.083219
~2~18~13~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Dynamic viscosity | kg/m-s | 3.0526e-05 | 3.0526e-05
~2~19~0~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 10.7585 | 10.7585
~2~19~1~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 45.3593 | 45.3593
~2~19~2~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 427.734 | 427.734
~2~19~20~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 0.64288 | 0.64288
~2~19~4~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 190.823 | 190.823
~2~19~3~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | -2356.6655 | -2356.6655
~2~19~5~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | -0.29257 | -0.29257
~2~19~10~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 990.5343 | 990.5343
~2~19~11~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 4.1771 | 4.1771
~2~19~12~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.63624 | 0.63624
~2~19~13~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 0.0005918 | 0.0005918
~2~20~0~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Pressure | bar | 52.204 | 52.204
~2~20~1~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Temperature | C | 381.5247 | 381.5247
~2~20~2~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Mass flow | t/h | 547.2429 | 547.2429
~2~20~20~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Entropy | kJ/kg-C | 6.5538 | 6.5538
~2~20~4~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy | kJ/kg | 3146.207 | 3146.207
~2~20~3~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy H* | kJ/kg | 598.7183 | 598.7183
~2~20~5~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Steam quality |  | 1.2179 | 1.2179
~2~20~10~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Density | kg/m^3 | 18.8118 | 18.8118
~2~20~11~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Specific heat | kJ/kg-C | 2.5329 | 2.5329
~2~20~12~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Thermal conductivity | W/m-C | 0.058091 | 0.058091
~2~20~13~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Dynamic viscosity | kg/m-s | 2.357e-05 | 2.357e-05
~2~21~0~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Pressure | bar | 52.204 | 52.204
~2~21~1~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Temperature | C | 381.5247 | 381.5247
~2~21~2~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Mass flow | t/h | 511.7598 | 511.7598
~2~21~20~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Entropy | kJ/kg-C | 6.5538 | 6.5538
~2~21~4~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy | kJ/kg | 3146.207 | 3146.207
~2~21~3~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy H* | kJ/kg | 598.7183 | 598.7183
~2~21~5~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Steam quality |  | 1.2179 | 1.2179
~2~21~10~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Density | kg/m^3 | 18.8118 | 18.8118
~2~21~11~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Specific heat | kJ/kg-C | 2.5329 | 2.5329
~2~21~12~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Thermal conductivity | W/m-C | 0.058091 | 0.058091
~2~21~13~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Dynamic viscosity | kg/m-s | 2.357e-05 | 2.357e-05
~2~22~0~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Pressure | bar | 52.204 | 52.204
~2~22~1~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Temperature | C | 381.5247 | 381.5247
~2~22~2~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Mass flow | t/h | 35.4831 | 35.4831
~2~22~20~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Entropy | kJ/kg-C | 6.5538 | 6.5538
~2~22~4~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy | kJ/kg | 3146.207 | 3146.207
~2~22~3~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy H* | kJ/kg | 598.7183 | 598.7183
~2~22~5~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Steam quality |  | 1.2179 | 1.2179
~2~22~10~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Density | kg/m^3 | 18.8118 | 18.8118
~2~22~11~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Specific heat | kJ/kg-C | 2.5329 | 2.5329
~2~22~12~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Thermal conductivity | W/m-C | 0.058091 | 0.058091
~2~22~13~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Dynamic viscosity | kg/m-s | 2.357e-05 | 2.357e-05
~2~23~0~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 31.266 | 31.266
~2~23~1~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Temperature | C | 322.5885 | 322.5885
~2~23~2~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Mass flow | t/h | 511.7598 | 511.7598
~2~23~20~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~23~4~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~23~3~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~23~5~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Steam quality |  | 1.1367 | 1.1367
~2~23~10~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Density | kg/m^3 | 12.2292 | 12.2292
~2~23~11~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~23~12~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~23~13~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~24~0~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Pressure | bar | 31.266 | 31.266
~2~24~1~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Temperature | C | 322.5885 | 322.5885
~2~24~2~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Mass flow | t/h | 469.2473 | 469.2473
~2~24~20~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~24~4~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~24~3~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~24~5~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Steam quality |  | 1.1367 | 1.1367
~2~24~10~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Density | kg/m^3 | 12.2292 | 12.2292
~2~24~11~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~24~12~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~24~13~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~25~0~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Pressure | bar | 31.266 | 31.266
~2~25~1~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Temperature | C | 322.5885 | 322.5885
~2~25~2~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Mass flow | t/h | 468.5106 | 468.5106
~2~25~20~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~25~4~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~25~3~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~25~5~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Steam quality |  | 1.1367 | 1.1367
~2~25~10~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Density | kg/m^3 | 12.2292 | 12.2292
~2~25~11~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~25~12~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~25~13~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Pressure | bar | 31.266 | 31.266
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Temperature | C | 322.5885 | 322.5885
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Mass flow | t/h | 39.1934 | 39.1934
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Steam quality |  | 1.1367 | 1.1367
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Density | kg/m^3 | 12.2292 | 12.2292
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~27~0~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Pressure | bar | 142.5 | 142.5
~2~27~1~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Temperature | C | 530.8859 | 530.8859
~2~27~2~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Mass flow | t/h | 547.7206 | 547.7206
~2~27~20~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Entropy | kJ/kg-C | 6.4906 | 6.4906
~2~27~4~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~27~3~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~27~5~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Steam quality |  | 1.7377 | 1.7377
~2~27~10~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Density | kg/m^3 | 42.6145 | 42.6145
~2~27~11~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Specific heat | kJ/kg-C | 2.6912 | 2.6912
~2~27~12~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Thermal conductivity | W/m-C | 0.083219 | 0.083219
~2~27~13~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Dynamic viscosity | kg/m-s | 3.0526e-05 | 3.0526e-05
~2~28~0~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 30.6529 | 30.6529
~2~28~1~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 321.5147 | 321.5147
~2~28~2~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 39.1934 | 39.1934
~2~28~20~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 6.6207 | 6.6207
~2~28~4~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 3046.1499 | 3046.1499
~2~28~3~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | 498.6613 | 498.6613
~2~28~5~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | 1.1357 | 1.1357
~2~28~10~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 11.9988 | 11.9988
~2~28~11~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 2.4698 | 2.4698
~2~28~12~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.049658 | 0.049658
~2~28~13~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 2.0974e-05 | 2.0974e-05
~2~29~0~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 158.9516 | 158.9516
~2~29~1~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 197.7425 | 197.7425
~2~29~2~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 546.162 | 546.162
~2~29~20~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.2878 | 2.2878
~2~29~4~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 848.4972 | 848.4972
~2~29~3~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1698.9913 | -1698.9913
~2~29~5~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | -0.84914 | -0.84914
~2~29~10~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 877.6897 | 877.6897
~2~29~11~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.411 | 4.411
~2~29~12~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.67746 | 0.67746
~2~29~13~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.00013877 | 0.00013877
~2~30~0~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Pressure | bar | 30.6529 | 30.6529
~2~30~1~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Temperature | C | 203.3476 | 203.3476
~2~30~2~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 74.6765 | 74.6765
~2~30~20~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.3601 | 2.3601
~2~30~4~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 868.0256 | 868.0256
~2~30~3~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1679.4629 | -1679.4629
~2~30~5~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Steam quality |  | -0.0816 | -0.0816
~2~30~10~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 861.8523 | 861.8523
~2~30~11~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.5052 | 4.5052
~2~30~12~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.66288 | 0.66288
~2~30~13~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00013166 | 0.00013166
~2~31~0~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Pressure | bar | 8.607 | 8.607
~2~31~1~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Temperature | C | 361.1295 | 361.1295
~2~31~2~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Mass flow | t/h | 407.4222 | 407.4222
~2~31~20~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~31~4~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~31~3~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~31~5~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Steam quality |  | 1.2028 | 1.2028
~2~31~10~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Density | kg/m^3 | 2.9827 | 2.9827
~2~31~11~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~31~12~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~31~13~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~32~0~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 28.487 | 28.487
~2~32~1~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Temperature | C | 532.3978 | 532.3978
~2~32~2~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Mass flow | t/h | 463.57 | 463.57
~2~32~20~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Entropy | kJ/kg-C | 7.3532 | 7.3532
~2~32~4~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy | kJ/kg | 3531.4062 | 3531.4062
~2~32~3~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy H* | kJ/kg | 983.9179 | 983.9179
~2~32~5~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Steam quality |  | 1.4028 | 1.4028
~2~32~10~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Density | kg/m^3 | 7.8076 | 7.8076
~2~32~11~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Specific heat | kJ/kg-C | 2.2361 | 2.2361
~2~32~12~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Thermal conductivity | W/m-C | 0.072949 | 0.072949
~2~32~13~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Dynamic viscosity | kg/m-s | 2.9967e-05 | 2.9967e-05
~2~33~0~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Pressure | bar | 28.487 | 28.487
~2~33~1~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Temperature | C | 532.3978 | 532.3978
~2~33~2~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Mass flow | t/h | 463.57 | 463.57
~2~33~20~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Entropy | kJ/kg-C | 7.3532 | 7.3532
~2~33~4~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy | kJ/kg | 3531.4065 | 3531.4065
~2~33~3~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy H* | kJ/kg | 983.918 | 983.918
~2~33~5~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Steam quality |  | 1.4028 | 1.4028
~2~33~10~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Density | kg/m^3 | 7.8076 | 7.8076
~2~33~11~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Specific heat | kJ/kg-C | 2.2361 | 2.2361
~2~33~12~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Thermal conductivity | W/m-C | 0.072949 | 0.072949
~2~33~13~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.9967e-05 | 2.9967e-05
~2~34~0~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 15.24 | 15.24
~2~34~1~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Temperature | C | 439.2987 | 439.2987
~2~34~2~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Mass flow | t/h | 463.57 | 463.57
~2~34~20~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.3859 | 7.3859
~2~34~4~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3341.123 | 3341.123
~2~34~3~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 793.6345 | 793.6345
~2~34~5~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Steam quality |  | 1.2828 | 1.2828
~2~34~10~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Density | kg/m^3 | 4.7109 | 4.7109
~2~34~11~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.158 | 2.158
~2~34~12~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.060534 | 0.060534
~2~34~13~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.6075e-05 | 2.6075e-05
~2~35~0~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Pressure | bar | 15.24 | 15.24
~2~35~1~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Temperature | C | 439.2987 | 439.2987
~2~35~2~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Mass flow | t/h | 452.0421 | 452.0421
~2~35~20~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Entropy | kJ/kg-C | 7.3859 | 7.3859
~2~35~4~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy | kJ/kg | 3341.123 | 3341.123
~2~35~3~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy H* | kJ/kg | 793.6345 | 793.6345
~2~35~5~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Steam quality |  | 1.2828 | 1.2828
~2~35~10~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Density | kg/m^3 | 4.7109 | 4.7109
~2~35~11~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Specific heat | kJ/kg-C | 2.158 | 2.158
~2~35~12~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Thermal conductivity | W/m-C | 0.060534 | 0.060534
~2~35~13~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Dynamic viscosity | kg/m-s | 2.6075e-05 | 2.6075e-05
~2~36~0~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Pressure | bar | 15.24 | 15.24
~2~36~1~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Temperature | C | 439.2987 | 439.2987
~2~36~2~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Mass flow | t/h | 11.5279 | 11.5279
~2~36~20~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Entropy | kJ/kg-C | 7.3859 | 7.3859
~2~36~4~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy | kJ/kg | 3341.123 | 3341.123
~2~36~3~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy H* | kJ/kg | 793.6345 | 793.6345
~2~36~5~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Steam quality |  | 1.2828 | 1.2828
~2~36~10~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Density | kg/m^3 | 4.7109 | 4.7109
~2~36~11~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Specific heat | kJ/kg-C | 2.158 | 2.158
~2~36~12~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Thermal conductivity | W/m-C | 0.060534 | 0.060534
~2~36~13~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.6075e-05 | 2.6075e-05
~2~37~0~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Pressure | bar | 15.24 | 15.24
~2~37~1~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Temperature | C | 526.4799 | 526.4799
~2~37~2~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Mass flow | t/h | 4.9405 | 4.9405
~2~37~20~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Entropy | kJ/kg-C | 7.6379 | 7.6379
~2~37~4~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy | kJ/kg | 3531.4065 | 3531.4065
~2~37~3~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy H* | kJ/kg | 983.918 | 983.918
~2~37~5~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Steam quality |  | 1.3807 | 1.3807
~2~37~10~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Density | kg/m^3 | 4.1721 | 4.1721
~2~37~11~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Specific heat | kJ/kg-C | 2.193 | 2.193
~2~37~12~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Thermal conductivity | W/m-C | 0.071273 | 0.071273
~2~37~13~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.969e-05 | 2.969e-05
~2~38~0~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Pressure | bar | 15.24 | 15.24
~2~38~1~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Temperature | C | 465.5762 | 465.5762
~2~38~2~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Mass flow | t/h | 16.4685 | 16.4685
~2~38~20~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Entropy | kJ/kg-C | 7.4646 | 7.4646
~2~38~4~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy | kJ/kg | 3398.208 | 3398.208
~2~38~3~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy H* | kJ/kg | 850.7195 | 850.7195
~2~38~5~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Steam quality |  | 1.3122 | 1.3122
~2~38~10~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Density | kg/m^3 | 4.5334 | 4.5334
~2~38~11~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Specific heat | kJ/kg-C | 2.1659 | 2.1659
~2~38~12~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Thermal conductivity | W/m-C | 0.063696 | 0.063696
~2~38~13~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Dynamic viscosity | kg/m-s | 2.7173e-05 | 2.7173e-05
~2~39~0~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Pressure | bar | 14.9412 | 14.9412
~2~39~1~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Temperature | C | 178.5169 | 178.5169
~2~39~2~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 91.145 | 91.145
~2~39~20~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 2.1244 | 2.1244
~2~39~4~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 756.822 | 756.822
~2~39~3~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1790.6666 | -1790.6666
~2~39~5~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Steam quality |  | -0.044713 | -0.044713
~2~39~10~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 888.9664 | 888.9664
~2~39~11~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.3993 | 4.3993
~2~39~12~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.6762 | 0.6762
~2~39~13~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00015087 | 0.00015087
~2~40~0~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Pressure | bar | 9.5177 | 9.5177
~2~40~1~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Temperature | C | 172.6459 | 172.6459
~2~40~2~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Mass flow | t/h | 549.0826 | 549.0826
~2~40~20~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Entropy | kJ/kg-C | 2.0678 | 2.0678
~2~40~4~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy | kJ/kg | 730.7694 | 730.7694
~2~40~3~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy H* | kJ/kg | -1816.7191 | -1816.7191
~2~40~5~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Steam quality |  | -0.01112 | -0.01112
~2~40~10~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Density | kg/m^3 | 894.8376 | 894.8376
~2~40~11~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Specific heat | kJ/kg-C | 4.3794 | 4.3794
~2~40~12~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Thermal conductivity | W/m-C | 0.67832 | 0.67832
~2~40~13~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Dynamic viscosity | kg/m-s | 0.00015627 | 0.00015627
~2~41~0~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 8.607 | 8.607
~2~41~1~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Temperature | C | 361.1295 | 361.1295
~2~41~2~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Mass flow | t/h | 452.0421 | 452.0421
~2~41~20~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~41~4~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~41~3~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~41~5~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Steam quality |  | 1.2028 | 1.2028
~2~41~10~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Density | kg/m^3 | 2.9827 | 2.9827
~2~41~11~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~41~12~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~41~13~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~42~0~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Pressure | bar | 8.607 | 8.607
~2~42~1~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Temperature | C | 361.1295 | 361.1295
~2~42~2~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Mass flow | t/h | 26.8845 | 26.8845
~2~42~20~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~42~4~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~42~3~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~42~5~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Steam quality |  | 1.2028 | 1.2028
~2~42~10~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Density | kg/m^3 | 2.9827 | 2.9827
~2~42~11~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~42~12~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~42~13~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~43~0~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Pressure | bar | 8.607 | 8.607
~2~43~1~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Temperature | C | 353.9801 | 353.9801
~2~43~2~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Mass flow | t/h | 30.2036 | 30.2036
~2~43~20~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Entropy | kJ/kg-C | 7.3888 | 7.3888
~2~43~4~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy | kJ/kg | 3169.3425 | 3169.3425
~2~43~3~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy H* | kJ/kg | 621.8541 | 621.8541
~2~43~5~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Steam quality |  | 1.1954 | 1.1954
~2~43~10~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Density | kg/m^3 | 3.0187 | 3.0187
~2~43~11~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Specific heat | kJ/kg-C | 2.1041 | 2.1041
~2~43~12~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Thermal conductivity | W/m-C | 0.050146 | 0.050146
~2~43~13~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Dynamic viscosity | kg/m-s | 2.2502e-05 | 2.2502e-05
~2~44~0~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Pressure | bar | 162.1306 | 162.1306
~2~44~1~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Temperature | C | 175.997 | 175.997
~2~44~2~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Mass flow | t/h | 549.0826 | 549.0826
~2~44~20~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~44~4~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~44~3~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~44~5~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Steam quality |  | -0.98764 | -0.98764
~2~44~10~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Density | kg/m^3 | 900.9072 | 900.9072
~2~44~11~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~44~12~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~44~13~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~45~0~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Pressure | bar | 31.266 | 31.266
~2~45~1~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Temperature | C | 322.5885 | 322.5885
~2~45~2~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Mass flow | t/h | 3.3191 | 3.3191
~2~45~20~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~45~4~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~45~3~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~45~5~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Steam quality |  | 1.1367 | 1.1367
~2~45~10~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Density | kg/m^3 | 12.2292 | 12.2292
~2~45~11~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~45~12~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~45~13~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~46~0~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Pressure | bar | 28.487 | 28.487
~2~46~1~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Temperature | C | 476.7819 | 476.7819
~2~46~2~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~46~20~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Entropy | kJ/kg-C | 7.1928 | 7.1928
~2~46~4~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~46~3~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~46~5~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Steam quality |  | 1.3338 | 1.3338
~2~46~10~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Density | kg/m^3 | 8.4402 | 8.4402
~2~46~11~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Specific heat | kJ/kg-C | 2.2234 | 2.2234
~2~46~12~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Thermal conductivity | W/m-C | 0.066087 | 0.066087
~2~46~13~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.7655e-05 | 2.7655e-05
~2~47~0~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 51.1804 | 51.1804
~2~47~1~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 380.3106 | 380.3106
~2~47~2~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 35.4831 | 35.4831
~2~47~20~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 6.5607 | 6.5607
~2~47~4~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 3145.207 | 3145.207
~2~47~3~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | 597.7184 | 597.7184
~2~47~5~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | 1.2158 | 1.2158
~2~47~10~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 18.4551 | 18.4551
~2~47~11~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 2.5252 | 2.5252
~2~47~12~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.057835 | 0.057835
~2~47~13~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 2.3517e-05 | 2.3517e-05
~2~48~0~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Pressure | bar | 31.266 | 31.266
~2~48~1~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Temperature | C | 478.2809 | 478.2809
~2~48~2~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~48~20~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Entropy | kJ/kg-C | 7.151 | 7.151
~2~48~4~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~48~3~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~48~5~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Steam quality |  | 1.3382 | 1.3382
~2~48~10~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Density | kg/m^3 | 9.2665 | 9.2665
~2~48~11~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Specific heat | kJ/kg-C | 2.2352 | 2.2352
~2~48~12~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Thermal conductivity | W/m-C | 0.066491 | 0.066491
~2~48~13~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Dynamic viscosity | kg/m-s | 2.7723e-05 | 2.7723e-05
~2~49~0~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 14.9412 | 14.9412
~2~49~1~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 464.9462 | 464.9462
~2~49~2~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 16.4685 | 16.4685
~2~49~20~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 7.4723 | 7.4723
~2~49~4~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 3397.2083 | 3397.2083
~2~49~3~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | 849.7196 | 849.7196
~2~49~5~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | 1.3114 | 1.3114
~2~49~10~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 4.4473 | 4.4473
~2~49~11~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 2.1645 | 2.1645
~2~49~12~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.063596 | 0.063596
~2~49~13~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 2.7147e-05 | 2.7147e-05
~2~50~0~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~50~1~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~50~2~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Mass flow | t/h | 17.7353 | 17.7353
~2~50~20~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Entropy | kJ/kg-C | 7.7417 | 7.7417
~2~50~4~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy | kJ/kg | 2450.488 | 2450.488
~2~50~3~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy H* | kJ/kg | -97.0006 | -97.0006
~2~50~5~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Steam quality |  | 0.94463 | 0.94463
~2~50~10~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Density | kg/m^3 | 0.070463 | 0.070463
~2~50~11~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~50~12~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~50~13~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~51~0~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Pressure | bar | 3.391 | 3.391
~2~51~1~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Temperature | C | 248.1745 | 248.1745
~2~51~2~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Mass flow | t/h | 407.4222 | 407.4222
~2~51~20~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.4525 | 7.4525
~2~51~4~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2962.8953 | 2962.8953
~2~51~3~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | 415.4068 | 415.4068
~2~51~5~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Steam quality |  | 1.108 | 1.108
~2~51~10~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Density | kg/m^3 | 1.4265 | 1.4265
~2~51~11~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 2.0469 | 2.0469
~2~51~12~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.038433 | 0.038433
~2~51~13~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.8112e-05 | 1.8112e-05
~2~52~0~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Pressure | bar | 28.487 | 28.487
~2~52~1~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Temperature | C | 532.3978 | 532.3978
~2~52~2~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Mass flow | t/h | 468.5106 | 468.5106
~2~52~20~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Entropy | kJ/kg-C | 7.3532 | 7.3532
~2~52~4~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy | kJ/kg | 3531.4065 | 3531.4065
~2~52~3~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy H* | kJ/kg | 983.918 | 983.918
~2~52~5~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Steam quality |  | 1.4028 | 1.4028
~2~52~10~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Density | kg/m^3 | 7.8076 | 7.8076
~2~52~11~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Specific heat | kJ/kg-C | 2.2361 | 2.2361
~2~52~12~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Thermal conductivity | W/m-C | 0.072949 | 0.072949
~2~52~13~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Dynamic viscosity | kg/m-s | 2.9967e-05 | 2.9967e-05
~2~53~0~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 149.7689 | 149.7689
~2~53~1~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 317.018 | 317.018
~2~53~2~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 546.162 | 546.162
~2~53~20~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 3.3953 | 3.3953
~2~53~4~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 1435.5515 | 1435.5515
~2~53~3~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | -1111.937 | -1111.937
~2~53~5~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Steam quality |  | -0.1733 | -0.1733
~2~53~10~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 686.5002 | 686.5002
~2~53~11~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Specific heat | kJ/kg-C | 6.0634 | 6.0634
~2~53~12~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Thermal conductivity | W/m-C | 0.52452 | 0.52452
~2~53~13~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dynamic viscosity | kg/m-s | 8.1467e-05 | 8.1467e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 149.7689 | 149.7689
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 342.0345 | 342.0345
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 544.8 | 544.8
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.3123 | 5.3123
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2611.5242 | 2611.5242
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 64.0357 | 64.0357
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 96.4802 | 96.4802
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 12.9713 | 12.9713
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.11558 | 0.11558
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.2748e-05 | 2.2748e-05
~2~55~0~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 148.2861 | 148.2861
~2~55~1~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 420.0042 | 420.0042
~2~55~2~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 544.8 | 544.8
~2~55~20~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 6.0063 | 6.0063
~2~55~4~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 3057.8013 | 3057.8013
~2~55~3~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | 510.3128 | 510.3128
~2~55~5~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | 1.4367 | 1.4367
~2~55~10~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 58.3703 | 58.3703
~2~55~11~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 3.6306 | 3.6306
~2~55~12~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.078077 | 0.078077
~2~55~13~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 2.5777e-05 | 2.5777e-05
~2~56~0~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 145.3642 | 145.3642
~2~56~1~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 514.9996 | 514.9996
~2~56~2~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 547.7206 | 547.7206
~2~56~20~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.423 | 6.423
~2~56~4~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3359.4287 | 3359.4287
~2~56~3~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 811.9401 | 811.9401
~2~56~5~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.7129 | 1.7129
~2~56~10~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 44.9202 | 44.9202
~2~56~11~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.7592 | 2.7592
~2~56~12~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.082097 | 0.082097
~2~56~13~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.9876e-05 | 2.9876e-05
~2~57~0~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Pressure | bar | 1.285 | 1.285
~2~57~1~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Temperature | C | 148.8532 | 148.8532
~2~57~2~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Mass flow | t/h | 385.2204 | 385.2204
~2~57~20~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Entropy | kJ/kg-C | 7.4896 | 7.4896
~2~57~4~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy | kJ/kg | 2772.1892 | 2772.1892
~2~57~3~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy H* | kJ/kg | 224.7006 | 224.7006
~2~57~5~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Steam quality |  | 1.0384 | 1.0384
~2~57~10~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Density | kg/m^3 | 0.66705 | 0.66705
~2~57~11~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Specific heat | kJ/kg-C | 2.009 | 2.009
~2~57~12~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Thermal conductivity | W/m-C | 0.028814 | 0.028814
~2~57~13~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Dynamic viscosity | kg/m-s | 1.4135e-05 | 1.4135e-05
~2~58~0~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Pressure | bar | 0.78 | 0.78
~2~58~1~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Temperature | C | 104.8294 | 104.8294
~2~58~2~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Mass flow | t/h | 373.8855 | 373.8855
~2~58~20~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Entropy | kJ/kg-C | 7.5081 | 7.5081
~2~58~4~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy | kJ/kg | 2688.509 | 2688.509
~2~58~3~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy H* | kJ/kg | 141.0205 | 141.0205
~2~58~5~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Steam quality |  | 1.0107 | 1.0107
~2~58~10~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Density | kg/m^3 | 0.45212 | 0.45212
~2~58~11~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Specific heat | kJ/kg-C | 1.9909 | 1.9909
~2~58~12~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Thermal conductivity | W/m-C | 0.024996 | 0.024996
~2~58~13~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~59~0~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Pressure | bar | 3.391 | 3.391
~2~59~1~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Temperature | C | 248.1745 | 248.1745
~2~59~2~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Mass flow | t/h | 22.2019 | 22.2019
~2~59~20~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Entropy | kJ/kg-C | 7.4525 | 7.4525
~2~59~4~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy | kJ/kg | 2962.8953 | 2962.8953
~2~59~3~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy H* | kJ/kg | 415.4068 | 415.4068
~2~59~5~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Steam quality |  | 1.108 | 1.108
~2~59~10~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Density | kg/m^3 | 1.4265 | 1.4265
~2~59~11~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Specific heat | kJ/kg-C | 2.0469 | 2.0469
~2~59~12~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Thermal conductivity | W/m-C | 0.038433 | 0.038433
~2~59~13~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Dynamic viscosity | kg/m-s | 1.8112e-05 | 1.8112e-05
~2~60~0~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Pressure | bar | 3.391 | 3.391
~2~60~1~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Temperature | C | 248.1745 | 248.1745
~2~60~2~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Mass flow | t/h | 385.2204 | 385.2204
~2~60~20~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Entropy | kJ/kg-C | 7.4525 | 7.4525
~2~60~4~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy | kJ/kg | 2962.8953 | 2962.8953
~2~60~3~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy H* | kJ/kg | 415.4068 | 415.4068
~2~60~5~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Steam quality |  | 1.108 | 1.108
~2~60~10~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Density | kg/m^3 | 1.4265 | 1.4265
~2~60~11~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Specific heat | kJ/kg-C | 2.0469 | 2.0469
~2~60~12~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Thermal conductivity | W/m-C | 0.038433 | 0.038433
~2~60~13~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Dynamic viscosity | kg/m-s | 1.8112e-05 | 1.8112e-05
~2~61~0~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Pressure | bar | 1.285 | 1.285
~2~61~1~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Temperature | C | 148.8532 | 148.8532
~2~61~2~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Mass flow | t/h | 11.3349 | 11.3349
~2~61~20~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Entropy | kJ/kg-C | 7.4896 | 7.4896
~2~61~4~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy | kJ/kg | 2772.1892 | 2772.1892
~2~61~3~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy H* | kJ/kg | 224.7006 | 224.7006
~2~61~5~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Steam quality |  | 1.0384 | 1.0384
~2~61~10~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Density | kg/m^3 | 0.66705 | 0.66705
~2~61~11~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Specific heat | kJ/kg-C | 2.009 | 2.009
~2~61~12~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Thermal conductivity | W/m-C | 0.028814 | 0.028814
~2~61~13~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Dynamic viscosity | kg/m-s | 1.4135e-05 | 1.4135e-05
~2~62~0~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Pressure | bar | 1.285 | 1.285
~2~62~1~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Temperature | C | 148.8532 | 148.8532
~2~62~2~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Mass flow | t/h | 373.8855 | 373.8855
~2~62~20~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Entropy | kJ/kg-C | 7.4896 | 7.4896
~2~62~4~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy | kJ/kg | 2772.1892 | 2772.1892
~2~62~3~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy H* | kJ/kg | 224.7006 | 224.7006
~2~62~5~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Steam quality |  | 1.0384 | 1.0384
~2~62~10~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Density | kg/m^3 | 0.66705 | 0.66705
~2~62~11~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Specific heat | kJ/kg-C | 2.009 | 2.009
~2~62~12~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Thermal conductivity | W/m-C | 0.028814 | 0.028814
~2~62~13~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Dynamic viscosity | kg/m-s | 1.4135e-05 | 1.4135e-05
~2~63~0~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Pressure | bar | 0.283 | 0.283
~2~63~1~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Temperature | C | 67.7608 | 67.7608
~2~63~2~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Mass flow | t/h | 358.3243 | 358.3243
~2~63~20~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Entropy | kJ/kg-C | 7.5452 | 7.5452
~2~63~4~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy | kJ/kg | 2539.6545 | 2539.6545
~2~63~3~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy H* | kJ/kg | -7.8341 | -7.8341
~2~63~5~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Steam quality |  | 0.96468 | 0.96468
~2~63~10~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Density | kg/m^3 | 0.18771 | 0.18771
~2~63~11~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~63~12~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~63~13~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~64~0~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Pressure | bar | 0.78 | 0.78
~2~64~1~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Temperature | C | 104.8294 | 104.8294
~2~64~2~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Mass flow | t/h | 15.5612 | 15.5612
~2~64~20~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Entropy | kJ/kg-C | 7.5081 | 7.5081
~2~64~4~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy | kJ/kg | 2688.509 | 2688.509
~2~64~3~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy H* | kJ/kg | 141.0205 | 141.0205
~2~64~5~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Steam quality |  | 1.0107 | 1.0107
~2~64~10~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Density | kg/m^3 | 0.45212 | 0.45212
~2~64~11~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Specific heat | kJ/kg-C | 1.9909 | 1.9909
~2~64~12~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Thermal conductivity | W/m-C | 0.024996 | 0.024996
~2~64~13~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~65~0~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Pressure | bar | 0.283 | 0.283
~2~65~1~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Temperature | C | 67.7608 | 67.7608
~2~65~2~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Mass flow | t/h | 10.7919 | 10.7919
~2~65~20~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Entropy | kJ/kg-C | 7.5452 | 7.5452
~2~65~4~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy | kJ/kg | 2539.6545 | 2539.6545
~2~65~3~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy H* | kJ/kg | -7.8341 | -7.8341
~2~65~5~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Steam quality |  | 0.96468 | 0.96468
~2~65~10~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Density | kg/m^3 | 0.18771 | 0.18771
~2~65~11~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~65~12~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~65~13~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~66~0~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Pressure | bar | 0.78 | 0.78
~2~66~1~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Temperature | C | 104.8294 | 104.8294
~2~66~2~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Mass flow | t/h | 358.3243 | 358.3243
~2~66~20~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Entropy | kJ/kg-C | 7.5081 | 7.5081
~2~66~4~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy | kJ/kg | 2688.509 | 2688.509
~2~66~3~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy H* | kJ/kg | 141.0205 | 141.0205
~2~66~5~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Steam quality |  | 1.0107 | 1.0107
~2~66~10~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Density | kg/m^3 | 0.45212 | 0.45212
~2~66~11~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Specific heat | kJ/kg-C | 1.9909 | 1.9909
~2~66~12~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Thermal conductivity | W/m-C | 0.024996 | 0.024996
~2~66~13~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2476e-05
~2~67~0~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~67~1~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~67~2~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 347.8045 | 347.8045
~2~67~20~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.6683 | 7.6683
~2~67~4~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2427.1348 | 2427.1348
~2~67~3~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | -120.3537 | -120.3537
~2~67~5~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Steam quality |  | 0.93487 | 0.93487
~2~67~10~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 0.071198 | 0.071198
~2~67~11~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~67~12~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~67~13~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~68~0~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~68~1~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Temperature | C | 27.3223 | 27.3223
~2~68~2~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Mass flow | t/h | 9802.543 | 9802.543
~2~68~20~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~68~4~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~68~3~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~68~5~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Steam quality |  | -0.13493 | -0.13493
~2~68~10~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Density | kg/m^3 | 996.4656 | 996.4656
~2~68~11~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~68~12~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~68~13~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~69~0~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Pressure | bar | 3.5 | 3.5
~2~69~1~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Temperature | C | 37.3673 | 37.3673
~2~69~2~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Mass flow | t/h | 19605.0859 | 19605.0859
~2~69~20~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Entropy | kJ/kg-C | 0.53702 | 0.53702
~2~69~4~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy | kJ/kg | 156.774 | 156.774
~2~69~3~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy H* | kJ/kg | -2390.7146 | -2390.7146
~2~69~5~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Steam quality |  | -0.19907 | -0.19907
~2~69~10~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Density | kg/m^3 | 993.3504 | 993.3504
~2~69~11~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Specific heat | kJ/kg-C | 4.1775 | 4.1775
~2~69~12~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Thermal conductivity | W/m-C | 0.62587 | 0.62587
~2~69~13~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Dynamic viscosity | kg/m-s | 0.00068574 | 0.00068574
~2~70~0~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Pressure | bar | 0.283 | 0.283
~2~70~1~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Temperature | C | 67.7608 | 67.7608
~2~70~2~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Mass flow | t/h | 347.5323 | 347.5323
~2~70~20~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Entropy | kJ/kg-C | 7.5452 | 7.5452
~2~70~4~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy | kJ/kg | 2539.6545 | 2539.6545
~2~70~3~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy H* | kJ/kg | -7.8341 | -7.8341
~2~70~5~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Steam quality |  | 0.96468 | 0.96468
~2~70~10~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Density | kg/m^3 | 0.18771 | 0.18771
~2~70~11~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~70~12~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~70~13~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~71~0~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Temperature | C | 48.5996 | 48.5996
~2~71~2~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Mass flow | t/h | 59.8899 | 59.8899
~2~71~20~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Entropy | kJ/kg-C | 0.68564 | 0.68564
~2~71~4~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy | kJ/kg | 203.4428 | 203.4428
~2~71~3~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy H* | kJ/kg | -2344.0457 | -2344.0457
~2~71~5~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Steam quality |  | -0.015226 | -0.015226
~2~71~10~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Density | kg/m^3 | 988.6748 | 988.6748
~2~71~11~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~71~12~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Thermal conductivity | W/m-C | 0.63944 | 0.63944
~2~71~13~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00055944 | 0.00055944
~2~72~0~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 10.4085 | 10.4085
~2~72~1~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 45.7868 | 45.7868
~2~72~2~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 427.734 | 427.734
~2~72~20~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.6485 | 0.6485
~2~72~4~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 192.5786 | 192.5786
~2~72~3~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2354.9099 | -2354.9099
~2~72~5~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.28773 | -0.28773
~2~72~10~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 990.3386 | 990.3386
~2~72~11~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1773 | 4.1773
~2~72~12~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.63673 | 0.63673
~2~72~13~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00058737 | 0.00058737
~2~73~0~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Pressure | bar | 0.45641 | 0.45641
~2~73~1~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Temperature | C | 45.2441 | 45.2441
~2~73~2~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Mass flow | t/h | 427.734 | 427.734
~2~73~20~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Entropy | kJ/kg-C | 0.64181 | 0.64181
~2~73~4~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy | kJ/kg | 189.4356 | 189.4356
~2~73~3~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy H* | kJ/kg | -2358.053 | -2358.053
~2~73~5~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Steam quality |  | -0.061276 | -0.061276
~2~73~10~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Density | kg/m^3 | 990.1342 | 990.1342
~2~73~11~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~73~12~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Thermal conductivity | W/m-C | 0.63557 | 0.63557
~2~73~13~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Dynamic viscosity | kg/m-s | 0.00059287 | 0.00059287
~2~74~0~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.175 | 0.175
~2~74~1~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 48.6379 | 48.6379
~2~74~2~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 60.1574 | 60.1574
~2~74~20~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.68614 | 0.68614
~2~74~4~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 203.6027 | 203.6027
~2~74~3~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2343.8857 | -2343.8857
~2~74~5~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.015158 | -0.015158
~2~74~10~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 988.6579 | 988.6579
~2~74~11~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~74~12~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.63949 | 0.63949
~2~74~13~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.00055908 | 0.00055908
~2~75~0~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~75~1~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Temperature | C | 57.2007 | 57.2007
~2~75~2~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Mass flow | t/h | 0.26747 | 0.26747
~2~75~20~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~75~4~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~75~3~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~75~5~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~75~10~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Density | kg/m^3 | 984.2903 | 984.2903
~2~75~11~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~75~12~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~75~13~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~76~0~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.0975 | 0.0975
~2~76~1~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 45.3132 | 45.3132
~2~76~2~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 366.0091 | 366.0091
~2~76~20~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 7.6744 | 7.6744
~2~76~4~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 2429.0613 | 2429.0613
~2~76~3~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -118.4272 | -118.4272
~2~76~5~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | 0.93567 | 0.93567
~2~76~10~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 0.071137 | 0.071137
~2~76~11~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~76~12~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~76~13~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~78~0~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 10.2044 | 10.2044
~2~78~1~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 61.713 | 61.713
~2~78~2~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 427.734 | 427.734
~2~78~20~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 0.85213 | 0.85213
~2~78~4~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 259.1459 | 259.1459
~2~78~3~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2288.3428 | -2288.3428
~2~78~5~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.25229 | -0.25229
~2~78~10~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 982.7588 | 982.7588
~2~78~11~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.1831 | 4.1831
~2~78~12~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.65345 | 0.65345
~2~78~13~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.0004548 | 0.0004548
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.70449 | 0.70449
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Temperature | C | 64.5156 | 64.5156
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 49.098 | 49.098
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.88752 | 0.88752
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 270.0787 | 270.0787
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2277.4099 | -2277.4099
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.047019 | -0.047019
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 980.852 | 980.852
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1866 | 4.1866
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.6555 | 0.6555
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00043641 | 0.00043641
~2~80~0~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 10.0043 | 10.0043
~2~80~1~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 84.4979 | 84.4979
~2~80~2~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 427.734 | 427.734
~2~80~20~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.1279 | 1.1279
~2~80~4~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 354.587 | 354.587
~2~80~3~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2192.9016 | -2192.9016
~2~80~5~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.20263 | -0.20263
~2~80~10~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 969.3892 | 969.3892
~2~80~11~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.1978 | 4.1978
~2~80~12~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.6709 | 0.6709
~2~80~13~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.00033608 | 0.00033608
~2~81~0~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Pressure | bar | 1.2598 | 1.2598
~2~81~1~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Temperature | C | 87.2969 | 87.2969
~2~81~2~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 33.5367 | 33.5367
~2~81~20~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 1.1612 | 1.1612
~2~81~4~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 365.6533 | 365.6533
~2~81~3~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2181.8352 | -2181.8352
~2~81~5~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.035537 | -0.035537
~2~81~10~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 967.1675 | 967.1675
~2~81~11~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.2021 | 4.2021
~2~81~12~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.67209 | 0.67209
~2~81~13~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.00032491 | 0.00032491
~2~82~0~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 9.8082 | 9.8082
~2~82~1~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 100.4939 | 100.4939
~2~82~2~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 427.734 | 427.734
~2~82~20~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 1.3119 | 1.3119
~2~82~4~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 421.8377 | 421.8377
~2~82~3~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | -2125.6509 | -2125.6509
~2~82~5~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | -0.16711 | -0.16711
~2~82~10~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 958.4468 | 958.4468
~2~82~11~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 4.214 | 4.214
~2~82~12~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.679 | 0.679
~2~82~13~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 0.00028095 | 0.00028095
~2~84~0~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Pressure | bar | 3.3245 | 3.3245
~2~84~1~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Temperature | C | 103.2964 | 103.2964
~2~84~2~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 22.2019 | 22.2019
~2~84~20~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.3439 | 1.3439
~2~84~4~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 433.167 | 433.167
~2~84~3~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2114.3215 | -2114.3215
~2~84~5~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.066621 | -0.066621
~2~84~10~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 956.1024 | 956.1024
~2~84~11~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.2189 | 4.2189
~2~84~12~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.67973 | 0.67973
~2~84~13~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.00027272 | 0.00027272
~2~85~0~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 3.3245 | 3.3245
~2~85~1~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 247.573 | 247.573
~2~85~2~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 22.2019 | 22.2019
~2~85~20~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 7.4596 | 7.4596
~2~85~4~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 2961.8955 | 2961.8955
~2~85~3~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | 414.4068 | 414.4068
~2~85~5~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | 1.1079 | 1.1079
~2~85~10~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 1.3999 | 1.3999
~2~85~11~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 2.0454 | 2.0454
~2~85~12~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.038364 | 0.038364
~2~85~13~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 1.8088e-05 | 1.8088e-05
~2~86~0~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 1.2598 | 1.2598
~2~86~1~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 148.2608 | 148.2608
~2~86~2~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 11.3349 | 11.3349
~2~86~20~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 7.4963 | 7.4963
~2~86~4~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 2771.1892 | 2771.1892
~2~86~3~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | 223.7006 | 223.7006
~2~86~5~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | 1.0384 | 1.0384
~2~86~10~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 0.65479 | 0.65479
~2~86~11~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 2.0075 | 2.0075
~2~86~12~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.028755 | 0.028755
~2~86~13~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 1.4113e-05 | 1.4113e-05
~2~87~0~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 0.76471 | 0.76471
~2~87~1~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 104.2386 | 104.2386
~2~87~2~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 15.5612 | 15.5612
~2~87~20~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 7.5145 | 7.5145
~2~87~4~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 2687.509 | 2687.509
~2~87~3~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | 140.0205 | 140.0205
~2~87~5~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | 1.0107 | 1.0107
~2~87~10~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 0.44388 | 0.44388
~2~87~11~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 1.9893 | 1.9893
~2~87~12~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.02494 | 0.02494
~2~87~13~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 1.2456e-05 | 1.2456e-05
~2~88~0~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.27745 | 0.27745
~2~88~1~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 67.3104 | 67.3104
~2~88~2~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 10.7919 | 10.7919
~2~88~20~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 7.551 | 7.551
~2~88~4~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 2538.6545 | 2538.6545
~2~88~3~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -8.834 | -8.834
~2~88~5~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | 0.9646 | 0.9646
~2~88~10~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 0.18428 | 0.18428
~2~88~11~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1881 | 4.1881
~2~88~12~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.021747 | 0.021747
~2~88~13~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 1.1177e-05 | 1.1177e-05
~2~99~0~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 31.266 | 31.266
~2~99~1~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 322.5885 | 322.5885
~2~99~2~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 468.5106 | 468.5106
~2~99~20~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 6.6139 | 6.6139
~2~99~4~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 3047.1499 | 3047.1499
~2~99~3~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy H* | kJ/kg | 499.6613 | 499.6613
~2~99~5~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Steam quality |  | 1.1367 | 1.1367
~2~99~10~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 12.2292 | 12.2292
~2~99~11~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Specific heat | kJ/kg-C | 2.4769 | 2.4769
~2~99~12~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Thermal conductivity | W/m-C | 0.049853 | 0.049853
~2~99~13~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dynamic viscosity | kg/m-s | 2.1018e-05 | 2.1018e-05
~2~100~0~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 30.9564 | 30.9564
~2~100~1~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 511.002 | 511.002
~2~100~2~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 468.5106 | 468.5106
~2~100~20~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 7.2519 | 7.2519
~2~100~4~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 3480.7429 | 3480.7429
~2~100~3~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy H* | kJ/kg | 933.2544 | 933.2544
~2~100~5~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Steam quality |  | 1.3792 | 1.3792
~2~100~10~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 8.7513 | 8.7513
~2~100~11~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Specific heat | kJ/kg-C | 2.2381 | 2.2381
~2~100~12~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Thermal conductivity | W/m-C | 0.070459 | 0.070459
~2~100~13~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dynamic viscosity | kg/m-s | 2.9089e-05 | 2.9089e-05
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 148.2861 | 148.2861
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 418.004 | 418.004
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 546.5478 | 546.5478
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 5.9956 | 5.9956
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 3050.4329 | 3050.4329
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy H* | kJ/kg | 502.9442 | 502.9442
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Steam quality |  | 1.4294 | 1.4294
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 58.7642 | 58.7642
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Specific heat | kJ/kg-C | 3.6693 | 3.6693
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Thermal conductivity | W/m-C | 0.078142 | 0.078142
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dynamic viscosity | kg/m-s | 2.5689e-05 | 2.5689e-05
~2~102~0~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 146.8179 | 146.8179
~2~102~1~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 489.9973 | 489.9973
~2~102~2~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 546.5478 | 546.5478
~2~102~20~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 6.3243 | 6.3243
~2~102~4~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 3286.0427 | 3286.0427
~2~102~3~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy H* | kJ/kg | 738.5544 | 738.5544
~2~102~5~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Steam quality |  | 1.6518 | 1.6518
~2~102~10~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 47.856 | 47.856
~2~102~11~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Specific heat | kJ/kg-C | 2.8841 | 2.8841
~2~102~12~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Thermal conductivity | W/m-C | 0.080254 | 0.080254
~2~102~13~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dynamic viscosity | kg/m-s | 2.8817e-05 | 2.8817e-05
~2~103~0~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Pressure | bar | 8.4382 | 8.4382
~2~103~1~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Temperature | C | 353.3496 | 353.3496
~2~103~2~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 30.2036 | 30.2036
~2~103~20~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 7.3962 | 7.3962
~2~103~4~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 3168.3425 | 3168.3425
~2~103~3~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | 620.8541 | 620.8541
~2~103~5~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Steam quality |  | 1.1951 | 1.1951
~2~103~10~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 2.9618 | 2.9618
~2~103~11~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 2.1026 | 2.1026
~2~103~12~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.05006 | 0.05006
~2~103~13~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 2.2476e-05 | 2.2476e-05
~2~104~0~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 162.1306 | 162.1306
~2~104~1~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 175.997 | 175.997
~2~104~2~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 1.7479 | 1.7479
~2~104~20~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~104~4~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~104~3~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~104~5~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | -0.98764 | -0.98764
~2~104~10~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 900.9072 | 900.9072
~2~104~11~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~104~12~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~104~13~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~105~0~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 162.1306 | 162.1306
~2~105~1~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 175.997 | 175.997
~2~105~2~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 1.1728 | 1.1728
~2~105~20~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~105~4~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~105~3~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~105~5~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | -0.98764 | -0.98764
~2~105~10~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 900.9072 | 900.9072
~2~105~11~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~105~12~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~105~13~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~106~0~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 162.1306 | 162.1306
~2~106~1~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 175.997 | 175.997
~2~106~2~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 546.162 | 546.162
~2~106~20~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~106~4~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~106~3~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~106~5~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | -0.98764 | -0.98764
~2~106~10~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 900.9072 | 900.9072
~2~106~11~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~106~12~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~106~13~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~107~0~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Pressure | bar | 162.1306 | 162.1306
~2~107~1~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Temperature | C | 175.997 | 175.997
~2~107~2~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Mass flow | t/h | 2.9207 | 2.9207
~2~107~20~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~107~4~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~107~3~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~107~5~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Steam quality |  | -0.98764 | -0.98764
~2~107~10~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Density | kg/m^3 | 900.9072 | 900.9072
~2~107~11~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~107~12~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~107~13~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~108~0~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 162.1306 | 162.1306
~2~108~1~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 175.997 | 175.997
~2~108~2~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~108~20~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~108~4~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 753.6765 | 753.6765
~2~108~3~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | -1793.8121 | -1793.8121
~2~108~5~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | -0.98764 | -0.98764
~2~108~10~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 900.9072 | 900.9072
~2~108~11~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~108~12~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~108~13~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Pressure | bar | 143.925 | 143.925
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Temperature | C | 532.1021 | 532.1021
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Mass flow | t/h | 547.7206 | 547.7206
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Entropy | kJ/kg-C | 6.4886 | 6.4886
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy | kJ/kg | 3408.4106 | 3408.4106
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy H* | kJ/kg | 860.9221 | 860.9221
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Steam quality |  | 1.7496 | 1.7496
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Density | kg/m^3 | 42.9941 | 42.9941
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Specific heat | kJ/kg-C | 2.6949 | 2.6949
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Thermal conductivity | W/m-C | 0.083499 | 0.083499
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Dynamic viscosity | kg/m-s | 3.0589e-05 | 3.0589e-05
~2~111~0~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Pressure | bar | 28.7719 | 28.7719
~2~111~1~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Temperature | C | 533.2796 | 533.2796
~2~111~2~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Mass flow | t/h | 468.5106 | 468.5106
~2~111~20~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Entropy | kJ/kg-C | 7.3508 | 7.3508
~2~111~4~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy | kJ/kg | 3533.1067 | 3533.1067
~2~111~3~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy H* | kJ/kg | 985.618 | 985.618
~2~111~5~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Steam quality |  | 1.4043 | 1.4043
~2~111~10~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Density | kg/m^3 | 7.8778 | 7.8778
~2~111~11~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Specific heat | kJ/kg-C | 2.2372 | 2.2372
~2~111~12~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Thermal conductivity | W/m-C | 0.073081 | 0.073081
~2~111~13~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Dynamic viscosity | kg/m-s | 3.0004e-05 | 3.0004e-05
~2~112~0~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 151.2666 | 151.2666
~2~112~1~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 263.6848 | 263.6848
~2~112~2~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 546.162 | 546.162
~2~112~20~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.8915 | 2.8915
~2~112~4~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 1151.7467 | 1151.7467
~2~112~3~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1395.7418 | -1395.7418
~2~112~5~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.46708 | -0.46708
~2~112~10~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 790.6851 | 790.6851
~2~112~11~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.8667 | 4.8667
~2~112~12~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.61551 | 0.61551
~2~112~13~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00010285 | 0.00010285
~2~115~0~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 145.3642 | 145.3642
~2~115~1~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 516.9999 | 516.9999
~2~115~2~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 546.5478 | 546.5478
~2~115~20~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 6.4301 | 6.4301
~2~115~4~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 3365.0205 | 3365.0205
~2~115~3~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | 817.5318 | 817.5318
~2~115~5~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | 1.7183 | 1.7183
~2~115~10~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 44.7441 | 44.7441
~2~115~11~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 2.7518 | 2.7518
~2~115~12~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.082274 | 0.082274
~2~115~13~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 2.9961e-05 | 2.9961e-05
~2~117~0~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Pressure | bar | 31.266 | 31.266
~2~117~1~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Temperature | C | 478.2809 | 478.2809
~2~117~2~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~117~20~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Entropy | kJ/kg-C | 7.151 | 7.151
~2~117~4~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~117~3~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~117~5~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Steam quality |  | 1.3382 | 1.3382
~2~117~10~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Density | kg/m^3 | 9.2665 | 9.2665
~2~117~11~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Specific heat | kJ/kg-C | 2.2352 | 2.2352
~2~117~12~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Thermal conductivity | W/m-C | 0.066491 | 0.066491
~2~117~13~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.7723e-05 | 2.7723e-05
~2~118~0~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Pressure | bar | 28.487 | 28.487
~2~118~1~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Temperature | C | 476.7819 | 476.7819
~2~118~2~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~118~20~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Entropy | kJ/kg-C | 7.1928 | 7.1928
~2~118~4~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy | kJ/kg | 3406.7107 | 3406.7107
~2~118~3~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy H* | kJ/kg | 859.222 | 859.222
~2~118~5~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Steam quality |  | 1.3338 | 1.3338
~2~118~10~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Density | kg/m^3 | 8.4402 | 8.4402
~2~118~11~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Specific heat | kJ/kg-C | 2.2234 | 2.2234
~2~118~12~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Thermal conductivity | W/m-C | 0.066087 | 0.066087
~2~118~13~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Dynamic viscosity | kg/m-s | 2.7655e-05 | 2.7655e-05
~2~119~0~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~119~1~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Temperature | C | 27.3223 | 27.3223
~2~119~2~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Mass flow | t/h | 9802.543 | 9802.543
~2~119~20~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~119~4~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~119~3~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~119~5~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Steam quality |  | -0.13493 | -0.13493
~2~119~10~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Density | kg/m^3 | 996.4656 | 996.4656
~2~119~11~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~119~12~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~119~13~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~120~0~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Pressure | bar | 1.0135 | 1.0135
~2~120~1~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Temperature | C | 27.3223 | 27.3223
~2~120~2~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Mass flow | t/h | 19605.0859 | 19605.0859
~2~120~20~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~120~4~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~120~3~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~120~5~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Steam quality |  | -0.13493 | -0.13493
~2~120~10~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Density | kg/m^3 | 996.4656 | 996.4656
~2~120~11~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~120~12~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~120~13~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~121~0~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~121~1~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~121~2~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Mass flow | t/h | 9802.543 | 9802.543
~2~121~20~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~121~4~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~121~3~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~121~5~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~121~10~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~121~11~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~121~12~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~121~13~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~122~0~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~122~1~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~122~2~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Mass flow | t/h | 9802.543 | 9802.543
~2~122~20~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~122~4~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~122~3~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~122~5~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~122~10~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~122~11~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~122~12~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~122~13~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~123~0~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 3.8447 | 3.8447
~2~123~1~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 27.3502 | 27.3502
~2~123~2~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 19605.0859 | 19605.0859
~2~123~20~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~123~4~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~123~3~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~123~5~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.22627 | -0.22627
~2~123~10~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 996.5845 | 996.5845
~2~123~11~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~123~12~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~123~13~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~124~0~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~124~1~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~124~2~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Mass flow | t/h | 8.8676 | 8.8676
~2~124~20~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Entropy | kJ/kg-C | 7.7417 | 7.7417
~2~124~4~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy | kJ/kg | 2450.488 | 2450.488
~2~124~3~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy H* | kJ/kg | -97.0006 | -97.0006
~2~124~5~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Steam quality |  | 0.94463 | 0.94463
~2~124~10~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Density | kg/m^3 | 0.070463 | 0.070463
~2~124~11~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~124~12~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~124~13~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~125~0~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~125~1~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~125~2~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Mass flow | t/h | 8.8676 | 8.8676
~2~125~20~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Entropy | kJ/kg-C | 7.7417 | 7.7417
~2~125~4~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy | kJ/kg | 2450.488 | 2450.488
~2~125~3~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy H* | kJ/kg | -97.0006 | -97.0006
~2~125~5~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Steam quality |  | 0.94463 | 0.94463
~2~125~10~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Density | kg/m^3 | 0.070463 | 0.070463
~2~125~11~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~125~12~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~125~13~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~126~0~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 9.5177 | 9.5177
~2~126~1~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 172.6459 | 172.6459
~2~126~2~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 274.5413 | 274.5413
~2~126~20~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 2.0678 | 2.0678
~2~126~4~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 730.7694 | 730.7694
~2~126~3~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | -1816.7191 | -1816.7191
~2~126~5~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | -0.01112 | -0.01112
~2~126~10~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 894.8376 | 894.8376
~2~126~11~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 4.3794 | 4.3794
~2~126~12~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.67832 | 0.67832
~2~126~13~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 0.00015627 | 0.00015627
~2~127~0~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 9.5177 | 9.5177
~2~127~1~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 172.6459 | 172.6459
~2~127~2~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 274.5413 | 274.5413
~2~127~20~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 2.0678 | 2.0678
~2~127~4~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 730.7694 | 730.7694
~2~127~3~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | -1816.7191 | -1816.7191
~2~127~5~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | -0.01112 | -0.01112
~2~127~10~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 894.8376 | 894.8376
~2~127~11~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 4.3794 | 4.3794
~2~127~12~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.67832 | 0.67832
~2~127~13~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 0.00015627 | 0.00015627
~2~128~0~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 8.607 | 8.607
~2~128~1~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 361.1295 | 361.1295
~2~128~2~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 8.8676 | 8.8676
~2~128~20~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~128~4~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~128~3~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~128~5~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | 1.2028 | 1.2028
~2~128~10~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 2.9827 | 2.9827
~2~128~11~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~128~12~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~128~13~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~129~0~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 8.607 | 8.607
~2~129~1~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 361.1295 | 361.1295
~2~129~2~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 8.8676 | 8.8676
~2~129~20~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 7.4127 | 7.4127
~2~129~4~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 3184.4282 | 3184.4282
~2~129~3~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | 636.9396 | 636.9396
~2~129~5~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | 1.2028 | 1.2028
~2~129~10~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 2.9827 | 2.9827
~2~129~11~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 2.1043 | 2.1043
~2~129~12~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.050942 | 0.050942
~2~129~13~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 2.2803e-05 | 2.2803e-05
~2~130~0~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Pressure | bar | 162.1306 | 162.1306
~2~130~1~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Temperature | C | 175.997 | 175.997
~2~130~2~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Mass flow | t/h | 274.5413 | 274.5413
~2~130~20~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~130~4~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy | kJ/kg | 753.6763 | 753.6763
~2~130~3~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy H* | kJ/kg | -1793.8123 | -1793.8123
~2~130~5~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Steam quality |  | -0.98764 | -0.98764
~2~130~10~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Density | kg/m^3 | 900.9072 | 900.9072
~2~130~11~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~130~12~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~130~13~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~2~131~0~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Pressure | bar | 162.1306 | 162.1306
~2~131~1~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Temperature | C | 175.997 | 175.997
~2~131~2~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Mass flow | t/h | 274.5413 | 274.5413
~2~131~20~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Entropy | kJ/kg-C | 2.0809 | 2.0809
~2~131~4~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy | kJ/kg | 753.6763 | 753.6763
~2~131~3~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy H* | kJ/kg | -1793.8123 | -1793.8123
~2~131~5~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Steam quality |  | -0.98764 | -0.98764
~2~131~10~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Density | kg/m^3 | 900.9072 | 900.9072
~2~131~11~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Specific heat | kJ/kg-C | 4.3321 | 4.3321
~2~131~12~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Thermal conductivity | W/m-C | 0.68822 | 0.68822
~2~131~13~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015683 | 0.00015683
~3~77~0~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0135 | 1.0135
~3~77~1~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 30 | 30
~3~77~2~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 92.7421 | 92.7421
~3~77~3~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | 17296.6777 | 17296.6777
~3~77~4~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: LHV | kJ/kg | 17286.1191 | 17286.1191
~3~77~5~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HHV | kJ/kg | 18840.5996 | 18840.5996
~3~77~8~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 6.9862 | 6.9862
~3~77~6~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (LHV) | kW | 445326.7188 | 445326.7188
~3~77~7~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (HHV) | kW | 485373.4062 | 485373.4062
~3~77~120~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fuel LHV price | USD/GJ | 2.362 | 2.362
~3~77~20~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Ash | % | 5.36 | 5.36
~3~77~21~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Moisture | % | 27.99 | 27.99
~3~77~22~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Carbon | % | 48.63 | 48.63
~3~77~23~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Hydrogen | % | 3.99 | 3.99
~3~77~24~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Oxygen | % | 13.04 | 13.04
~3~77~25~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Nitrogen | % | 0.8 | 0.8
~3~77~26~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Sulfur | % | 0.19 | 0.19
~3~77~27~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Chlorine | % | 0 | 0
~3~77~28~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Advisory: 103 - The ratio of tempering air over total primary air at the design point is low. Then at off-design, pulverizer may not have enough energy to dry the fuel to the desired outlet conditions when the load is low. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [56] - LPH-5 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,6
Note on E6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Advisory: 103 - The ratio of tempering air over total primary air at the design point is low. Then at off-design, pulverizer may not have enough energy to dry the fuel to the desired outlet conditions when the load is low. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [56] - LPH-5 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,6

## ELINK (2)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTAW_What if_75%_RevD.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 6.9 | 6.9 | #N/A | 6.9
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 26.95 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 75.41 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 23.5477 | 23.5477 | #N/A | 23.5477
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
~31~1~7~~-27~ | Deaerator [31] - DAER : Deaerator design pressure | bar | 9.0647 | 9.0647 | #N/A | 9.0647
~31~1~8~~-27~ | Deaerator [31] - DAER : Deaerator outlet temperature @ design | C | 175.6625 | 175.6625 | #N/A | 175.6625
~31~1~5~~-27~ | Deaerator [31] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 12 | 12 | #N/A | 12
~31~1~6~~-27~ | Deaerator [31] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 11 | 11 | #N/A | 11
~67~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Specified outlet temperature | C | 325 | 325 | #N/A | 325
~67~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Specified outlet temperature | C | 418 | 418 | #N/A | 418
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~69~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Specified outlet temperature | C | 515 | 515 | #N/A | 515
~69~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed gas temperature drop | C | 1.1111 | 1.1111 | #N/A | 1.1111
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 317 | 317 | #N/A | 317
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.6181 | 99.6181 | #N/A | 99.6181
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.48135 | 0.48135 | #N/A | 0.48135
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 0 | 0 | #N/A | 0
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 38.6052 | 38.6052 | #N/A | 38.6052
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 22.8433 | 22.8433 | #N/A | 22.8433
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 475.0406 | 475.0406 | #N/A | 475.0406
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 57.9711 | 57.9711 | #N/A | 57.9711
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~66~1~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan design point overall pressure rise | millibar | 3.5334 | 3.5334 | #N/A | 3.5334
91¦~66~1~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~66~1~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~66~1~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~66~1~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~7~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~66~1~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~66~1~16~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss | kW | 1.0086 | 1.0086 | #N/A | 1.0086
91¦~66~1~13~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~66~1~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 226.2071 | 226.2071 | #N/A | 226.2071
91¦~66~1~12~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 3.608 | 3.608 | #N/A | 3.608
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan design point overall pressure rise | millibar | 24.9066 | 24.9066 | #N/A | 24.9066
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss | kW | 1.9109 | 1.9109 | #N/A | 1.9109
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan off-design control damper dP | millibar | 2.0531e-06 | 2.0531e-06 | #N/A | 2.0531e-06
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 61.2029 | 61.2029 | #N/A | 61.2029
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 23.5974 | 23.5974 | #N/A | 23.5974
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~16~1~2~~-38~ | Feedwater Heater [16] - HPH-1 : Design point FW temperature @ heater exit | C | 268.4385 | 268.4385 | #N/A | 268.4385
91¦~16~1~3~~-38~ | Feedwater Heater [16] - HPH-1 : Design point terminal difference | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~4~~-38~ | Feedwater Heater [16] - HPH-1 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~16~1~19~~-38~ | Feedwater Heater [16] - HPH-1 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~16~1~5~~-38~ | Feedwater Heater [16] - HPH-1 : Design point minimum pinch | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~6~~-38~ | Feedwater Heater [16] - HPH-1 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~16~2~2~~-38~ | Feedwater Heater [16] - HPH-1 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~16~1~16~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature @ heater exit at off-design | C | 268.4385 | 268.4385 | #N/A | 268.4385
91¦~16~1~8~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~16~1~9~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~16~1~10~~-38~ | Feedwater Heater [16] - HPH-1 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~16~1~11~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam mass flow | t/h | 56.1408 | 56.1408 | #N/A | 56.1408
91¦~16~1~12~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water mass flow | t/h | 835.3832 | 835.3832 | #N/A | 835.3832
91¦~16~1~13~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of condensing section | kW/C | 3273.1946 | 3273.1946 | #N/A | 3273.1946
91¦~16~1~20~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of drain cooling section | kW/C | 193.2963 | 193.2963 | #N/A | 193.2963
91¦~16~1~21~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~16~1~14~~-38~ | Feedwater Heater [16] - HPH-1 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~16~1~15~~-38~ | Feedwater Heater [16] - HPH-1 : Water-side flow resistance coefficient | m^-4 | 0.021001 | 0.021001 | #N/A | 0.021001
91¦~16~1~17~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~16~1~18~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~2~~-38~ | Feedwater Heater [17] - HPH-2 : Design point FW temperature @ heater exit | C | 238.7984 | 238.7984 | #N/A | 238.7984
91¦~17~1~3~~-38~ | Feedwater Heater [17] - HPH-2 : Design point terminal difference | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~4~~-38~ | Feedwater Heater [17] - HPH-2 : Design point drain cooler approach | C | 5.6 | 5.6 | #N/A | 5.6
91¦~17~1~19~~-38~ | Feedwater Heater [17] - HPH-2 : Design point residual superheat | C | 2.8 | 2.8 | #N/A | 2.8
91¦~17~1~5~~-38~ | Feedwater Heater [17] - HPH-2 : Design point minimum pinch | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~6~~-38~ | Feedwater Heater [17] - HPH-2 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~17~2~2~~-38~ | Feedwater Heater [17] - HPH-2 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~17~1~16~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature @ heater exit at off-design | C | 238.7984 | 238.7984 | #N/A | 238.7984
91¦~17~1~8~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~17~1~9~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~17~1~10~~-38~ | Feedwater Heater [17] - HPH-2 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~17~1~11~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam mass flow | t/h | 117.5333 | 117.5333 | #N/A | 117.5333
91¦~17~1~12~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water mass flow | t/h | 835.3832 | 835.3832 | #N/A | 835.3832
91¦~17~1~13~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of condensing section | kW/C | 5008.3823 | 5008.3823 | #N/A | 5008.3823
91¦~17~1~20~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of drain cooling section | kW/C | 314.6343 | 314.6343 | #N/A | 314.6343
91¦~17~1~21~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~17~1~14~~-38~ | Feedwater Heater [17] - HPH-2 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~17~1~15~~-38~ | Feedwater Heater [17] - HPH-2 : Water-side flow resistance coefficient | m^-4 | 0.021421 | 0.021421 | #N/A | 0.021421
91¦~17~1~17~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~17~1~18~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~24~1~2~~-38~ | Feedwater Heater [24] - HPH-3 : Design point FW temperature @ heater exit | C | 201.1456 | 201.1456 | #N/A | 201.1456
91¦~24~1~3~~-38~ | Feedwater Heater [24] - HPH-3 : Design point terminal difference | C | 0.38 | 0.38 | #N/A | 0.38
91¦~24~1~4~~-38~ | Feedwater Heater [24] - HPH-3 : Design point drain cooler approach | C | 2.5 | 2.5 | #N/A | 2.5
91¦~24~1~19~~-38~ | Feedwater Heater [24] - HPH-3 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~24~1~5~~-38~ | Feedwater Heater [24] - HPH-3 : Design point minimum pinch | C | 0.3 | 0.3 | #N/A | 0.3
91¦~24~1~6~~-38~ | Feedwater Heater [24] - HPH-3 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~24~2~2~~-38~ | Feedwater Heater [24] - HPH-3 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~24~1~16~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature @ heater exit at off-design | C | 201.1456 | 201.1456 | #N/A | 201.1456
91¦~24~1~8~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~24~1~9~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~24~1~10~~-38~ | Feedwater Heater [24] - HPH-3 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~24~1~11~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam mass flow | t/h | 142.8921 | 142.8921 | #N/A | 142.8921
91¦~24~1~12~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water mass flow | t/h | 835.3832 | 835.3832 | #N/A | 835.3832
91¦~24~1~13~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of condensing section | kW/C | 3955.1506 | 3955.1506 | #N/A | 3955.1506
91¦~24~1~20~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of drain cooling section | kW/C | 431.6781 | 431.6781 | #N/A | 431.6781
91¦~24~1~21~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~24~1~14~~-38~ | Feedwater Heater [24] - HPH-3 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~24~1~15~~-38~ | Feedwater Heater [24] - HPH-3 : Water-side flow resistance coefficient | m^-4 | 0.021849 | 0.021849 | #N/A | 0.021849
91¦~24~1~17~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~24~1~18~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~53~1~2~~-38~ | Feedwater Heater [53] - LPH-8 : Design point FW temperature @ heater exit | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~3~~-38~ | Feedwater Heater [53] - LPH-8 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~53~1~4~~-38~ | Feedwater Heater [53] - LPH-8 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~53~1~19~~-38~ | Feedwater Heater [53] - LPH-8 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~53~1~5~~-38~ | Feedwater Heater [53] - LPH-8 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~53~1~6~~-38~ | Feedwater Heater [53] - LPH-8 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~53~2~2~~-38~ | Feedwater Heater [53] - LPH-8 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~53~1~16~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature @ heater exit at off-design | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~8~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~53~1~9~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~53~1~10~~-38~ | Feedwater Heater [53] - LPH-8 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~53~1~11~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam mass flow | t/h | 93.9353 | 93.9353 | #N/A | 93.9353
91¦~53~1~12~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water mass flow | t/h | 650.5074 | 650.5074 | #N/A | 650.5074
91¦~53~1~13~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of condensing section | kW/C | 915.1556 | 915.1556 | #N/A | 915.1556
91¦~53~1~20~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of drain cooling section | kW/C | 242.9729 | 242.9729 | #N/A | 242.9729
91¦~53~1~21~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~53~1~14~~-38~ | Feedwater Heater [53] - LPH-8 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~53~1~15~~-38~ | Feedwater Heater [53] - LPH-8 : Water-side flow resistance coefficient | m^-4 | 0.0023019 | 0.0023019 | #N/A | 0.0023019
91¦~53~1~17~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~53~1~18~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~54~1~2~~-38~ | Feedwater Heater [54] - LPH-7 : Design point FW temperature @ heater exit | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~3~~-38~ | Feedwater Heater [54] - LPH-7 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~54~1~4~~-38~ | Feedwater Heater [54] - LPH-7 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~54~1~19~~-38~ | Feedwater Heater [54] - LPH-7 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~54~1~5~~-38~ | Feedwater Heater [54] - LPH-7 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~54~1~6~~-38~ | Feedwater Heater [54] - LPH-7 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~54~2~2~~-38~ | Feedwater Heater [54] - LPH-7 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~54~1~16~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature @ heater exit at off-design | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~8~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~54~1~9~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~54~1~10~~-38~ | Feedwater Heater [54] - LPH-7 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~54~1~11~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam mass flow | t/h | 77.5411 | 77.5411 | #N/A | 77.5411
91¦~54~1~12~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water mass flow | t/h | 650.5074 | 650.5074 | #N/A | 650.5074
91¦~54~1~13~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of condensing section | kW/C | 1142.2688 | 1142.2688 | #N/A | 1142.2688
91¦~54~1~20~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of drain cooling section | kW/C | 225.9312 | 225.9312 | #N/A | 225.9312
91¦~54~1~21~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~54~1~14~~-38~ | Feedwater Heater [54] - LPH-7 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~54~1~15~~-38~ | Feedwater Heater [54] - LPH-7 : Water-side flow resistance coefficient | m^-4 | 0.0022568 | 0.0022568 | #N/A | 0.0022568
91¦~54~1~17~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~54~1~18~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~55~1~2~~-38~ | Feedwater Heater [55] - LPH-6 : Design point FW temperature @ heater exit | C | 102.5815 | 102.5815 | #N/A | 102.5815
91¦~55~1~3~~-38~ | Feedwater Heater [55] - LPH-6 : Design point terminal difference | C | 5.7 | 5.7 | #N/A | 5.7
91¦~55~1~4~~-38~ | Feedwater Heater [55] - LPH-6 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~55~1~19~~-38~ | Feedwater Heater [55] - LPH-6 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~55~1~5~~-38~ | Feedwater Heater [55] - LPH-6 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~55~1~6~~-38~ | Feedwater Heater [55] - LPH-6 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~55~2~2~~-38~ | Feedwater Heater [55] - LPH-6 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~55~1~16~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature @ heater exit at off-design | C | 102.5815 | 102.5815 | #N/A | 102.5815
91¦~55~1~8~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~55~1~9~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~55~1~10~~-38~ | Feedwater Heater [55] - LPH-6 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~55~1~11~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam mass flow | t/h | 53.8701 | 53.8701 | #N/A | 53.8701
91¦~55~1~12~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water mass flow | t/h | 650.5074 | 650.5074 | #N/A | 650.5074
91¦~55~1~13~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of condensing section | kW/C | 1027.843 | 1027.843 | #N/A | 1027.843
91¦~55~1~20~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of drain cooling section | kW/C | 141.894 | 141.894 | #N/A | 141.894
91¦~55~1~21~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~55~1~14~~-38~ | Feedwater Heater [55] - LPH-6 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~55~1~15~~-38~ | Feedwater Heater [55] - LPH-6 : Water-side flow resistance coefficient | m^-4 | 0.0022125 | 0.0022125 | #N/A | 0.0022125
91¦~55~1~17~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~55~1~18~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~56~1~2~~-38~ | Feedwater Heater [56] - LPH-5 : Design point FW temperature @ heater exit | C | 133.9635 | 133.9635 | #N/A | 133.9635
91¦~56~1~3~~-38~ | Feedwater Heater [56] - LPH-5 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~56~1~4~~-38~ | Feedwater Heater [56] - LPH-5 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~56~1~19~~-38~ | Feedwater Heater [56] - LPH-5 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~56~1~5~~-38~ | Feedwater Heater [56] - LPH-5 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~56~1~6~~-38~ | Feedwater Heater [56] - LPH-5 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~56~2~2~~-38~ | Feedwater Heater [56] - LPH-5 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~56~1~16~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature @ heater exit at off-design | C | 133.9635 | 133.9635 | #N/A | 133.9635
91¦~56~1~8~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~56~1~9~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~56~1~10~~-38~ | Feedwater Heater [56] - LPH-5 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~56~1~11~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam mass flow | t/h | 34.3848 | 34.3848 | #N/A | 34.3848
91¦~56~1~12~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water mass flow | t/h | 650.5074 | 650.5074 | #N/A | 650.5074
91¦~56~1~13~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of condensing section | kW/C | 1408.4451 | 1408.4451 | #N/A | 1408.4451
91¦~56~1~20~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of drain cooling section | kW/C | 108.5123 | 108.5123 | #N/A | 108.5123
91¦~56~1~21~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~56~1~14~~-38~ | Feedwater Heater [56] - LPH-5 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~56~1~15~~-38~ | Feedwater Heater [56] - LPH-5 : Water-side flow resistance coefficient | m^-4 | 0.0021691 | 0.0021691 | #N/A | 0.0021691
91¦~56~1~17~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~56~1~18~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30 | #N/A | 30
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 215 | 215 | #N/A | 215
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100 | #N/A | TJA_Whatif100
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 27.99 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 5.36 | 5.36 | #N/A | 5.36
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 48.63 | 48.63 | #N/A | 48.63
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 3.99 | 3.99 | #N/A | 3.99
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.8 | 0.8 | #N/A | 0.8
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.19 | 0.19 | #N/A | 0.19
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 13.04 | 13.04 | #N/A | 13.04
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 4500 | 4500 | 4500
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 32.75 | 32.75 | #N/A | 32.75
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~7~1~10~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam production rate | t/h | 833.3 | 945.59 | 945.59 | 945.59
91¦~7~1~18~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1141.4 | 1145.33 | 1145.33 | 1145.33
91¦~7~1~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25 | 25 | 25
91¦~7~1~7~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Minor heat loss | % | 3.25 | 3.25 | #N/A | 3.25
91¦~7~1~8~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gage pressure | millibar | -0.62267 | -0.62267 | #N/A | -0.62267
91¦~7~1~6~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Secondary air pressure drop | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
91¦~7~1~39~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | % | 20 | 20 | #N/A | 20
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content (for emission level definition) | % | 5.3 | 5.3 | #N/A | 5.3
91¦~7~1~152~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
91¦~7~1~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit temperature @ design | C | 60.8 | 60.8 | #N/A | 60.8
91¦~7~1~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inlet air/fuel mass ratio in pulverizer @ design |  | 1.8 | 1.8 | #N/A | 1.8
91¦~7~1~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverized fuel fineness @ design | % | 65 | 65 | #N/A | 65
91¦~7~1~8~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Power consumption converted into heat in pulverizer @ design | % | 80 | 80 | #N/A | 80
91¦~7~1~7~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : % of as-received fuel moisture evaporated in pulverizer | % | 60 | 60 | #N/A | 60
91¦~7~1~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pressure drop in pulverizer | millibar | 20 | 20 | #N/A | 20
91¦~7~1~18~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit gauge pressure | millibar | 99.6264 | 99.6264 | #N/A | 99.6264
91¦~7~1~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer nameplate specific power | kWh/tonne | 22.0462 | 22.0462 | #N/A | 22.0462
91¦~3~1~2~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332 | #N/A | 1.0332
91¦~3~1~3~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~3~1~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 695.23 | 695.23 | #N/A | 695.23
91¦~3~1~5~~-1~ | Gas/Air Source [3] - Sec.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~3~1~18~~-1~ | Gas/Air Source [3] - Sec.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~3~1~21~~-1~ | Gas/Air Source [3] - Sec.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~3~1~22~~-1~ | Gas/Air Source [3] - Sec.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~11~1~2~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129 | #N/A | 1.1129
91¦~11~1~3~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~11~1~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 579.01 | 579.01 | #N/A | 579.01
91¦~11~1~5~~-1~ | Gas/Air Source [11] - Prim.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~11~1~18~~-1~ | Gas/Air Source [11] - Prim.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~11~1~21~~-1~ | Gas/Air Source [11] - Prim.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - Prim.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~40~1~12~~-168~ | General Pump [40] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Rating / design point load |  | 1.0212 | 1.0212 | #N/A | 1.0212
91¦~6~1~1~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25 | #N/A | 25
91¦~6~1~2~~-46~ | Makeup / Blowdown [6] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99 | #N/A | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01 | #N/A | 0.01
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3 | #N/A | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7 | #N/A | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989 | #N/A | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011 | #N/A | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761 | #N/A | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239 | #N/A | 0.79239
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~35~1~4~~-107~ | Pipe (PCE) [35] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~35~1~9~~-107~ | Pipe (PCE) [35] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~36~1~4~~-107~ | Pipe (PCE) [36] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~36~1~9~~-107~ | Pipe (PCE) [36] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~37~1~4~~-107~ | Pipe (PCE) [37] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~37~1~9~~-107~ | Pipe (PCE) [37] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~60~1~4~~-107~ | Pipe (PCE) [60] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~60~1~9~~-107~ | Pipe (PCE) [60] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~61~1~4~~-107~ | Pipe (PCE) [61] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~61~1~9~~-107~ | Pipe (PCE) [61] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~63~1~4~~-107~ | Pipe (PCE) [63] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~63~1~9~~-107~ | Pipe (PCE) [63] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~64~1~4~~-107~ | Pipe (PCE) [64] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~64~1~9~~-107~ | Pipe (PCE) [64] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~73~1~4~~-107~ | Pipe (PCE) [73] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~73~1~9~~-107~ | Pipe (PCE) [73] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~74~1~4~~-107~ | Pipe (PCE) [74] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~74~1~9~~-107~ | Pipe (PCE) [74] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~75~1~4~~-107~ | Pipe (PCE) [75] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~75~1~9~~-107~ | Pipe (PCE) [75] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~76~1~4~~-107~ | Pipe (PCE) [76] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~76~1~9~~-107~ | Pipe (PCE) [76] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
83¦91¦~82~1~12~~-100~ | Pump (PCE) [82] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~83~1~12~~-100~ | Pump (PCE) [83] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
91¦~8~1~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air outlet temperature | C | 273.8889 | 273.8889 | #N/A | 273.8889
91¦~8~1~3~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path cold end leakage | % | 7 | 7 | #N/A | 7
91¦~8~1~4~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path hot end leakage | % | 3 | 3 | #N/A | 3
91¦~8~1~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air outlet temperature | C | 343.3334 | 343.3334 | #N/A | 343.3334
91¦~8~1~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air cold end leakage | % | 10 | 10 | #N/A | 10
91¦~8~1~14~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air hot end leakage | % | 5 | 5 | #N/A | 5
91¦~1~1~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump design point overall pressure rise | bar | 163.4004 | 163.4004 | #N/A | 163.4004
91¦~1~1~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~1~1~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Flow margin | % | 10 | 10 | #N/A | 10
91¦~1~1~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~1~1~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Design point RPM |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~1~1~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~1~1~16~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss | kW | 92.7797 | 92.7797 | #N/A | 92.7797
91¦~1~1~13~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~1~1~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal RPM for off-design pump curve |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~11~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal rating flow for off-design pump curve | t/h | 466.7679 | 466.7679 | #N/A | 466.7679
91¦~1~1~12~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal pressure rise for off-design pump curve | bar | 154.7352 | 154.7352 | #N/A | 154.7352
91¦~1~1~2~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 8.98 | 8.98 | #N/A | 8.98
91¦~1~1~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~1~1~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~1~1~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~1~1~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~1~1~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~1~5~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~1~1~5~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~1~1~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~86~1~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump design point overall pressure rise | bar | 163.4004 | 163.4004 | #N/A | 163.4004
91¦~86~1~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~86~1~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Flow margin | % | 10 | 10 | #N/A | 10
91¦~86~1~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~86~1~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Design point RPM |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~86~1~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~86~1~16~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss | kW | 92.7797 | 92.7797 | #N/A | 92.7797
91¦~86~1~13~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~86~1~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal RPM for off-design pump curve |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~11~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal rating flow for off-design pump curve | t/h | 466.7679 | 466.7679 | #N/A | 466.7679
91¦~86~1~12~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal pressure rise for off-design pump curve | bar | 154.7352 | 154.7352 | #N/A | 154.7352
91¦~86~1~2~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 9.246 | 9.246 | #N/A | 9.246
91¦~86~1~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~86~1~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~86~1~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~86~1~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~86~1~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~86~5~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~86~1~5~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~86~1~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~34~1~84~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~34~1~72~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Assumed water-side pressure drop for TD mode | bar | 0.35 | 0.35 | #N/A | 0.35
91¦~34~1~34~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Min. pinch temp. difference | C | 2.5 | 2.5 | #N/A | 2.5
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998 | #N/A | 0.9998
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8 | #N/A | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195 | #N/A | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005 | #N/A | 0.005
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001 | #N/A | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057 | #N/A | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843 | #N/A | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668 | #N/A | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332 | #N/A | 0.0332
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417 | #N/A | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005 | #N/A | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578 | #N/A | 0.1578
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 534.4 | 534.17 | 534.17 | 534.17
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 420 | 420 | #N/A | 420
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~77~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Desired steam outlet temperature | C | 511 | 511 | #N/A | 511
~77~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~77~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~77~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~78~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Desired steam outlet temperature | C | 534.1 | 534.1 | #N/A | 534.1
~78~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~78~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~78~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~23~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Desired steam outlet temperature | C | 490 | 490 | #N/A | 490
~23~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~23~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~23~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~79~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Desired steam outlet temperature | C | 517 | 517 | #N/A | 517
~79~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~79~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~79~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
~14~2~2~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~14~1~5~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~14~1~6~~-32~ | Boiler Assembly [1]: Valve [14] : Upstream set point | bar | 36.6 | 36.6 | #N/A | 36.6
~14~1~8~~-32~ | Boiler Assembly [1]: Valve [14] : Downstream set point | bar | 36.6045 | 36.6045 | #N/A | 36.6045
~14~1~7~~-32~ | Boiler Assembly [1]: Valve [14] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~80~2~2~~-32~ | Valve [80] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~80~1~5~~-32~ | Valve [80] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~80~1~6~~-32~ | Valve [80] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~8~~-32~ | Valve [80] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~7~~-32~ | Valve [80] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~81~2~2~~-32~ | Valve [81] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~81~1~5~~-32~ | Valve [81] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~81~1~6~~-32~ | Valve [81] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~8~~-32~ | Valve [81] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~7~~-32~ | Valve [81] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~58~1~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5 | #N/A | 3.5
91¦~58~1~21~~-14~ | Water Sink [58] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~58~1~22~~-14~ | Water Sink [58] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~57~1~2~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~57~1~3~~-9~ | Water Source [57] : Temperature | C | 27.3 | 29 | 29 | 29
91¦~57~1~4~~-9~ | Water Source [57] : Steam quality |  | -2 | -2 | #N/A | -2
91¦~57~1~5~~-9~ | Water Source [57] : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~57~1~21~~-9~ | Water Source [57] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~57~1~22~~-9~ | Water Source [57] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~59~1~53~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975 | #N/A | 0.0975
~59~1~5~~-104~ | Water-cooled Condenser (PCE) [59] : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~59~1~9~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
~2~23~1~~-10100~ | Fix Pressure Stream 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 33.585 | 34.4868 | 34.4868 | 34.4868
~2~32~1~~-10100~ | Fix Pressure Stream 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 30.6 | 31.4223 | 31.4223 | 31.4223
~2~34~1~~-10100~ | Fix Pressure Stream 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 16.37 | 16.81 | 16.81 | 16.81
~2~41~1~~-10100~ | Fix Pressure Stream 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 9.246 | 9.4941 | 9.4941 | 9.4941
91¦~1~1~4~~-20000~ | Generator [1]: Design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~1~1~5~~-20000~ | Generator [1]: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~1~3~18~~-20000~ | Generator [1]: Generator mech loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~13~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [13] - G[1] |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~66~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [66] - SA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux |  | 1 | 1 | #N/A | 1
91¦~40~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [40] - CP |  | 1 | 1 | #N/A | 1
91¦~82~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [82] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~83~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [83] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~13~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~13~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~13~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~1~-4100~ | ST Assembly [1]: Leakage flow (HPT LP leak 1 to LPT crossover) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~13~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~13~1~2~~-11~ | ST Assembly [1]: ST Group [13] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 152.532 | 156.63 | 156.63 | 156.63
91¦~13~1~3~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry step efficiency | % | 85.1821 | 85.1821 | #N/A | 85.1821
91¦~13~1~7~~-11~ | ST Assembly [1]: ST Group [13] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~13~5~15~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~13~1~4~~-11~ | ST Assembly [1]: ST Group [13] : Reference pressure ratio for steam turbine expansion step |  | 1.1 | 1.1 | #N/A | 1.1
91¦~13~1~5~~-11~ | ST Assembly [1]: ST Group [13] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~13~1~6~~-11~ | ST Assembly [1]: ST Group [13] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~13~1~11~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~13~1~12~~-11~ | ST Assembly [1]: ST Group [13] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~15~1~2~~-11~ | ST Assembly [1]: ST Group [15] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 56.075 | 57.582 | 57.582 | 57.582
91¦~15~1~20~~-11~ | ST Assembly [1]: ST Group [15] : Outlet specific enthalpy (before exhaust loss if any) | kJ/kg | 3047.1499 | 3047.1499 | #N/A | 3047.1499
91¦~15~1~7~~-11~ | ST Assembly [1]: ST Group [15] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~15~5~15~~-11~ | ST Assembly [1]: ST Group [15] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~15~1~4~~-11~ | ST Assembly [1]: ST Group [15] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~15~1~5~~-11~ | ST Assembly [1]: ST Group [15] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~15~1~6~~-11~ | ST Assembly [1]: ST Group [15] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~15~1~11~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~15~1~12~~-11~ | ST Assembly [1]: ST Group [15] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~26~1~2~~-11~ | ST Assembly [1]: ST Group [26] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 30.6 | 31.4223 | 31.4223 | 31.4223
91¦~26~1~3~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry step efficiency | % | 88.6914 | 88.6914 | #N/A | 88.6914
91¦~26~1~7~~-11~ | ST Assembly [1]: ST Group [26] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~26~5~15~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~26~1~4~~-11~ | ST Assembly [1]: ST Group [26] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~26~1~5~~-11~ | ST Assembly [1]: ST Group [26] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~26~1~6~~-11~ | ST Assembly [1]: ST Group [26] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~26~1~11~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~26~1~12~~-11~ | ST Assembly [1]: ST Group [26] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~28~1~2~~-11~ | ST Assembly [1]: ST Group [28] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 16.37 | 16.81 | 16.81 | 16.81
91¦~28~1~3~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry step efficiency | % | 89.8737 | 89.8737 | #N/A | 89.8737
91¦~28~1~7~~-11~ | ST Assembly [1]: ST Group [28] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~28~5~15~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~28~1~4~~-11~ | ST Assembly [1]: ST Group [28] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~28~1~5~~-11~ | ST Assembly [1]: ST Group [28] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~6~~-11~ | ST Assembly [1]: ST Group [28] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~28~1~11~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~28~1~12~~-11~ | ST Assembly [1]: ST Group [28] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~44~1~2~~-11~ | ST Assembly [1]: ST Group [44] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 9.246 | 9.4941 | 9.4941 | 9.4941
91¦~44~1~3~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry step efficiency | % | 90.9151 | 90.9151 | #N/A | 90.9151
91¦~44~1~7~~-11~ | ST Assembly [1]: ST Group [44] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~44~5~15~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~44~1~4~~-11~ | ST Assembly [1]: ST Group [44] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~44~1~5~~-11~ | ST Assembly [1]: ST Group [44] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~44~1~6~~-11~ | ST Assembly [1]: ST Group [44] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~44~1~11~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~44~1~12~~-11~ | ST Assembly [1]: ST Group [44] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~45~1~2~~-11~ | ST Assembly [1]: ST Group [45] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 3.642 | 3.7398 | 3.7398 | 3.7398
91¦~45~1~3~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry step efficiency | % | 92.0601 | 92.0601 | #N/A | 92.0601
91¦~45~1~7~~-11~ | ST Assembly [1]: ST Group [45] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~45~5~15~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~45~1~4~~-11~ | ST Assembly [1]: ST Group [45] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~45~1~5~~-11~ | ST Assembly [1]: ST Group [45] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~45~1~6~~-11~ | ST Assembly [1]: ST Group [45] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~45~1~11~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~45~1~12~~-11~ | ST Assembly [1]: ST Group [45] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~46~1~2~~-11~ | ST Assembly [1]: ST Group [46] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.38 | 1.4169 | 1.4169 | 1.4169
91¦~46~1~3~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry step efficiency | % | 92.3209 | 92.3209 | #N/A | 92.3209
91¦~46~1~7~~-11~ | ST Assembly [1]: ST Group [46] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~46~5~15~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~46~1~4~~-11~ | ST Assembly [1]: ST Group [46] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~46~1~5~~-11~ | ST Assembly [1]: ST Group [46] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~46~1~6~~-11~ | ST Assembly [1]: ST Group [46] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~46~1~11~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~46~1~12~~-11~ | ST Assembly [1]: ST Group [46] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~47~1~2~~-11~ | ST Assembly [1]: ST Group [47] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.78 | 0.78 | #N/A | 0.78
91¦~47~1~3~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry step efficiency | % | 92.25 | 92.25 | #N/A | 92.25
91¦~47~1~7~~-11~ | ST Assembly [1]: ST Group [47] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~47~5~15~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~47~1~4~~-11~ | ST Assembly [1]: ST Group [47] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~47~1~5~~-11~ | ST Assembly [1]: ST Group [47] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~47~1~6~~-11~ | ST Assembly [1]: ST Group [47] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~47~1~11~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~47~1~12~~-11~ | ST Assembly [1]: ST Group [47] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~5~1~2~~-11~ | ST Assembly [1]: ST Group [5] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.283 | 0.283 | #N/A | 0.283
91¦~5~1~3~~-11~ | ST Assembly [1]: ST Group [5] : Design point dry step efficiency | % | 92.15 | 92.15 | #N/A | 92.15
91¦~5~1~7~~-11~ | ST Assembly [1]: ST Group [5] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~5~5~6~~-11~ | ST Assembly [1]: ST Group [5] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~5~1~4~~-11~ | ST Assembly [1]: ST Group [5] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~5~1~5~~-11~ | ST Assembly [1]: ST Group [5] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~5~1~6~~-11~ | ST Assembly [1]: ST Group [5] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~5~1~11~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~5~1~12~~-11~ | ST Assembly [1]: ST Group [5] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~2~1~~~-5007~ | HIP Turbin: Label 1 |  | BFPT-A | BFPT-A | #N/A | BFPT-A
~2~2~~~-5007~ | HIP Turbin: Label 2 |  | BFPT-B | BFPT-B | #N/A | BFPT-B
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 26.95 | 26.95
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 75.41 | 75.41
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 23.5477 | 23.5477
~~~4~~-5000~ | Plant Summary: Gross power | kW | 265504.9062 | 265504.9062
~~~7~~-5000~ | Plant Summary: Net power | kW | 248972.5312 | 248972.5312
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 16532.3672 | 16532.3672
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 15204.8428 | 15204.8428
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 1327.5245 | 1327.5245
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 39.2824 | 39.2824
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 9164.415 | 9164.415
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 36.8364 | 36.8364
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 9772.9541 | 9772.9541
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 675888.125 | 675888.125
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 36.8364 | 36.8364
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 36.8364 | 36.8364
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 33.7971 | 33.7971
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 10651.8027 | 10651.8027
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 736668.4375 | 736668.4375
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 675888.125 | 675888.125
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 36.8364 | 36.8364
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 2.2897 | 2.2897
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 2.0833 | 2.0833
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 675888.125 | 675888.125
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 736668.4375 | 736668.4375
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.362 | 2.362
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 5747.146 | 5747.146
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 54234588 | 54234588
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 68379856 | 68379856
~1~3~1~~-2005~ | Shaft 1: Shaft net power | kW | 268586.9062 | 268586.9062
~1~3~2~~-2005~ | Shaft 1: Shaft speed | RPM | 3000 | 3000
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 2016.6775 | 2016.6775
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 19708.8965 | 19708.8965
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 18.7607 | 18.7607
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 2024.7289 | 2024.7289
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 68379.8594 | 68379.8594
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 274.6482 | 274.6482
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 1280332.75 | 1280332.75
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 20513.957 | 20513.957
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 76.7994 | 76.7994
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 231.2942 | 231.2942
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.43814 | 0.43814
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 669743.3125 | 669743.3125
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.029913 | 0.029913
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.9522 | 5.9522
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 54234588 | 54234588
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 54234588 | 54234588
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 9264151 | 9264151
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 63498740 | 63498740
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 68379856 | 68379856
~1~9~13~~-5003~ | Generator / Motor Power: Generator [1] of ST Assembly [1] power | kW | 265504.9062 | 265504.9062
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 929.257 | 929.257
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 2358.0356 | 2358.0356
~4~66~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [66] - SA Fan : aux | kW | 106.5465 | 106.5465
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan : aux | kW | 200.4736 | 200.4736
~4~7~158~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux | kW | 4787.0396 | 4787.0396
~4~40~168~~-5003~ | Generator / Motor Power: General Pump [40] - CP | kW | 288.0398 | 288.0398
~4~82~100~~-5003~ | Generator / Motor Power: Pump (PCE) [82] - CWP-1 | kW | 1661.4205 | 1661.4205
~4~83~100~~-5003~ | Generator / Motor Power: Pump (PCE) [83] - CWP-2 | kW | 1661.4205 | 1661.4205
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 557.5603 | 557.5603
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 2655.0491 | 2655.0491
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 1327.5245 | 1327.5245
~5~9~13~1~-5003~ | Generator / Motor Power: Shaft-1 net power | kW | 268586.9062 | 268586.9062
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 15204.8428 | 15204.8428
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 675888.125 | 675888.125
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~3~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer | kW | -304.9287 | -304.9287
91¦~3~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer | kW | -88.9669 | -88.9669
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air status |  | Ignored | Ignored
93¦~6~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer | kW | 66.7378 | 66.7378
91¦~6~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~57~3~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer | kW | 942656.375 | 942656.375
91¦~57~1~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer multiplier |  | 1 | 1
82¦71¦~57~5~10~1~-7000~ | Energy Inflow: Water Source [57] status |  | Ignored | Ignored
93¦~6~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer | kW | 0 | 0
91¦~6~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~58~3~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer | kW | 1290164.25 | 1290164.25
91¦~58~1~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer multiplier |  | 1 | 1
82¦71¦~58~5~10~2~-7000~ | Energy Outflow: Water Sink [58] status |  | Ignored | Ignored
93¦~13~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [13] shaft power | kW | 60016.5977 | 60016.5977
93¦~15~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [15] shaft power | kW | 20737.0547 | 20737.0547
93¦~26~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [26] shaft power | kW | 37203.2188 | 37203.2188
93¦~28~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [28] shaft power | kW | 29839.543 | 29839.543
93¦~44~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [44] shaft power | kW | 37877.9414 | 37877.9414
93¦~45~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [45] shaft power | kW | 30789.873 | 30789.873
93¦~46~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [46] shaft power | kW | 14799.0479 | 14799.0479
93¦~47~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [47] shaft power | kW | 22068.9531 | 22068.9531
93¦~5~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [5] shaft power | kW | 15254.6992 | 15254.6992
82¦71¦~5~5~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] power | kW | 265504.9062 | 265504.9062
91¦~5~1~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] multiplier |  | 1 | 1
93¦~5~3~3~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] efficiency | % | 98.8525 | 98.8525
82¦71¦~5~5~10~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] status |  | power producer | power producer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 929.257 | 929.257
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 2358.0356 | 2358.0356
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~66~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux power | kW | 106.5465 | 106.5465
91¦~66~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux multiplier |  | 1 | 1
82¦71¦~66~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux power | kW | 200.4736 | 200.4736
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux status |  | power consumer | power consumer
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux power | kW | 4787.0396 | 4787.0396
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux status |  | power consumer | power consumer
93¦~40~3~2~4~-7000~ | Auxiliary Device: General Pump [40] - CP power | kW | 288.0398 | 288.0398
91¦~40~1~1~4~-7000~ | Auxiliary Device: General Pump [40] - CP multiplier |  | 1 | 1
82¦71¦~40~5~10~4~-7000~ | Auxiliary Device: General Pump [40] - CP status |  | power consumer | power consumer
93¦~82~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 power | kW | 1661.4205 | 1661.4205
91¦~82~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 multiplier |  | 1 | 1
82¦71¦~82~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 status |  | power consumer | power consumer
93¦~83~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 power | kW | 1661.4205 | 1661.4205
91¦~83~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 multiplier |  | 1 | 1
82¦71¦~83~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 status |  | power consumer | power consumer
~31~6~1~~-27~ | Deaerator [31] - DAER : Mode |  | TD | TD
~31~6~3~~-27~ | Deaerator [31] - DAER : DA pressure specification |  | Specified by user | Specified by user
~31~4~4~~-27~ | Deaerator [31] - DAER : Operating pressure | bar | 9.0647 | 9.0647
~31~4~5~~-27~ | Deaerator [31] - DAER : Temperature | C | 175.6625 | 175.6625
93¦~31~4~7~~-27~ | Deaerator [31] - DAER : FW inlet pressure | bar | 10.2423 | 10.2423
93¦~31~4~8~~-27~ | Deaerator [31] - DAER : FW inlet temperature | C | 133.9796 | 133.9796
93¦~31~4~28~~-27~ | Deaerator [31] - DAER : FW inlet enthalpy | kJ/kg | 563.8093 | 563.8093
93¦~31~4~9~~-27~ | Deaerator [31] - DAER : FW inlet mass flow | t/h | 650.5074 | 650.5074
93¦~31~4~23~~-27~ | Deaerator [31] - DAER : Additional water head at inlet | bar | 1.1775 | 1.1775
93¦~31~4~10~~-27~ | Deaerator [31] - DAER : Heating stream pressure | bar | 9.0647 | 9.0647
93¦~31~4~12~~-27~ | Deaerator [31] - DAER : Heating stream temperature | C | 353.1704 | 353.1704
93¦~31~4~11~~-27~ | Deaerator [31] - DAER : Heating stream enthalpy | kJ/kg | 3166.7363 | 3166.7363
93¦~31~4~13~~-27~ | Deaerator [31] - DAER : Heating stream mass flow | t/h | 46.7826 | 46.7826
93¦~31~4~17~~-27~ | Deaerator [31] - DAER : Flash in pressure | bar | 16.049 | 16.049
93¦~31~4~18~~-27~ | Deaerator [31] - DAER : Flash in temperature | C | 181.8336 | 181.8336
93¦~31~4~19~~-27~ | Deaerator [31] - DAER : Flash in enthalpy | kJ/kg | 771.4896 | 771.4896
93¦~31~4~20~~-27~ | Deaerator [31] - DAER : Flash in mass flow | t/h | 142.8921 | 142.8921
93¦~31~4~14~~-27~ | Deaerator [31] - DAER : FW outlet pressure | bar | 10.1442 | 10.1442
93¦~31~4~15~~-27~ | Deaerator [31] - DAER : FW outlet temperature | C | 175.6707 | 175.6707
93¦~31~4~29~~-27~ | Deaerator [31] - DAER : FW outlet enthalpy | kJ/kg | 744.0651 | 744.0651
93¦~31~4~16~~-27~ | Deaerator [31] - DAER : FW outlet mass flow | t/h | 840.1822 | 840.1822
93¦~31~4~24~~-27~ | Deaerator [31] - DAER : Additional water head at outlet | bar | 1.0794 | 1.0794
~67~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Temperature drop | C | 0.085992 | 0.085992
~67~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet pressure | bar | 33.585 | 33.585
~67~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet temperature | C | 325.0843 | 325.0843
~67~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet mass flow | t/h | 713.7567 | 713.7567
~67~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet enthalpy | kJ/kg | 3047.1497 | 3047.1497
~67~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet pressure | bar | 33.585 | 33.585
~67~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet temperature | C | 324.9984 | 324.9984
~67~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet mass flow | t/h | 713.8239 | 713.8239
~67~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet enthalpy | kJ/kg | 3046.9353 | 3046.9353
~67~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray mass flow | t/h | 0.067146 | 0.067146
~67~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray water enthalpy | kJ/kg | 768.6777 | 768.6777
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Temperature drop | C | 2.0003 | 2.0003
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet pressure | bar | 158.7254 | 158.7254
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet temperature | C | 420.0035 | 420.0035
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet mass flow | t/h | 833.2999 | 833.2999
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet enthalpy | kJ/kg | 3033.8652 | 3033.8652
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet pressure | bar | 158.7254 | 158.7254
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet temperature | C | 418.0032 | 418.0032
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet mass flow | t/h | 836.1783 | 836.1783
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet enthalpy | kJ/kg | 3026.0681 | 3026.0681
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray mass flow | t/h | 2.8783 | 2.8783
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray water enthalpy | kJ/kg | 768.6777 | 768.6777
~69~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Temperature drop | C | 2.0003 | 2.0003
~69~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet pressure | bar | 155.5979 | 155.5979
~69~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet temperature | C | 516.9989 | 516.9989
~69~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet mass flow | t/h | 836.1783 | 836.1783
~69~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet enthalpy | kJ/kg | 3352.4443 | 3352.4443
~69~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet pressure | bar | 155.5979 | 155.5979
~69~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet temperature | C | 514.9985 | 514.9985
~69~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet mass flow | t/h | 838.0318 | 838.0318
~69~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet enthalpy | kJ/kg | 3346.7295 | 3346.7295
~69~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray mass flow | t/h | 1.8535 | 1.8535
~69~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray water enthalpy | kJ/kg | 768.6777 | 768.6777
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Heat loss | kW | 80.221 | 80.221
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Temperature drop | C | 1.1111 | 1.1111
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Heat loss | kW | 464.709 | 464.709
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Temperature drop | C | 0 | 0
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Heat loss | kW | 0 | 0
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 835.3832 | 835.3832
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 161.9158 | 161.9158
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 1173.7863 | 1173.7863
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 268.2197 | 268.2197
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 835.3832 | 835.3832
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 160.3127 | 160.3127
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 317 | 317
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1433.7714 | 1433.7714
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 1271.106 | 1271.106
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 6.2274 | 6.2274
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 503.6234 | 503.6234
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 357.8631 | 357.8631
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 51.0935 | 51.0935
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1740.5242 | 1740.5242
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 60330.7148 | 60330.7148
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 60330.7148 | 60330.7148
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 452.4804 | 452.4804
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 1.6031 | 1.6031
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.6181 | 99.6181
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 929.257 | 929.257
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.98686 | 0.98686
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 146.1556 | 146.1556
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 1691952 | 1691952
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 1389.806 | 1389.806
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 6.2274 | 6.2274
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 6.2036 | 6.2036
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.023781 | 0.023781
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 2348.2073 | 2348.2073
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 6546.4287 | 6546.4287
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 8.9674 | 8.9674
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 24.9998 | 24.9998
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 0 | 0
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2114 | 1.2114
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 2284.3337 | 2284.3337
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 2284.3337 | 2284.3337
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 2261.4905 | 2261.4905
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 475.0406 | 475.0406
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 38.6052 | 38.6052
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 38.6052 | 38.6052
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1004 | 80.1004
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 22.8433 | 22.8433
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 2475.9373 | 2475.9373
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.89 | 96.89
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 2358.0356 | 2358.0356
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 2284.3337 | 2284.3337
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.8744 | 96.8744
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 73.702 | 73.702
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 2398.5503 | 2398.5503
82¦71¦~66~5~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~66~5~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~66~1~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of existing units |  | 1 | 1
93¦~66~3~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1
93¦~66~3~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Total shaft power | kW | 100.8585 | 100.8585
93¦~66~3~1~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Shaft power per unit | kW | 100.8585 | 100.8585
93¦~66~3~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan compression power per unit | kW | 99.8499 | 99.8499
93¦~66~3~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan inlet volume flow per unit | m^3/s | 226.2071 | 226.2071
93¦~66~3~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure rise (before control damper) | millibar | 3.5334 | 3.5334
93¦~66~3~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan overall pressure rise | millibar | 3.5334 | 3.5334
93¦~66~3~6~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~66~3~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan polytropic efficiency | % | 80.0232 | 80.0232
93¦~66~3~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200
93¦~66~3~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss per unit | kW | 1.0086 | 1.0086
93¦~66~3~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~66~6~1~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Mode |  | Design | Design
91¦~66~1~7~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate power | kW | 111.8738 | 111.8738
91¦~66~1~19~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate efficiency | % | 94.6881 | 94.6881
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~66~2~8~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Number of operating units |  | 1 | 1
93¦~66~7~2~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electricity consumption | kW | 106.5465 | 106.5465
93¦~66~7~6~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Shaft power | kW | 100.8585 | 100.8585
93¦~66~7~4~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Efficiency | % | 94.6615 | 94.6615
93¦~66~7~3~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electrical loss | kW | 5.688 | 5.688
89¦~66~3~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate motor shaft power | kW | 105.9014 | 105.9014
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Total shaft power | kW | 191.0879 | 191.0879
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Shaft power per unit | kW | 191.0879 | 191.0879
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan compression power per unit | kW | 189.177 | 189.177
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan inlet volume flow per unit | m^3/s | 61.2029 | 61.2029
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure rise (before control damper) | millibar | 24.9066 | 24.9066
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan overall pressure rise | millibar | 24.9066 | 24.9066
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan polytropic efficiency | % | 80.0643 | 80.0643
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss per unit | kW | 1.9109 | 1.9109
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate power | kW | 210.4973 | 210.4973
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate efficiency | % | 95.3415 | 95.3415
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electricity consumption | kW | 200.4736 | 200.4736
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Shaft power | kW | 191.0879 | 191.0879
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Efficiency | % | 95.3182 | 95.3182
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electrical loss | kW | 9.3857 | 9.3857
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate motor shaft power | kW | 200.6423 | 200.6423
82¦71¦~16~5~1~~-38~ | Feedwater Heater [16] - HPH-1 : Mode |  | Design | Design
89¦~16~3~7~~-38~ | Feedwater Heater [16] - HPH-1 : Heat transfer | kW | 32696.6719 | 32696.6719
89¦~16~3~8~~-38~ | Feedwater Heater [16] - HPH-1 : Shell pressure | bar | 54.9755 | 54.9755
89¦~16~3~9~~-38~ | Feedwater Heater [16] - HPH-1 : Saturation temperature | C | 269.9385 | 269.9385
89¦~16~3~13~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature at heater exit | C | 268.4385 | 268.4385
89¦~16~3~11~~-38~ | Feedwater Heater [16] - HPH-1 : Terminal difference | C | 1.5 | 1.5
89¦~16~3~12~~-38~ | Feedwater Heater [16] - HPH-1 : Drain cooler approach | C | 2.8 | 2.8
89¦~16~3~3~~-38~ | Feedwater Heater [16] - HPH-1 : UA of drain cooler section | kW/C | 193.2963 | 193.2963
89¦~16~3~1~~-38~ | Feedwater Heater [16] - HPH-1 : UA of condensing section | kW/C | 3273.1946 | 3273.1946
82¦71¦~17~5~1~~-38~ | Feedwater Heater [17] - HPH-2 : Mode |  | Design | Design
89¦~17~3~7~~-38~ | Feedwater Heater [17] - HPH-2 : Heat transfer | kW | 39403.7656 | 39403.7656
89¦~17~3~8~~-38~ | Feedwater Heater [17] - HPH-2 : Shell pressure | bar | 32.9265 | 32.9265
89¦~17~3~9~~-38~ | Feedwater Heater [17] - HPH-2 : Saturation temperature | C | 239.0764 | 239.0764
89¦~17~3~13~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature at heater exit | C | 238.7984 | 238.7984
89¦~17~3~11~~-38~ | Feedwater Heater [17] - HPH-2 : Terminal difference | C | 0.27802 | 0.27802
89¦~17~3~12~~-38~ | Feedwater Heater [17] - HPH-2 : Drain cooler approach | C | 5.6 | 5.6
89¦~17~3~3~~-38~ | Feedwater Heater [17] - HPH-2 : UA of drain cooler section | kW/C | 314.6343 | 314.6343
89¦~17~3~1~~-38~ | Feedwater Heater [17] - HPH-2 : UA of condensing section | kW/C | 5008.3823 | 5008.3823
82¦71¦~24~5~1~~-38~ | Feedwater Heater [24] - HPH-3 : Mode |  | Design | Design
89¦~24~3~7~~-38~ | Feedwater Heater [24] - HPH-3 : Heat transfer | kW | 22138.8848 | 22138.8848
89¦~24~3~8~~-38~ | Feedwater Heater [24] - HPH-3 : Shell pressure | bar | 16.049 | 16.049
89¦~24~3~9~~-38~ | Feedwater Heater [24] - HPH-3 : Saturation temperature | C | 201.5256 | 201.5256
89¦~24~3~13~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature at heater exit | C | 201.1456 | 201.1456
89¦~24~3~11~~-38~ | Feedwater Heater [24] - HPH-3 : Terminal difference | C | 0.38001 | 0.38001
89¦~24~3~12~~-38~ | Feedwater Heater [24] - HPH-3 : Drain cooler approach | C | 2.5 | 2.5
89¦~24~3~3~~-38~ | Feedwater Heater [24] - HPH-3 : UA of drain cooler section | kW/C | 431.6781 | 431.6781
89¦~24~3~1~~-38~ | Feedwater Heater [24] - HPH-3 : UA of condensing section | kW/C | 3955.1506 | 3955.1506
82¦71¦~53~5~1~~-38~ | Feedwater Heater [53] - LPH-8 : Mode |  | Design | Design
89¦~53~3~7~~-38~ | Feedwater Heater [53] - LPH-8 : Heat transfer | kW | 12019.5059 | 12019.5059
89¦~53~3~8~~-38~ | Feedwater Heater [53] - LPH-8 : Shell pressure | bar | 0.27745 | 0.27745
89¦~53~3~9~~-38~ | Feedwater Heater [53] - LPH-8 : Saturation temperature | C | 67.3104 | 67.3104
89¦~53~3~13~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature at heater exit | C | 61.7104 | 61.7104
89¦~53~3~11~~-38~ | Feedwater Heater [53] - LPH-8 : Terminal difference | C | 5.6 | 5.6
89¦~53~3~12~~-38~ | Feedwater Heater [53] - LPH-8 : Drain cooler approach | C | 2.8 | 2.8
89¦~53~3~3~~-38~ | Feedwater Heater [53] - LPH-8 : UA of drain cooler section | kW/C | 242.9729 | 242.9729
89¦~53~3~1~~-38~ | Feedwater Heater [53] - LPH-8 : UA of condensing section | kW/C | 915.1556 | 915.1556
82¦71¦~54~5~1~~-38~ | Feedwater Heater [54] - LPH-7 : Mode |  | Design | Design
89¦~54~3~7~~-38~ | Feedwater Heater [54] - LPH-7 : Heat transfer | kW | 17245.3281 | 17245.3281
89¦~54~3~8~~-38~ | Feedwater Heater [54] - LPH-7 : Shell pressure | bar | 0.70449 | 0.70449
89¦~54~3~9~~-38~ | Feedwater Heater [54] - LPH-7 : Saturation temperature | C | 90.1 | 90.1
89¦~54~3~13~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature at heater exit | C | 84.5 | 84.5
89¦~54~3~11~~-38~ | Feedwater Heater [54] - LPH-7 : Terminal difference | C | 5.6 | 5.6
89¦~54~3~12~~-38~ | Feedwater Heater [54] - LPH-7 : Drain cooler approach | C | 2.8 | 2.8
89¦~54~3~3~~-38~ | Feedwater Heater [54] - LPH-7 : UA of drain cooler section | kW/C | 225.9312 | 225.9312
89¦~54~3~1~~-38~ | Feedwater Heater [54] - LPH-7 : UA of condensing section | kW/C | 1142.2688 | 1142.2688
82¦71¦~55~5~1~~-38~ | Feedwater Heater [55] - LPH-6 : Mode |  | Design | Design
89¦~55~3~7~~-38~ | Feedwater Heater [55] - LPH-6 : Heat transfer | kW | 13742.8271 | 13742.8271
89¦~55~3~8~~-38~ | Feedwater Heater [55] - LPH-6 : Shell pressure | bar | 1.3529 | 1.3529
89¦~55~3~9~~-38~ | Feedwater Heater [55] - LPH-6 : Saturation temperature | C | 108.2815 | 108.2815
89¦~55~3~13~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature at heater exit | C | 102.5815 | 102.5815
89¦~55~3~11~~-38~ | Feedwater Heater [55] - LPH-6 : Terminal difference | C | 5.7 | 5.7
89¦~55~3~12~~-38~ | Feedwater Heater [55] - LPH-6 : Drain cooler approach | C | 2.8 | 2.8
89¦~55~3~3~~-38~ | Feedwater Heater [55] - LPH-6 : UA of drain cooler section | kW/C | 141.894 | 141.894
89¦~55~3~1~~-38~ | Feedwater Heater [55] - LPH-6 : UA of condensing section | kW/C | 1027.843 | 1027.843
82¦71¦~56~5~1~~-38~ | Feedwater Heater [56] - LPH-5 : Mode |  | Design | Design
89¦~56~3~7~~-38~ | Feedwater Heater [56] - LPH-5 : Heat transfer | kW | 24054.252 | 24054.252
89¦~56~3~8~~-38~ | Feedwater Heater [56] - LPH-5 : Shell pressure | bar | 3.5706 | 3.5706
89¦~56~3~9~~-38~ | Feedwater Heater [56] - LPH-5 : Saturation temperature | C | 139.5635 | 139.5635
89¦~56~3~13~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature at heater exit | C | 133.9635 | 133.9635
89¦~56~3~11~~-38~ | Feedwater Heater [56] - LPH-5 : Terminal difference | C | 5.6 | 5.6
89¦~56~3~12~~-38~ | Feedwater Heater [56] - LPH-5 : Drain cooler approach | C | 2.8 | 2.8
89¦~56~3~3~~-38~ | Feedwater Heater [56] - LPH-5 : UA of drain cooler section | kW/C | 108.5123 | 108.5123
89¦~56~3~1~~-38~ | Feedwater Heater [56] - LPH-5 : UA of condensing section | kW/C | 1408.4451 | 1408.4451
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0135 | 1.0135
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 30 | 30
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 17296.6777 | 17296.6777
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 140.758 | 140.758
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 675888.125 | 675888.125
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 736668.4375 | 736668.4375
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.362 | 2.362
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 5747.146 | 5747.146
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 17286.1191 | 17286.1191
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 18840.5996
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 17296.6777 | 17296.6777
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 18922.1328 | 18922.1328
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 48.63 | 48.63
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 3.99 | 3.99
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 13.04 | 13.04
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.8 | 0.8
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.19 | 0.19
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 5.36 | 5.36
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 27.99 | 27.99
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9862 | 6.9862
93¦~7~4~57~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total steam produced | t/h | 833.2999 | 833.2999
93¦~7~4~54~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam pressure | bar | 160.3127 | 160.3127
93¦~7~4~55~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam temperature | C | 347.5147 | 347.5147
93¦~7~4~56~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam enthalpy | kJ/kg | 2579.814 | 2579.814
93¦~7~4~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Adiabatic temperature | C | 1707.3843 | 1707.3843
93¦~7~4~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Effective radiating temperature | C | 1426.5481 | 1426.5481
93¦~7~4~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1141.2968 | 1141.2968
93¦~7~4~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Waterwall surface temperature | C | 1069.8296 | 1069.8296
93¦~7~4~19~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25
82¦71¦~7~6~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas N2 mol% | % | 69.3633 | 69.3633
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas O2 mol% | % | 3.7173 | 3.7173
93¦~7~4~104~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas CO2 mol% | % | 13.0047 | 13.0047
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas H2O mol% | % | 13.0614 | 13.0614
93¦~7~4~191~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas SO2 mol% | % | 0.019061 | 0.019061
82¦71¦~7~6~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas Ar mol% | % | 0.83426 | 0.83426
93¦~7~4~289~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total heat transfer to water/steam side | kW | 265453.7812 | 265453.7812
93¦~7~4~5~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat transfer to waterwall | kW | 265453.7812 | 265453.7812
82¦71¦~7~6~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon in ash | kW | 2244.3975 | 2244.3975
93¦~7~4~13~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat losses | kW | 8625.5967 | 8625.5967
93¦~7~4~109~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | kW | 2627.9812 | 2627.9812
93¦~7~4~321~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash (bed drain) sensible heat | kW | 544.2052 | 544.2052
93¦~7~4~322~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash sensible heat | kW | 2176.8208 | 2176.8208
93¦~7~4~43~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat absorption rate | kW/m^2 | 106.2999 | 106.2999
93¦~7~4~41~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat release rate | kW/m^2 | 295.5501 | 295.5501
93¦~7~4~42~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Volumetric fuel release rate | kW/m^3 | 102.5316 | 102.5316
93¦~7~4~305~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : SO2 removal efficiency | % | 0 | 0
93¦~7~4~302~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Sulfur removed | t/h | 0 | 0
93¦~7~4~301~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reagent consumption | t/h | 0 | 0
93¦~7~4~32~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas mass flux @ aperture | t/h-m^2 | 10.5159 | 10.5159
93¦~7~4~46~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas velocity leaving aperture @ exit temperature | m/s | 11.6879 | 11.6879
93¦~7~4~247~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gas mass flux | t/h-m^2 | 7.5499 | 7.5499
93¦~7~4~33~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace velocity @ effective radiating temperature | m/s | 10.0836 | 10.0836
93¦~7~4~339~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel mass flow | t/h | 140.758 | 140.758
82¦71¦~7~6~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel consumption per day | tonne/day | 3378.1902 | 3378.1902
93¦~7~4~17~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (LHV) | kW | 675888.125 | 675888.125
93¦~7~4~49~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (HHV) | kW | 736668.4375 | 736668.4375
93¦~7~4~28~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel delivery power | kW | 3971.3933 | 3971.3933
93¦~7~4~246~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Ash handling power | kW | 343.2241 | 343.2241
93¦~7~4~47~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Forced circulation pump power | kW | 472.4223 | 472.4223
93¦~7~4~16~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel ash flow | t/h | 7.5446 | 7.5446
93¦~7~4~24~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon flow | t/h | 0.23958 | 0.23958
93¦~7~4~312~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solids added to ash due to reagent addition | t/h | 0 | 0
93¦~7~4~326~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inert bed material feed | t/h | 0 | 0
93¦~7~4~327~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solid produced from combustion | t/h | 7.7842 | 7.7842
93¦~7~4~314~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash flow | t/h | 1.5568 | 1.5568
93¦~7~4~317~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash flow | t/h | 6.2274 | 6.2274
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content | % | 5.3 | 5.3
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas O2 content | % | 3.7173 | 3.7173
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas H2O content | % | 13.0614 | 13.0614
93¦~7~4~431~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
76¦~7~2~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of existing pulverizers |  | 6 | 6
76¦~7~2~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of operating pulverizers |  | 5 | 5
91¦~7~1~92~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow | t/h | 140.758 | 140.758
93¦~7~3~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow (each) | t/h | 28.1516 | 28.1516
91¦~7~1~80~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel temperature | C | 30 | 30
91¦~7~1~89~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel moisture percent | % | 27.99 | 27.99
93¦~7~3~20~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel flow (each) | t/h | 23.4238 | 23.4238
93¦~7~3~19~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel moisture percent | % | 13.4558 | 13.4558
93¦~7~3~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet temperature | C | 60.8 | 60.8
93¦~7~3~33~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total moisture evaporated | t/h | 23.6389 | 23.6389
93¦~7~3~34~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percent of moisture evaporated | % | 60 | 60
82¦71¦~7~10~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow | t/h | 201.5084 | 201.5084
82¦71¦~7~10~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow (each) | t/h | 40.3017 | 40.3017
91¦~7~1~41~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet temperature | C | 326.0734 | 326.0734
82¦71¦~7~10~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow | t/h | 51.856 | 51.856
82¦71¦~7~10~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow (each) | t/h | 10.3712 | 10.3712
91¦~7~1~51~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air temperature | C | 27.2082 | 27.2082
82¦71¦~7~10~3~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow | t/h | 253.3644 | 253.3644
82¦71¦~7~10~13~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow (each) | t/h | 50.6729 | 50.6729
91¦~7~1~61~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air temperature | C | 266.1161 | 266.1161
91¦~7~1~60~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air pressure | bar | 1.1254 | 1.1254
93¦~7~3~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percentage of tempering air over total drying air | % | 20.467 | 20.467
93¦~7~3~35~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet air/fuel mass ratio |  | 1.8 | 1.8
82¦71¦~7~10~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow | t/h | 277.0033 | 277.0033
82¦71¦~7~10~14~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow (each) | t/h | 55.4007 | 55.4007
93¦~7~3~37~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas dew point | C | 55.521 | 55.521
93¦~7~3~38~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas relative humidity | % | 78.077 | 78.077
93¦~7~3~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer power (each) | kW | 782.1964 | 782.1964
82¦71¦~7~10~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exhaust fan power (each) | kW | 12.0823 | 12.0823
93¦~7~3~30~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total power consumption | kW | 3971.3933 | 3971.3933
93¦~3~3~1~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332
93¦~3~3~2~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85
93¦~3~3~3~~-1~ | Gas/Air Source [3] - Sec.Air : Enthalpy | kJ/kg | 0.86557 | 0.86557
93¦~3~3~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 973.2435 | 973.2435
93¦~3~3~5~~-1~ | Gas/Air Source [3] - Sec.Air : Molecular weight |  | 28.7578 | 28.7578
93¦~3~3~11~~-1~ | Gas/Air Source [3] - Sec.Air : N2 mole percent | % | 76.5891 | 76.5891
93¦~3~3~12~~-1~ | Gas/Air Source [3] - Sec.Air : O2 mole percent | % | 20.5495 | 20.5495
93¦~3~3~13~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mole percent | % | 0.029724 | 0.029724
93¦~3~3~14~~-1~ | Gas/Air Source [3] - Sec.Air : H2O mole percent | % | 1.9093 | 1.9093
93¦~3~3~15~~-1~ | Gas/Air Source [3] - Sec.Air : SO2 mole percent | % | 0 | 0
93¦~3~3~16~~-1~ | Gas/Air Source [3] - Sec.Air : Ar mole percent | % | 0.92239 | 0.92239
93¦~3~3~20~~-1~ | Gas/Air Source [3] - Sec.Air : Liquid H2O mole percent | % | 0 | 0
93¦~3~3~21~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mass flow | t/h | 0.44272 | 0.44272
93¦~11~3~1~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129
93¦~11~3~2~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85
93¦~11~3~3~~-1~ | Gas/Air Source [11] - Prim.Air : Enthalpy | kJ/kg | 0.86495 | 0.86495
93¦~11~3~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 283.799 | 283.799
93¦~11~3~5~~-1~ | Gas/Air Source [11] - Prim.Air : Molecular weight |  | 28.7728 | 28.7728
93¦~11~3~11~~-1~ | Gas/Air Source [11] - Prim.Air : N2 mole percent | % | 76.6959 | 76.6959
93¦~11~3~12~~-1~ | Gas/Air Source [11] - Prim.Air : O2 mole percent | % | 20.5782 | 20.5782
93¦~11~3~13~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mole percent | % | 0.029766 | 0.029766
93¦~11~3~14~~-1~ | Gas/Air Source [11] - Prim.Air : H2O mole percent | % | 1.7725 | 1.7725
93¦~11~3~15~~-1~ | Gas/Air Source [11] - Prim.Air : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - Prim.Air : Ar mole percent | % | 0.92367 | 0.92367
93¦~11~3~20~~-1~ | Gas/Air Source [11] - Prim.Air : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mass flow | t/h | 0.12921 | 0.12921
82¦71¦~40~10~3~~-168~ | General Pump [40] - CP : Mode |  | TD | TD
82¦71¦~40~10~7~~-168~ | General Pump [40] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~40~10~6~~-168~ | General Pump [40] - CP : Pump head | m | 113.0849 | 113.0849
83¦93¦~40~3~15~~-168~ | General Pump [40] - CP : Pressure rise before control valve | bar | 10.9802 | 10.9802
83¦93¦~40~3~18~~-168~ | General Pump [40] - CP : Pressure rise after valve pressure drop | bar | 10.9802 | 10.9802
83¦93¦~40~3~16~~-168~ | General Pump [40] - CP : Pressure drop across valve | bar | 2.6301e-07 | 2.6301e-07
83¦93¦~40~3~12~~-168~ | General Pump [40] - CP : Apparent isentropic efficiency | % | 74.9998 | 74.9998
83¦93¦~40~3~13~~-168~ | General Pump [40] - CP : Shaft work per station | kW | 275.44 | 275.44
82¦71¦~40~10~1~~-168~ | General Pump [40] - CP : Hydraulic work per station | kW | 267.1768 | 267.1768
82¦71¦~40~10~2~~-168~ | General Pump [40] - CP : Electricity consumption per station | kW | 288.0398 | 288.0398
83¦93¦~40~3~5~~-168~ | General Pump [40] - CP : Suction flow | t/h | 650.5074 | 650.5074
83¦93¦~40~3~27~~-168~ | General Pump [40] - CP : Suction pressure | bar | 0.45641 | 0.45641
83¦93¦~40~3~28~~-168~ | General Pump [40] - CP : Suction temperature | C | 45.247 | 45.247
83¦93¦~40~3~4~~-168~ | General Pump [40] - CP : Suction enthalpy | kJ/kg | 189.4476 | 189.4476
83¦93¦~40~3~8~~-168~ | General Pump [40] - CP : Discharge flow | t/h | 650.5074 | 650.5074
83¦93¦~40~3~29~~-168~ | General Pump [40] - CP : Discharge pressure | bar | 11.4366 | 11.4366
83¦93¦~40~3~6~~-168~ | General Pump [40] - CP : Discharge temperature | C | 45.3698 | 45.3698
83¦93¦~40~3~7~~-168~ | General Pump [40] - CP : Discharge enthalpy | kJ/kg | 190.9262 | 190.9262
82¦71¦~40~6~1~1000~-168~ | General Pump [40] - CP : Motor: Mode |  | Design | Design
91¦~40~1~7~1000~-168~ | General Pump [40] - CP : Motor: Nameplate power | kW | 294.1529 | 294.1529
91¦~40~1~19~1000~-168~ | General Pump [40] - CP : Motor: Nameplate efficiency | % | 95.6349 | 95.6349
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate / Design point load |  | 1.0212 | 1.0212
76¦~40~2~8~1000~-168~ | General Pump [40] - CP : Motor: Number of operating units |  | 1 | 1
93¦~40~7~2~1000~-168~ | General Pump [40] - CP : Motor: Electricity consumption | kW | 288.0398 | 288.0398
93¦~40~7~6~1000~-168~ | General Pump [40] - CP : Motor: Shaft power | kW | 275.44 | 275.44
93¦~40~7~4~1000~-168~ | General Pump [40] - CP : Motor: Efficiency | % | 95.6257 | 95.6257
93¦~40~7~3~1000~-168~ | General Pump [40] - CP : Motor: Electrical loss | kW | 12.5998 | 12.5998
89¦~40~3~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate motor shaft power | kW | 281.2857 | 281.2857
93¦~6~3~1~~-46~ | Makeup / Blowdown [6] : Makeup flow | t/h | 2.2897 | 2.2897
93¦~6~3~3~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25
93¦~6~3~2~~-46~ | Makeup / Blowdown [6] : Makeup enthalpy | kJ/kg | 104.9292 | 104.9292
93¦~6~3~4~~-46~ | Makeup / Blowdown [6] : Blowdown flow | t/h | 0 | 0
93¦~6~3~6~~-46~ | Makeup / Blowdown [6] : Blowdown temperature | C | 45.3184 | 45.3184
93¦~6~3~5~~-46~ | Makeup / Blowdown [6] : Blowdown enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~11~~-46~ | Makeup / Blowdown [6] : Inlet pressure | bar | 0.45641 | 0.45641
93¦~6~3~12~~-46~ | Makeup / Blowdown [6] : Inlet flow | t/h | 648.2178 | 648.2178
93¦~6~3~14~~-46~ | Makeup / Blowdown [6] : Inlet temperature | C | 45.3184 | 45.3184
93¦~6~3~13~~-46~ | Makeup / Blowdown [6] : Inlet enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~22~~-46~ | Makeup / Blowdown [6] : Outlet flow | t/h | 650.5074 | 650.5074
93¦~6~3~24~~-46~ | Makeup / Blowdown [6] : Outlet temperature | C | 45.247 | 45.247
93¦~6~3~23~~-46~ | Makeup / Blowdown [6] : Outlet enthalpy | kJ/kg | 189.4476 | 189.4476
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~21~3~1~~-6~ | Mixer [21] : Actual mass flow fraction of 1st clockwise inlet |  | 4.1217e-10 | 4.1217e-10
93¦~21~3~3~~-6~ | Mixer [21] : Actual mass flow fraction of 3rd clockwise inlet |  | 1 | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01
93¦~25~3~1~~-6~ | Mixer [25] : Actual mass flow fraction of 1st clockwise inlet |  | 1 | 1
93¦~25~3~3~~-6~ | Mixer [25] : Actual mass flow fraction of 3rd clockwise inlet |  | 4.1657e-10 | 4.1657e-10
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7
93¦~30~3~1~~-6~ | Mixer [30] : Actual mass flow fraction of 1st clockwise inlet |  | 0.3 | 0.3
93¦~30~3~3~~-6~ | Mixer [30] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.7 | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011
93¦~33~3~1~~-6~ | Mixer [33] : Actual mass flow fraction of 1st clockwise inlet |  | 0.10989 | 0.10989
93¦~33~3~2~~-6~ | Mixer [33] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.89011 | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~39~3~2~~-6~ | Mixer [39] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99568 | 0.99568
93¦~39~3~3~~-6~ | Mixer [39] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.0043192 | 0.0043192
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.94647 | 0.94647
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.0012907 | 0.0012907
93¦~62~3~3~~-6~ | Mixer [62] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.052237 | 0.052237
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~85~3~1~~-6~ | Mixer [85] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~85~3~3~~-6~ | Mixer [85] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.50115 | 0.50115
93¦~87~3~3~~-6~ | Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.49885 | 0.49885
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~90~3~1~~-6~ | Mixer [90] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~90~3~3~~-6~ | Mixer [90] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
~35~6~5~~-107~ | Pipe (PCE) [35] : Mode |  | TD | TD
~35~6~1~~-107~ | Pipe (PCE) [35] : Pressure drop from inlet to exit | bar | 1.0995 | 1.0995
~35~6~2~~-107~ | Pipe (PCE) [35] : Pressure drop as percent of exit pressure | % | 2 | 2
~35~6~4~~-107~ | Pipe (PCE) [35] : Heat loss | kW | 15.5942 | 15.5942
~36~6~5~~-107~ | Pipe (PCE) [36] : Mode |  | TD | TD
~36~6~1~~-107~ | Pipe (PCE) [36] : Pressure drop from inlet to exit | bar | 0.65853 | 0.65853
~36~6~2~~-107~ | Pipe (PCE) [36] : Pressure drop as percent of exit pressure | % | 2 | 2
~36~6~4~~-107~ | Pipe (PCE) [36] : Heat loss | kW | 17.053 | 17.053
~37~6~5~~-107~ | Pipe (PCE) [37] : Mode |  | TD | TD
~37~6~1~~-107~ | Pipe (PCE) [37] : Pressure drop from inlet to exit | bar | 0.32098 | 0.32098
~37~6~2~~-107~ | Pipe (PCE) [37] : Pressure drop as percent of exit pressure | % | 2 | 2
~37~6~4~~-107~ | Pipe (PCE) [37] : Heat loss | kW | 7.0439 | 7.0439
~60~6~5~~-107~ | Pipe (PCE) [60] : Mode |  | TD | TD
~60~6~1~~-107~ | Pipe (PCE) [60] : Pressure drop from inlet to exit | bar | 0.071412 | 0.071412
~60~6~2~~-107~ | Pipe (PCE) [60] : Pressure drop as percent of exit pressure | % | 2 | 2
~60~6~4~~-107~ | Pipe (PCE) [60] : Heat loss | kW | 9.5511 | 9.5511
~61~6~5~~-107~ | Pipe (PCE) [61] : Mode |  | TD | TD
~61~6~1~~-107~ | Pipe (PCE) [61] : Pressure drop from inlet to exit | bar | 0.027059 | 0.027059
~61~6~2~~-107~ | Pipe (PCE) [61] : Pressure drop as percent of exit pressure | % | 2 | 2
~61~6~4~~-107~ | Pipe (PCE) [61] : Heat loss | kW | 5.4124 | 5.4124
~63~6~5~~-107~ | Pipe (PCE) [63] : Mode |  | TD | TD
~63~6~1~~-107~ | Pipe (PCE) [63] : Pressure drop from inlet to exit | bar | 0.015294 | 0.015294
~63~6~2~~-107~ | Pipe (PCE) [63] : Pressure drop as percent of exit pressure | % | 2 | 2
~63~6~4~~-107~ | Pipe (PCE) [63] : Heat loss | kW | 6.5751 | 6.5751
~64~6~5~~-107~ | Pipe (PCE) [64] : Mode |  | TD | TD
~64~6~1~~-107~ | Pipe (PCE) [64] : Pressure drop from inlet to exit | bar | 0.005549 | 0.005549
~64~6~2~~-107~ | Pipe (PCE) [64] : Pressure drop as percent of exit pressure | % | 2 | 2
~64~6~4~~-107~ | Pipe (PCE) [64] : Heat loss | kW | 4.5538 | 4.5538
~73~6~5~~-107~ | Pipe (PCE) [73] : Mode |  | TD | TD
~73~6~1~~-107~ | Pipe (PCE) [73] : Pressure drop from inlet to exit | bar | 0.18129 | 0.18129
~73~6~2~~-107~ | Pipe (PCE) [73] : Pressure drop as percent of exit pressure | % | 2 | 2
~73~6~4~~-107~ | Pipe (PCE) [73] : Heat loss | kW | 12.9948 | 12.9948
~74~6~5~~-107~ | Pipe (PCE) [74] : Mode |  | TD | TD
~74~6~1~~-107~ | Pipe (PCE) [74] : Pressure drop from inlet to exit | bar | 1.5253 | 1.5253
~74~6~2~~-107~ | Pipe (PCE) [74] : Pressure drop as percent of exit pressure | % | 1 | 1
~74~6~4~~-107~ | Pipe (PCE) [74] : Heat loss | kW | 395.7661 | 395.7661
~75~6~5~~-107~ | Pipe (PCE) [75] : Mode |  | TD | TD
~75~6~1~~-107~ | Pipe (PCE) [75] : Pressure drop from inlet to exit | bar | 0.306 | 0.306
~75~6~2~~-107~ | Pipe (PCE) [75] : Pressure drop as percent of exit pressure | % | 1 | 1
~75~6~4~~-107~ | Pipe (PCE) [75] : Heat loss | kW | 337.1081 | 337.1081
~76~6~5~~-107~ | Pipe (PCE) [76] : Mode |  | TD | TD
~76~6~1~~-107~ | Pipe (PCE) [76] : Pressure drop from inlet to exit | bar | 1.6191 | 1.6191
~76~6~2~~-107~ | Pipe (PCE) [76] : Pressure drop as percent of exit pressure | % | 0.99999 | 0.99999
~76~6~4~~-107~ | Pipe (PCE) [76] : Heat loss | kW | 232.061 | 232.061
82¦71¦~82~10~3~~-100~ | Pump (PCE) [82] - CWP-1 : Mode |  | TD | TD
82¦71¦~82~10~7~~-100~ | Pump (PCE) [82] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~82~10~6~~-100~ | Pump (PCE) [82] - CWP-1 : Pump head | m | 28.9733 | 28.9733
83¦93¦~82~3~15~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~82~3~18~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~82~3~16~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~82~3~12~~-100~ | Pump (PCE) [82] - CWP-1 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~82~3~13~~-100~ | Pump (PCE) [82] - CWP-1 : Shaft work per station | kW | 1606.9744 | 1606.9744
82¦71¦~82~10~1~~-100~ | Pump (PCE) [82] - CWP-1 : Hydraulic work per station | kW | 1558.7653 | 1558.7653
82¦71¦~82~10~2~~-100~ | Pump (PCE) [82] - CWP-1 : Electricity consumption per station | kW | 1661.4205 | 1661.4205
83¦93¦~82~3~5~~-100~ | Pump (PCE) [82] - CWP-1 : Suction flow | t/h | 14812.7949 | 14812.7949
83¦93¦~82~3~27~~-100~ | Pump (PCE) [82] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~82~3~28~~-100~ | Pump (PCE) [82] - CWP-1 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~82~3~4~~-100~ | Pump (PCE) [82] - CWP-1 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~82~3~8~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge flow | t/h | 14812.7949 | 14812.7949
83¦93¦~82~3~29~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~82~3~6~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~82~3~7~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~82~6~1~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Mode |  | Design | Design
91¦~82~1~7~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate power | kW | 1719.4677 | 1719.4677
91¦~82~1~19~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate efficiency | % | 96.7343 | 96.7343
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~82~2~8~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~82~7~2~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electricity consumption | kW | 1661.4205 | 1661.4205
93¦~82~7~6~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Shaft power | kW | 1606.9744 | 1606.9744
93¦~82~7~4~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Efficiency | % | 96.7229 | 96.7229
93¦~82~7~3~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electrical loss | kW | 54.4462 | 54.4462
89¦~82~3~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate motor shaft power | kW | 1663.1193 | 1663.1193
82¦71¦~83~10~3~~-100~ | Pump (PCE) [83] - CWP-2 : Mode |  | TD | TD
82¦71¦~83~10~7~~-100~ | Pump (PCE) [83] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~83~10~6~~-100~ | Pump (PCE) [83] - CWP-2 : Pump head | m | 28.9733 | 28.9733
83¦93¦~83~3~15~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~83~3~18~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~83~3~16~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~83~3~12~~-100~ | Pump (PCE) [83] - CWP-2 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~83~3~13~~-100~ | Pump (PCE) [83] - CWP-2 : Shaft work per station | kW | 1606.9744 | 1606.9744
82¦71¦~83~10~1~~-100~ | Pump (PCE) [83] - CWP-2 : Hydraulic work per station | kW | 1558.7653 | 1558.7653
82¦71¦~83~10~2~~-100~ | Pump (PCE) [83] - CWP-2 : Electricity consumption per station | kW | 1661.4205 | 1661.4205
83¦93¦~83~3~5~~-100~ | Pump (PCE) [83] - CWP-2 : Suction flow | t/h | 14812.7949 | 14812.7949
83¦93¦~83~3~27~~-100~ | Pump (PCE) [83] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~83~3~28~~-100~ | Pump (PCE) [83] - CWP-2 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~83~3~4~~-100~ | Pump (PCE) [83] - CWP-2 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~83~3~8~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge flow | t/h | 14812.7949 | 14812.7949
83¦93¦~83~3~29~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~83~3~6~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~83~3~7~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~83~6~1~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Mode |  | Design | Design
91¦~83~1~7~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate power | kW | 1719.4677 | 1719.4677
91¦~83~1~19~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate efficiency | % | 96.7343 | 96.7343
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~83~2~8~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~83~7~2~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electricity consumption | kW | 1661.4205 | 1661.4205
93¦~83~7~6~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Shaft power | kW | 1606.9744 | 1606.9744
93¦~83~7~4~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Efficiency | % | 96.7229 | 96.7229
93¦~83~7~3~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electrical loss | kW | 54.4462 | 54.4462
89¦~83~3~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate motor shaft power | kW | 1663.1193 | 1663.1193
93¦~8~3~64~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air path heat transfer | kW | 18168.4355 | 18168.4355
93¦~8~3~44~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Secondary air path heat transfer | kW | 64610.0703 | 64610.0703
82¦71¦~8~5~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Total heat transfer | kW | 82778.5 | 82778.5
93¦~8~3~69~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Heat transfer duty ratio (Qpa / Qsa) | % | 28.1201 | 28.1201
93¦~8~3~24~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Average cold end temperature (ACET) | C | 89.7083 | 89.7083
93¦~8~3~191~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O dew point temperature | C | 49.3431 | 49.3431
93¦~8~3~138~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit sulfur dew point temperature | C | -273.15 | -273.15
93¦~8~3~139~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas sulfur dew point temperature within air heater | C | -273.15 | -273.15
93¦~8~3~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit O2 mol% | % | 5.1684 | 5.1684
93¦~8~3~12~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit CO2 mol% | % | 11.8865 | 11.8865
93¦~8~3~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O mol% | % | 12.0974 | 12.0974
82¦71¦~8~5~2~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit N2 mol% | % | 69.9883 | 69.9883
93¦~8~3~132~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit Ar mol% | % | 0.84189 | 0.84189
93¦~8~3~131~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit SO2 mol% | % | 0.017419 | 0.017419
82¦71¦~1~5~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~1~5~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~1~1~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of existing units |  | 1 | 1
93¦~1~3~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1
93¦~1~3~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Total shaft power | kW | 2964.9277 | 2964.9277
93¦~1~3~1~~-85~ | ST-Driven Pump [1] - BFPT-A : Shaft power per unit | kW | 2964.9277 | 2964.9277
93¦~1~3~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping power per unit | kW | 2872.1479 | 2872.1479
93¦~1~3~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping flow per unit | t/h | 420.0911 | 420.0911
93¦~1~3~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump pressure rise (before control valve) | bar | 163.4004 | 163.4004
93¦~1~3~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall pressure rise | bar | 163.4004 | 163.4004
93¦~1~3~6~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~1~3~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall apparent isentropic efficiency | % | 74.45 | 74.45
93¦~1~3~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600 | 3600
93¦~1~3~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss per unit | kW | 92.7797 | 92.7797
93¦~1~3~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~1~10~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Type of inlet control |  | Sliding | Sliding
93¦~1~3~29~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Steam supply pressure | bar | 9.246 | 9.246
93¦~1~3~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet pressure | bar | 8.98 | 8.98
93¦~1~3~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet temperature | C | 360.8472 | 360.8472
93¦~1~3~14~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet flow per unit | t/h | 14.4996 | 14.4996
93¦~1~3~13~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~1~3~16~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion massflow per unit | t/h | 14.4996 | 14.4996
93¦~1~3~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial pressure | bar | 8.98 | 8.98
93¦~1~3~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~1~3~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~1~3~25~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2444.6487 | 2444.6487
93¦~1~3~21~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~1~3~22~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~1~3~24~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet flow per unit | t/h | 14.4996 | 14.4996
93¦~1~3~23~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet enthalpy | kJ/kg | 2444.6487 | 2444.6487
72¦79¦93¦~1~7~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust volume flow per unit | m^3/s | 57.0121 | 57.0121
72¦79¦93¦~1~7~18~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~1~7~17~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~1~3~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual flow function | m^2 | 0.0036051 | 0.0036051
93¦~1~3~10~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual pressure ratio (blading) |  | 92.1026 | 92.1026
93¦~1~3~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry step efficiency | % | 85 | 85
93¦~1~3~1~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group overall efficiency | % | 87.4437 | 87.4437
93¦~1~3~30~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group blading efficiency | % | 87.4437 | 87.4437
93¦~1~3~50~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion power per unit | kW | 2972.3591 | 2972.3591
93¦~1~3~9~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical loss per unit | kW | 7.4309 | 7.4309
82¦71¦~86~5~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~86~5~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~86~1~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of existing units |  | 1 | 1
93¦~86~3~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1
93¦~86~3~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Total shaft power | kW | 2964.9277 | 2964.9277
93¦~86~3~1~~-85~ | ST-Driven Pump [86] - BFPT-B : Shaft power per unit | kW | 2964.9277 | 2964.9277
93¦~86~3~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping power per unit | kW | 2872.1479 | 2872.1479
93¦~86~3~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping flow per unit | t/h | 420.0911 | 420.0911
93¦~86~3~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump pressure rise (before control valve) | bar | 163.4004 | 163.4004
93¦~86~3~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall pressure rise | bar | 163.4004 | 163.4004
93¦~86~3~6~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~86~3~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall apparent isentropic efficiency | % | 74.45 | 74.45
93¦~86~3~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000 | 3000
93¦~86~3~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss per unit | kW | 92.7797 | 92.7797
93¦~86~3~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~86~10~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Type of inlet control |  | Sliding | Sliding
93¦~86~3~29~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Steam supply pressure | bar | 9.246 | 9.246
93¦~86~3~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet pressure | bar | 9.246 | 9.246
93¦~86~3~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet temperature | C | 360.8472 | 360.8472
93¦~86~3~14~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet flow per unit | t/h | 14.4332 | 14.4332
93¦~86~3~13~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~86~3~16~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion massflow per unit | t/h | 14.4332 | 14.4332
93¦~86~3~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial pressure | bar | 9.246 | 9.246
93¦~86~3~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~86~3~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~86~3~25~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2441.2544 | 2441.2544
93¦~86~3~21~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~86~3~22~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~86~3~24~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet flow per unit | t/h | 14.4332 | 14.4332
93¦~86~3~23~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet enthalpy | kJ/kg | 2441.2544 | 2441.2544
72¦79¦93¦~86~7~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust volume flow per unit | m^3/s | 56.6656 | 56.6656
72¦79¦93¦~86~7~18~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~86~7~17~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~86~3~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual flow function | m^2 | 0.0034853 | 0.0034853
93¦~86~3~10~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual pressure ratio (blading) |  | 94.8308 | 94.8308
93¦~86~3~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry step efficiency | % | 85 | 85
93¦~86~3~1~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group overall efficiency | % | 87.4082 | 87.4082
93¦~86~3~30~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group blading efficiency | % | 87.4082 | 87.4082
93¦~86~3~50~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion power per unit | kW | 2972.3591 | 2972.3591
93¦~86~3~9~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical loss per unit | kW | 7.4309 | 7.4309
91¦~34~1~13~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~34~1~71~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~34~3~7~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer | kW | 317.8068 | 317.8068
91¦~34~1~101~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Feedwater temperature rise (overall) | C | 0.42822 | 0.42822
82¦71¦~34~5~2~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Terminal difference | C | 11.4027 | 11.4027
91¦~34~1~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer area | m^2 | 65.2424 | 65.2424
91¦~34~1~82~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~34~3~52~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell length | m | 0 | 0
89¦~34~3~53~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell inner diameter | m | 1.1308 | 1.1308
89¦~34~3~56~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall length | m | 0 | 0
89¦~34~3~27~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall outer diameter | m | 0 | 0
89¦~34~3~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total dry weight | kg | 0 | 0
89¦~34~3~57~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~34~5~5~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total estimated installed cost | USD | 0 | 0
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~4~3~1~~-7~ | Splitter [4] : Actual flow fraction of 1st clockwise outlet |  | 0.96966 | 0.96966
93¦~4~3~3~~-7~ | Splitter [4] : Actual flow fraction of 3rd clockwise outlet |  | 0.03034 | 0.03034
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~9~3~1~~-7~ | Splitter [9] : Actual flow fraction of 1st clockwise outlet |  | 0.81652 | 0.81652
93¦~9~3~3~~-7~ | Splitter [9] : Actual flow fraction of 3rd clockwise outlet |  | 0.18348 | 0.18348
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998
93¦~18~3~1~~-7~ | Splitter [18] : Actual flow fraction of 1st clockwise outlet |  | 3.5105e-10 | 3.5105e-10
93¦~18~3~2~~-7~ | Splitter [18] : Actual flow fraction of 2nd clockwise outlet |  | 3.5105e-10 | 3.5105e-10
93¦~18~3~3~~-7~ | Splitter [18] : Actual flow fraction of 3rd clockwise outlet |  | 1 | 1
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~19~3~1~~-7~ | Splitter [19] : Actual flow fraction of 1st clockwise outlet |  | 0.93297 | 0.93297
93¦~19~3~3~~-7~ | Splitter [19] : Actual flow fraction of 3rd clockwise outlet |  | 0.067029 | 0.067029
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005
93¦~20~3~1~~-7~ | Splitter [20] : Actual flow fraction of 1st clockwise outlet |  | 0.91485 | 0.91485
93¦~20~3~2~~-7~ | Splitter [20] : Actual flow fraction of 2nd clockwise outlet |  | 0.078566 | 0.078566
93¦~20~3~3~~-7~ | Splitter [20] : Actual flow fraction of 3rd clockwise outlet |  | 0.006579 | 0.006579
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843
93¦~22~3~1~~-7~ | Splitter [22] : Actual flow fraction of 1st clockwise outlet |  | 0.001 | 0.001
93¦~22~3~2~~-7~ | Splitter [22] : Actual flow fraction of 2nd clockwise outlet |  | 0.00057 | 0.00057
93¦~22~3~3~~-7~ | Splitter [22] : Actual flow fraction of 3rd clockwise outlet |  | 0.99843 | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~27~3~1~~-7~ | Splitter [27] : Actual flow fraction of 1st clockwise outlet |  | 0.98934 | 0.98934
93¦~27~3~3~~-7~ | Splitter [27] : Actual flow fraction of 3rd clockwise outlet |  | 0.010658 | 0.010658
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.97486 | 0.97486
93¦~29~3~3~~-7~ | Splitter [29] : Actual flow fraction of 3rd clockwise outlet |  | 0.025136 | 0.025136
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578
93¦~32~3~1~~-7~ | Splitter [32] : Actual flow fraction of 1st clockwise outlet |  | 0.042025 | 0.042025
93¦~32~3~2~~-7~ | Splitter [32] : Actual flow fraction of 2nd clockwise outlet |  | 0.89749 | 0.89749
93¦~32~3~3~~-7~ | Splitter [32] : Actual flow fraction of 3rd clockwise outlet |  | 0.060485 | 0.060485
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.94435 | 0.94435
93¦~49~3~3~~-7~ | Splitter [49] : Actual flow fraction of 3rd clockwise outlet |  | 0.055649 | 0.055649
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~50~3~1~~-7~ | Splitter [50] : Actual flow fraction of 1st clockwise outlet |  | 0.96661 | 0.96661
93¦~50~3~3~~-7~ | Splitter [50] : Actual flow fraction of 3rd clockwise outlet |  | 0.033393 | 0.033393
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~51~3~1~~-7~ | Splitter [51] : Actual flow fraction of 1st clockwise outlet |  | 0.95803 | 0.95803
93¦~51~3~3~~-7~ | Splitter [51] : Actual flow fraction of 3rd clockwise outlet |  | 0.041969 | 0.041969
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~70~3~1~~-7~ | Splitter [70] : Actual flow fraction of 1st clockwise outlet |  | 0.39171 | 0.39171
93¦~70~3~3~~-7~ | Splitter [70] : Actual flow fraction of 3rd clockwise outlet |  | 0.60829 | 0.60829
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~71~3~1~~-7~ | Splitter [71] : Actual flow fraction of 1st clockwise outlet |  | 7.9919e-05 | 7.9919e-05
93¦~71~3~2~~-7~ | Splitter [71] : Actual flow fraction of 2nd clockwise outlet |  | 0.0056319 | 0.0056319
93¦~71~3~3~~-7~ | Splitter [71] : Actual flow fraction of 3rd clockwise outlet |  | 0.99429 | 0.99429
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~84~3~1~~-7~ | Splitter [84] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~84~3~3~~-7~ | Splitter [84] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~88~3~1~~-7~ | Splitter [88] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~88~3~3~~-7~ | Splitter [88] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~89~3~1~~-7~ | Splitter [89] : Actual flow fraction of 1st clockwise outlet |  | 0.50115 | 0.50115
93¦~89~3~3~~-7~ | Splitter [89] : Actual flow fraction of 3rd clockwise outlet |  | 0.49885 | 0.49885
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 150.4492 | 150.4492
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 49.8568 | 49.8568
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 143.5047 | 143.5047
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 6012.9233 | 6012.9233
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 5.1684 | 5.1684
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 11.8866 | 11.8866
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 12.0974 | 12.0974
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 69.9883 | 69.9883
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.84189 | 0.84189
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.017419 | 0.017419
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 201.5122 | 201.5122
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 561.7834 | 561.7834
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 196.554 | 196.554
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.023781 | 0.023781
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 8.9674 | 8.9674
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9998 | 24.9998
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 5.1684 | 5.1684
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 12.0974 | 12.0974
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~23~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Mode |  | TD | TD
~23~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet mass flow | t/h | 836.1783 | 836.1783
~23~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet pressure | bar | 158.7254 | 158.7254
~23~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet enthalpy | kJ/kg | 3026.0681 | 3026.0681
~23~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet temperature | C | 418.0031 | 418.0031
~23~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit mass flow | t/h | 836.1783 | 836.1783
~23~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit pressure | bar | 157.1539 | 157.1539
~23~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit temperature | C | 490 | 490
~23~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit enthalpy | kJ/kg | 3271.4119 | 3271.4119
~23~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas mass flow | t/h | 1271.106 | 1271.106
~23~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Flyash mass flow | t/h | 6.2274 | 6.2274
~23~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas inlet temperature | C | 1141.3999 | 1141.3999
~23~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas exit temperature | C | 1025.738 | 1025.738
~23~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat transfer to steam | kW | 56987.3281 | 56987.3281
~23~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss | kW | 427.405 | 427.405
~23~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Radiant heat influx | kW | 2627.5137 | 2627.5137
~23~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~23~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam side pressure drop | bar | 1.5715 | 1.5715
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 838.0318 | 838.0318
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 155.5979 | 155.5979
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3346.7295 | 3346.7295
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 514.9985 | 514.9985
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 838.0318 | 838.0318
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 154.0573 | 154.0573
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 534.4 | 534.4
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3403.2319 | 3403.2319
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 1271.106 | 1271.106
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 6.2274 | 6.2274
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 775.0101 | 775.0101
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 745.5891 | 745.5891
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 13153.208 | 13153.208
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 98.6491 | 98.6491
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 1.5406 | 1.5406
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 833.2999 | 833.2999
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 160.3127 | 160.3127
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2579.814 | 2579.814
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 347.521 | 347.521
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 833.2999 | 833.2999
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 158.7254 | 158.7254
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 420 | 420
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3033.8652 | 3033.8652
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 1271.106 | 1271.106
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 6.2274 | 6.2274
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 745.5911 | 745.5911
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 503.6178 | 503.6178
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 105101.8828 | 105101.8828
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 788.2642 | 788.2642
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 1.5873 | 1.5873
~77~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Mode |  | TD | TD
~77~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet mass flow | t/h | 713.8239 | 713.8239
~77~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet pressure | bar | 33.585 | 33.585
~77~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet enthalpy | kJ/kg | 3046.9353 | 3046.9353
~77~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet temperature | C | 324.9983 | 324.9983
~77~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit mass flow | t/h | 713.8239 | 713.8239
~77~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit pressure | bar | 33.2525 | 33.2525
~77~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit temperature | C | 511 | 511
~77~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit enthalpy | kJ/kg | 3478.2825 | 3478.2825
~77~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas mass flow | t/h | 1271.106 | 1271.106
~77~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Flyash mass flow | t/h | 6.2274 | 6.2274
~77~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas inlet temperature | C | 985.27 | 985.27
~77~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas exit temperature | C | 798.2156 | 798.2156
~77~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat transfer to steam | kW | 85530.7578 | 85530.7578
~77~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss | kW | 641.4807 | 641.4807
~77~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Radiant heat influx | kW | 0 | 0
~77~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~77~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam side pressure drop | bar | 0.33252 | 0.33252
~78~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Mode |  | TD | TD
~78~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet mass flow | t/h | 713.8239 | 713.8239
~78~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet pressure | bar | 33.2525 | 33.2525
~78~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet enthalpy | kJ/kg | 3478.2825 | 3478.2825
~78~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet temperature | C | 511.0024 | 511.0024
~78~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit mass flow | t/h | 713.8239 | 713.8239
~78~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit pressure | bar | 32.9232 | 32.9232
~78~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit temperature | C | 534.1 | 534.1
~78~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit enthalpy | kJ/kg | 3530.863 | 3530.863
~78~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas mass flow | t/h | 1271.106 | 1271.106
~78~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Flyash mass flow | t/h | 6.2274 | 6.2274
~78~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas inlet temperature | C | 798.2159 | 798.2159
~78~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas exit temperature | C | 775.0092 | 775.0092
~78~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat transfer to steam | kW | 10426.0859 | 10426.0859
~78~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss | kW | 78.1956 | 78.1956
~78~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Radiant heat influx | kW | 0 | 0
~78~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~78~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam side pressure drop | bar | 0.32923 | 0.32923
~79~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Mode |  | TD | TD
~79~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet mass flow | t/h | 836.1783 | 836.1783
~79~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet pressure | bar | 157.1539 | 157.1539
~79~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet enthalpy | kJ/kg | 3271.4119 | 3271.4119
~79~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet temperature | C | 489.9969 | 489.9969
~79~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit mass flow | t/h | 836.1783 | 836.1783
~79~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit pressure | bar | 155.5979 | 155.5979
~79~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit temperature | C | 517 | 517
~79~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit enthalpy | kJ/kg | 3352.4443 | 3352.4443
~79~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas mass flow | t/h | 1271.106 | 1271.106
~79~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Flyash mass flow | t/h | 6.2274 | 6.2274
~79~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas inlet temperature | C | 1025.7385 | 1025.7385
~79~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas exit temperature | C | 985.2706 | 985.2706
~79~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat transfer to steam | kW | 18821.8086 | 18821.8086
~79~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss | kW | 141.1636 | 141.1636
~79~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Radiant heat influx | kW | 0 | 0
~79~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~79~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam side pressure drop | bar | 1.556 | 1.556
~14~5~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control mode |  | Down set point | Down set point
~14~5~2~~-32~ | Boiler Assembly [1]: Valve [14] : Valve current status |  | Wide open | Wide open
~14~3~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop @ VWO | bar | 0 | 0
~14~3~10~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop | bar | 2.0172 | 2.0172
~14~3~3~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet pressure | bar | 32.9232 | 32.9232
~14~3~4~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet temperature | C | 534.1032 | 534.1032
~14~3~5~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet enthalpy | kJ/kg | 3530.863 | 3530.863
~14~3~6~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet mass flow | t/h | 713.8239 | 713.8239
~14~3~7~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet pressure | bar | 30.906 | 30.906
~14~3~8~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet temperature | C | 533.22 | 533.22
~14~3~9~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet enthalpy | kJ/kg | 3530.863 | 3530.863
~80~5~1~~-32~ | Valve [80] : Pressure control mode |  | Closed | Closed
~80~5~2~~-32~ | Valve [80] : Valve current status |  | Closed | Closed
~80~3~1~~-32~ | Valve [80] : Pressure drop @ VWO | bar | 0 | 0
~80~3~10~~-32~ | Valve [80] : Pressure drop | bar | 0 | 0
~80~3~3~~-32~ | Valve [80] : Inlet pressure | bar | 33.585 | 33.585
~80~3~4~~-32~ | Valve [80] : Inlet temperature | C | 477.2355 | 477.2355
~80~3~5~~-32~ | Valve [80] : Inlet enthalpy | kJ/kg | 3401.532 | 3401.532
~80~3~6~~-32~ | Valve [80] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~80~3~7~~-32~ | Valve [80] : Outlet pressure | bar | 33.585 | 33.585
~80~3~8~~-32~ | Valve [80] : Outlet temperature | C | 477.2355 | 477.2355
~80~3~9~~-32~ | Valve [80] : Outlet enthalpy | kJ/kg | 3401.532 | 3401.532
~81~5~1~~-32~ | Valve [81] : Pressure control mode |  | Closed | Closed
~81~5~2~~-32~ | Valve [81] : Valve current status |  | Closed | Closed
~81~3~1~~-32~ | Valve [81] : Pressure drop @ VWO | bar | 0 | 0
~81~3~10~~-32~ | Valve [81] : Pressure drop | bar | 0 | 0
~81~3~3~~-32~ | Valve [81] : Inlet pressure | bar | 30.6 | 30.6
~81~3~4~~-32~ | Valve [81] : Inlet temperature | C | 475.6206 | 475.6206
~81~3~5~~-32~ | Valve [81] : Inlet enthalpy | kJ/kg | 3401.532 | 3401.532
~81~3~6~~-32~ | Valve [81] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~81~3~7~~-32~ | Valve [81] : Outlet pressure | bar | 30.6 | 30.6
~81~3~8~~-32~ | Valve [81] : Outlet temperature | C | 475.6206 | 475.6206
~81~3~9~~-32~ | Valve [81] : Outlet enthalpy | kJ/kg | 3401.532 | 3401.532
93¦~58~3~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5
93¦~58~3~2~~-14~ | Water Sink [58] : Temperature | C | 37.3673 | 37.3673
93¦~58~3~3~~-14~ | Water Sink [58] : Enthalpy | kJ/kg | 156.7739 | 156.7739
93¦~58~3~4~~-14~ | Water Sink [58] : Mass flow | t/h | 29625.5898 | 29625.5898
93¦~57~3~1~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135
93¦~57~3~2~~-9~ | Water Source [57] : Temperature | C | 27.3223 | 27.3223
93¦~57~3~3~~-9~ | Water Source [57] : Enthalpy | kJ/kg | 114.5466 | 114.5466
93¦~57~3~4~~-9~ | Water Source [57] : Mass flow | t/h | 29625.5898 | 29625.5898
~59~10~1~~-104~ | Water-cooled Condenser (PCE) [59] : Mode |  | TD | TD
~59~3~27~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975
~59~3~26~~-104~ | Water-cooled Condenser (PCE) [59] : Saturation temperature | C | 45.3132 | 45.3132
~59~3~21~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser heat rejection (per unit) | kW | 344390.2188 | 344390.2188
~59~3~23~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
82¦71¦~1~6~1~~-20000~ | Generator [1]: Mode |  | Design | Design
91¦~1~1~7~~-20000~ | Generator [1]: Nameplate power | kW | 278780.125 | 278780.125
91¦~1~1~19~~-20000~ | Generator [1]: Nameplate efficiency | % | 98.8682 | 98.8682
91¦~1~1~5~~-20000~ | Generator [1]: Nameplate / Design point load |  | 1.05 | 1.05
76¦~1~2~8~~-20000~ | Generator [1]: Number of operating units |  | 1 | 1
93¦~1~7~2~~-20000~ | Generator [1]: Generator power output | kW | 265504.9062 | 265504.9062
93¦~1~7~6~~-20000~ | Generator [1]: Shaft power | kW | 268586.9062 | 268586.9062
93¦~1~7~4~~-20000~ | Generator [1]: Generator efficiency | % | 98.8525 | 98.8525
93¦~1~7~3~~-20000~ | Generator [1]: Total loss | kW | 3082.0088 | 3082.0088
93¦~1~7~28~~-20000~ | Generator [1]: Electrical & Windage loss | kW | 2703.3699 | 2703.3699
93¦~1~7~29~~-20000~ | Generator [1]: Mechanical loss | kW | 378.6389 | 378.6389
86¦87¦68¦86¦86¦~13~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 265504.9062 | 265504.9062
86¦87¦68¦86¦86¦~13~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.8525 | 98.8525
86¦87¦68¦86¦86¦~13~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 418.1702 | 418.1702
86¦87¦68¦86¦86¦~13~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 139.3901 | 139.3901
86¦87¦68¦86¦86¦~13~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 309.7557 | 309.7557
86¦87¦68¦86¦86¦~13~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~13~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.8682 | 98.8682
86¦87¦68¦86¦86¦~13~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 160.1586 | 160.1586
86¦87¦68¦86¦86¦~13~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 533.1628 | 533.1628
86¦87¦68¦86¦86¦~13~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 838.0318 | 838.0318
86¦87¦68¦86¦86¦~13~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~13~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 6 | 6
86¦87¦68¦86¦86¦~13~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~13~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~13~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 278780.125 | 278780.125
91¦~13~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.8682 | 98.8682
91¦~13~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~13~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~13~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 265504.9062 | 265504.9062
93¦~13~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 268586.9062 | 268586.9062
93¦~13~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.8525 | 98.8525
93¦~13~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 3082.0088 | 3082.0088
93¦~13~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 2703.3699 | 2703.3699
93¦~13~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 378.6389 | 378.6389
86¦87¦68¦86¦86¦~13~3~30~~-4100~ | ST Assembly [1]: Steam turbine length (including gear box) | m | 22.4153 | 22.4153
86¦87¦68¦86¦86¦~13~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.9827 | 4.9827
86¦87¦68¦86¦86¦~13~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight (including weight of gear box) | kg | 399729.625 | 399729.625
86¦87¦68¦86¦86¦~13~3~33~~-4100~ | ST Assembly [1]: Gear box length | m | 0 | 0
86¦87¦68¦86¦86¦~13~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 12.6893 | 12.6893
86¦87¦68¦86¦86¦~13~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.9356 | 3.9356
86¦87¦68¦86¦86¦~13~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 318347.9062 | 318347.9062
86¦87¦68¦86¦86¦~13~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 35.1046 | 35.1046
86¦87¦68¦86¦86¦~13~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.9827 | 4.9827
86¦87¦68¦86¦86¦~13~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 718077.5 | 718077.5
86¦87¦68¦86¦86¦~13~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 37.4703 | 37.4703
86¦87¦68¦86¦86¦~13~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.9793 | 5.9793
86¦87¦68¦86¦86¦~13~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 46712428 | 46712428
86¦87¦68¦86¦86¦~13~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 54234588 | 54234588
82¦71¦~13~10~3~~-11~ | ST Assembly [1]: ST Group [13] : Mode |  | Design | Design
82¦71¦~13~10~4~~-11~ | ST Assembly [1]: ST Group [13] : Type of inlet control |  | Sliding | Sliding
93¦~13~3~29~~-11~ | ST Assembly [1]: ST Group [13] : Steam supply pressure | bar | 152.532 | 152.532
93¦~13~3~11~~-11~ | ST Assembly [1]: ST Group [13] : Inlet pressure | bar | 152.532 | 152.532
93¦~13~3~12~~-11~ | ST Assembly [1]: ST Group [13] : Inlet temperature | C | 533.1628 | 533.1628
93¦~13~3~14~~-11~ | ST Assembly [1]: ST Group [13] : Inlet flow | t/h | 838.0318 | 838.0318
93¦~13~3~13~~-11~ | ST Assembly [1]: ST Group [13] : Inlet enthalpy | kJ/kg | 3401.532 | 3401.532
93¦~13~3~16~~-11~ | ST Assembly [1]: ST Group [13] : Expansion massflow | t/h | 837.5533 | 837.5533
93¦~13~3~4~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial pressure | bar | 152.532 | 152.532
93¦~13~3~15~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial enthalpy | kJ/kg | 3401.532 | 3401.532
93¦~13~3~6~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end pressure (before Exhaust Loss) | bar | 56.075 | 56.075
93¦~13~3~25~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3142.9241 | 3142.9241
93¦~13~3~21~~-11~ | ST Assembly [1]: ST Group [13] : Outlet pressure | bar | 56.075 | 56.075
93¦~13~3~22~~-11~ | ST Assembly [1]: ST Group [13] : Outlet temperature | C | 383.3184 | 383.3184
93¦~13~3~24~~-11~ | ST Assembly [1]: ST Group [13] : Outlet flow | t/h | 837.5533 | 837.5533
93¦~13~3~23~~-11~ | ST Assembly [1]: ST Group [13] : Outlet enthalpy | kJ/kg | 3142.9241 | 3142.9241
72¦79¦93¦~13~7~15~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust volume flow | m^3/s | 11.4752 | 11.4752
72¦79¦93¦~13~7~18~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~13~7~17~~-11~ | ST Assembly [1]: ST Group [13] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~13~3~7~~-11~ | ST Assembly [1]: ST Group [13] : Actual flow function | m^2 | 0.013182 | 0.013182
93¦~13~3~10~~-11~ | ST Assembly [1]: ST Group [13] : Actual pressure ratio (blading) |  | 2.7201 | 2.7201
93¦~13~3~3~~-11~ | ST Assembly [1]: ST Group [13] : Dry step efficiency | % | 85.1821 | 85.1821
93¦~13~3~1~~-11~ | ST Assembly [1]: ST Group [13] : Group overall efficiency | % | 86.436 | 86.436
93¦~13~3~30~~-11~ | ST Assembly [1]: ST Group [13] : Group blading efficiency | % | 86.436 | 86.436
93¦~13~3~50~~-11~ | ST Assembly [1]: ST Group [13] : Expansion power | kW | 60167.0156 | 60167.0156
93¦~13~3~8~~-11~ | ST Assembly [1]: ST Group [13] : Shaft power | kW | 60016.5977 | 60016.5977
93¦~13~3~9~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical loss | kW | 150.4174 | 150.4174
82¦71¦~15~10~3~~-11~ | ST Assembly [1]: ST Group [15] : Mode |  | Design | Design
82¦71¦~15~10~4~~-11~ | ST Assembly [1]: ST Group [15] : Type of inlet control |  | Sliding | Sliding
93¦~15~3~29~~-11~ | ST Assembly [1]: ST Group [15] : Steam supply pressure | bar | 56.075 | 56.075
93¦~15~3~11~~-11~ | ST Assembly [1]: ST Group [15] : Inlet pressure | bar | 56.075 | 56.075
93¦~15~3~12~~-11~ | ST Assembly [1]: ST Group [15] : Inlet temperature | C | 383.3184 | 383.3184
93¦~15~3~14~~-11~ | ST Assembly [1]: ST Group [15] : Inlet flow | t/h | 781.4125 | 781.4125
93¦~15~3~13~~-11~ | ST Assembly [1]: ST Group [15] : Inlet enthalpy | kJ/kg | 3142.9241 | 3142.9241
93¦~15~3~16~~-11~ | ST Assembly [1]: ST Group [15] : Expansion massflow | t/h | 781.4125 | 781.4125
93¦~15~3~4~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial pressure | bar | 56.075 | 56.075
93¦~15~3~15~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial enthalpy | kJ/kg | 3142.9241 | 3142.9241
93¦~15~3~6~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end pressure (before Exhaust Loss) | bar | 33.585 | 33.585
93¦~15~3~25~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3047.1497 | 3047.1497
93¦~15~3~21~~-11~ | ST Assembly [1]: ST Group [15] : Outlet pressure | bar | 33.585 | 33.585
93¦~15~3~22~~-11~ | ST Assembly [1]: ST Group [15] : Outlet temperature | C | 325.0843 | 325.0843
93¦~15~3~24~~-11~ | ST Assembly [1]: ST Group [15] : Outlet flow | t/h | 781.4125 | 781.4125
93¦~15~3~23~~-11~ | ST Assembly [1]: ST Group [15] : Outlet enthalpy | kJ/kg | 3047.1497 | 3047.1497
72¦79¦93¦~15~7~15~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust volume flow | m^3/s | 16.5157 | 16.5157
72¦79¦93¦~15~7~18~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~15~7~17~~-11~ | ST Assembly [1]: ST Group [15] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~15~3~7~~-11~ | ST Assembly [1]: ST Group [15] : Actual flow function | m^2 | 0.030484 | 0.030484
93¦~15~3~10~~-11~ | ST Assembly [1]: ST Group [15] : Actual pressure ratio (blading) |  | 1.6696 | 1.6696
93¦~15~3~3~~-11~ | ST Assembly [1]: ST Group [15] : Dry step efficiency | % | 70.5762 | 70.5762
93¦~15~3~1~~-11~ | ST Assembly [1]: ST Group [15] : Group overall efficiency | % | 71.4826 | 71.4826
93¦~15~3~30~~-11~ | ST Assembly [1]: ST Group [15] : Group blading efficiency | % | 71.4826 | 71.4826
93¦~15~3~50~~-11~ | ST Assembly [1]: ST Group [15] : Expansion power | kW | 20789.0273 | 20789.0273
93¦~15~3~8~~-11~ | ST Assembly [1]: ST Group [15] : Shaft power | kW | 20737.0547 | 20737.0547
93¦~15~3~9~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical loss | kW | 51.9725 | 51.9725
82¦71¦~26~10~3~~-11~ | ST Assembly [1]: ST Group [26] : Mode |  | Design | Design
82¦71¦~26~10~4~~-11~ | ST Assembly [1]: ST Group [26] : Type of inlet control |  | Sliding | Sliding
93¦~26~3~29~~-11~ | ST Assembly [1]: ST Group [26] : Steam supply pressure | bar | 30.6 | 30.6
93¦~26~3~11~~-11~ | ST Assembly [1]: ST Group [26] : Inlet pressure | bar | 30.6 | 30.6
93¦~26~3~12~~-11~ | ST Assembly [1]: ST Group [26] : Inlet temperature | C | 532.3315 | 532.3315
93¦~26~3~14~~-11~ | ST Assembly [1]: ST Group [26] : Inlet flow | t/h | 706.2162 | 706.2162
93¦~26~3~13~~-11~ | ST Assembly [1]: ST Group [26] : Inlet enthalpy | kJ/kg | 3529.1631 | 3529.1631
93¦~26~3~16~~-11~ | ST Assembly [1]: ST Group [26] : Expansion massflow | t/h | 706.2162 | 706.2162
93¦~26~3~4~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial pressure | bar | 30.6 | 30.6
93¦~26~3~15~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial enthalpy | kJ/kg | 3529.1631 | 3529.1631
93¦~26~3~6~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end pressure (before Exhaust Loss) | bar | 16.37 | 16.37
93¦~26~3~25~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3339.0439 | 3339.0439
93¦~26~3~21~~-11~ | ST Assembly [1]: ST Group [26] : Outlet pressure | bar | 16.37 | 16.37
93¦~26~3~22~~-11~ | ST Assembly [1]: ST Group [26] : Outlet temperature | C | 439.0564 | 439.0564
93¦~26~3~24~~-11~ | ST Assembly [1]: ST Group [26] : Outlet flow | t/h | 706.2162 | 706.2162
93¦~26~3~23~~-11~ | ST Assembly [1]: ST Group [26] : Outlet enthalpy | kJ/kg | 3339.0439 | 3339.0439
72¦79¦93¦~26~7~15~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust volume flow | m^3/s | 38.7056 | 38.7056
72¦79¦93¦~26~7~18~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~26~7~17~~-11~ | ST Assembly [1]: ST Group [26] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~26~3~7~~-11~ | ST Assembly [1]: ST Group [26] : Actual flow function | m^2 | 0.057943 | 0.057943
93¦~26~3~10~~-11~ | ST Assembly [1]: ST Group [26] : Actual pressure ratio (blading) |  | 1.8693 | 1.8693
93¦~26~3~3~~-11~ | ST Assembly [1]: ST Group [26] : Dry step efficiency | % | 88.6914 | 88.6914
93¦~26~3~1~~-11~ | ST Assembly [1]: ST Group [26] : Group overall efficiency | % | 89.213 | 89.213
93¦~26~3~30~~-11~ | ST Assembly [1]: ST Group [26] : Group blading efficiency | % | 89.213 | 89.213
93¦~26~3~50~~-11~ | ST Assembly [1]: ST Group [26] : Expansion power | kW | 37296.457 | 37296.457
93¦~26~3~8~~-11~ | ST Assembly [1]: ST Group [26] : Shaft power | kW | 37203.2188 | 37203.2188
93¦~26~3~9~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical loss | kW | 93.2411 | 93.2411
82¦71¦~28~10~3~~-11~ | ST Assembly [1]: ST Group [28] : Mode |  | Design | Design
82¦71¦~28~10~4~~-11~ | ST Assembly [1]: ST Group [28] : Type of inlet control |  | Sliding | Sliding
93¦~28~3~29~~-11~ | ST Assembly [1]: ST Group [28] : Steam supply pressure | bar | 16.37 | 16.37
93¦~28~3~11~~-11~ | ST Assembly [1]: ST Group [28] : Inlet pressure | bar | 16.37 | 16.37
93¦~28~3~12~~-11~ | ST Assembly [1]: ST Group [28] : Inlet temperature | C | 439.0564 | 439.0564
93¦~28~3~14~~-11~ | ST Assembly [1]: ST Group [28] : Inlet flow | t/h | 688.465 | 688.465
93¦~28~3~13~~-11~ | ST Assembly [1]: ST Group [28] : Inlet enthalpy | kJ/kg | 3339.0439 | 3339.0439
93¦~28~3~16~~-11~ | ST Assembly [1]: ST Group [28] : Expansion massflow | t/h | 688.465 | 688.465
93¦~28~3~4~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial pressure | bar | 16.37 | 16.37
93¦~28~3~15~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial enthalpy | kJ/kg | 3339.0439 | 3339.0439
93¦~28~3~6~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end pressure (before Exhaust Loss) | bar | 9.246 | 9.246
93¦~28~3~25~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3182.6235 | 3182.6235
93¦~28~3~21~~-11~ | ST Assembly [1]: ST Group [28] : Outlet pressure | bar | 9.246 | 9.246
93¦~28~3~22~~-11~ | ST Assembly [1]: ST Group [28] : Outlet temperature | C | 360.8472 | 360.8472
93¦~28~3~24~~-11~ | ST Assembly [1]: ST Group [28] : Outlet flow | t/h | 688.465 | 688.465
93¦~28~3~23~~-11~ | ST Assembly [1]: ST Group [28] : Outlet enthalpy | kJ/kg | 3182.6235 | 3182.6235
72¦79¦93¦~28~7~15~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust volume flow | m^3/s | 59.5915 | 59.5915
72¦79¦93¦~28~7~18~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~28~7~17~~-11~ | ST Assembly [1]: ST Group [28] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~28~3~7~~-11~ | ST Assembly [1]: ST Group [28] : Actual flow function | m^2 | 0.099421 | 0.099421
93¦~28~3~10~~-11~ | ST Assembly [1]: ST Group [28] : Actual pressure ratio (blading) |  | 1.7705 | 1.7705
93¦~28~3~3~~-11~ | ST Assembly [1]: ST Group [28] : Dry step efficiency | % | 89.8737 | 89.8737
93¦~28~3~1~~-11~ | ST Assembly [1]: ST Group [28] : Group overall efficiency | % | 90.2706 | 90.2706
93¦~28~3~30~~-11~ | ST Assembly [1]: ST Group [28] : Group blading efficiency | % | 90.2706 | 90.2706
93¦~28~3~50~~-11~ | ST Assembly [1]: ST Group [28] : Expansion power | kW | 29914.3301 | 29914.3301
93¦~28~3~8~~-11~ | ST Assembly [1]: ST Group [28] : Shaft power | kW | 29839.543 | 29839.543
93¦~28~3~9~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical loss | kW | 74.7858 | 74.7858
82¦71¦~44~10~3~~-11~ | ST Assembly [1]: ST Group [44] : Mode |  | Design | Design
82¦71¦~44~10~4~~-11~ | ST Assembly [1]: ST Group [44] : Type of inlet control |  | Sliding | Sliding
93¦~44~3~29~~-11~ | ST Assembly [1]: ST Group [44] : Steam supply pressure | bar | 9.246 | 9.246
93¦~44~3~11~~-11~ | ST Assembly [1]: ST Group [44] : Inlet pressure | bar | 9.246 | 9.246
93¦~44~3~12~~-11~ | ST Assembly [1]: ST Group [44] : Inlet temperature | C | 360.8472 | 360.8472
93¦~44~3~14~~-11~ | ST Assembly [1]: ST Group [44] : Inlet flow | t/h | 617.8905 | 617.8905
93¦~44~3~13~~-11~ | ST Assembly [1]: ST Group [44] : Inlet enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~44~3~16~~-11~ | ST Assembly [1]: ST Group [44] : Expansion massflow | t/h | 617.8905 | 617.8905
93¦~44~3~4~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial pressure | bar | 9.246 | 9.246
93¦~44~3~15~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial enthalpy | kJ/kg | 3182.6235 | 3182.6235
93¦~44~3~6~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end pressure (before Exhaust Loss) | bar | 3.642 | 3.642
93¦~44~3~25~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2961.3867 | 2961.3867
93¦~44~3~21~~-11~ | ST Assembly [1]: ST Group [44] : Outlet pressure | bar | 3.642 | 3.642
93¦~44~3~22~~-11~ | ST Assembly [1]: ST Group [44] : Outlet temperature | C | 247.8567 | 247.8567
93¦~44~3~24~~-11~ | ST Assembly [1]: ST Group [44] : Outlet flow | t/h | 617.8905 | 617.8905
93¦~44~3~23~~-11~ | ST Assembly [1]: ST Group [44] : Outlet enthalpy | kJ/kg | 2961.3867 | 2961.3867
72¦79¦93¦~44~7~15~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust volume flow | m^3/s | 111.8561 | 111.8561
72¦79¦93¦~44~7~18~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~44~7~17~~-11~ | ST Assembly [1]: ST Group [44] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~44~3~7~~-11~ | ST Assembly [1]: ST Group [44] : Actual flow function | m^2 | 0.14921 | 0.14921
93¦~44~3~10~~-11~ | ST Assembly [1]: ST Group [44] : Actual pressure ratio (blading) |  | 2.5387 | 2.5387
93¦~44~3~3~~-11~ | ST Assembly [1]: ST Group [44] : Dry step efficiency | % | 90.9151 | 90.9151
93¦~44~3~1~~-11~ | ST Assembly [1]: ST Group [44] : Group overall efficiency | % | 91.5081 | 91.5081
93¦~44~3~30~~-11~ | ST Assembly [1]: ST Group [44] : Group blading efficiency | % | 91.5081 | 91.5081
93¦~44~3~50~~-11~ | ST Assembly [1]: ST Group [44] : Expansion power | kW | 37972.875 | 37972.875
93¦~44~3~8~~-11~ | ST Assembly [1]: ST Group [44] : Shaft power | kW | 37877.9414 | 37877.9414
93¦~44~3~9~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical loss | kW | 94.9321 | 94.9321
82¦71¦~45~10~3~~-11~ | ST Assembly [1]: ST Group [45] : Mode |  | Design | Design
82¦71¦~45~10~4~~-11~ | ST Assembly [1]: ST Group [45] : Type of inlet control |  | Sliding | Sliding
93¦~45~3~29~~-11~ | ST Assembly [1]: ST Group [45] : Steam supply pressure | bar | 3.642 | 3.642
93¦~45~3~11~~-11~ | ST Assembly [1]: ST Group [45] : Inlet pressure | bar | 3.642 | 3.642
93¦~45~3~12~~-11~ | ST Assembly [1]: ST Group [45] : Inlet temperature | C | 247.8567 | 247.8567
93¦~45~3~14~~-11~ | ST Assembly [1]: ST Group [45] : Inlet flow | t/h | 583.5057 | 583.5057
93¦~45~3~13~~-11~ | ST Assembly [1]: ST Group [45] : Inlet enthalpy | kJ/kg | 2961.3867 | 2961.3867
93¦~45~3~16~~-11~ | ST Assembly [1]: ST Group [45] : Expansion massflow | t/h | 583.5057 | 583.5057
93¦~45~3~4~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial pressure | bar | 3.642 | 3.642
93¦~45~3~15~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial enthalpy | kJ/kg | 2961.3867 | 2961.3867
93¦~45~3~6~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end pressure (before Exhaust Loss) | bar | 1.38 | 1.38
93¦~45~3~25~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2770.9521 | 2770.9521
93¦~45~3~21~~-11~ | ST Assembly [1]: ST Group [45] : Outlet pressure | bar | 1.38 | 1.38
93¦~45~3~22~~-11~ | ST Assembly [1]: ST Group [45] : Outlet temperature | C | 148.594 | 148.594
93¦~45~3~24~~-11~ | ST Assembly [1]: ST Group [45] : Outlet flow | t/h | 583.5057 | 583.5057
93¦~45~3~23~~-11~ | ST Assembly [1]: ST Group [45] : Outlet enthalpy | kJ/kg | 2770.9521 | 2770.9521
72¦79¦93¦~45~7~15~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust volume flow | m^3/s | 225.9259 | 225.9259
72¦79¦93¦~45~7~18~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~45~7~17~~-11~ | ST Assembly [1]: ST Group [45] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~45~3~7~~-11~ | ST Assembly [1]: ST Group [45] : Actual flow function | m^2 | 0.32468 | 0.32468
93¦~45~3~10~~-11~ | ST Assembly [1]: ST Group [45] : Actual pressure ratio (blading) |  | 2.6391 | 2.6391
93¦~45~3~3~~-11~ | ST Assembly [1]: ST Group [45] : Dry step efficiency | % | 92.0601 | 92.0601
93¦~45~3~1~~-11~ | ST Assembly [1]: ST Group [45] : Group overall efficiency | % | 92.4759 | 92.4759
93¦~45~3~30~~-11~ | ST Assembly [1]: ST Group [45] : Group blading efficiency | % | 92.4759 | 92.4759
93¦~45~3~50~~-11~ | ST Assembly [1]: ST Group [45] : Expansion power | kW | 30867.041 | 30867.041
93¦~45~3~8~~-11~ | ST Assembly [1]: ST Group [45] : Shaft power | kW | 30789.873 | 30789.873
93¦~45~3~9~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical loss | kW | 77.1675 | 77.1675
82¦71¦~46~10~3~~-11~ | ST Assembly [1]: ST Group [46] : Mode |  | Design | Design
82¦71¦~46~10~4~~-11~ | ST Assembly [1]: ST Group [46] : Type of inlet control |  | Sliding | Sliding
93¦~46~3~29~~-11~ | ST Assembly [1]: ST Group [46] : Steam supply pressure | bar | 1.38 | 1.38
93¦~46~3~11~~-11~ | ST Assembly [1]: ST Group [46] : Inlet pressure | bar | 1.38 | 1.38
93¦~46~3~12~~-11~ | ST Assembly [1]: ST Group [46] : Inlet temperature | C | 148.594 | 148.594
93¦~46~3~14~~-11~ | ST Assembly [1]: ST Group [46] : Inlet flow | t/h | 564.0204 | 564.0204
93¦~46~3~13~~-11~ | ST Assembly [1]: ST Group [46] : Inlet enthalpy | kJ/kg | 2770.9521 | 2770.9521
93¦~46~3~16~~-11~ | ST Assembly [1]: ST Group [46] : Expansion massflow | t/h | 564.0204 | 564.0204
93¦~46~3~4~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial pressure | bar | 1.38 | 1.38
93¦~46~3~15~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial enthalpy | kJ/kg | 2770.9521 | 2770.9521
93¦~46~3~6~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end pressure (before Exhaust Loss) | bar | 0.78 | 0.78
93¦~46~3~25~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2676.2583 | 2676.2583
93¦~46~3~21~~-11~ | ST Assembly [1]: ST Group [46] : Outlet pressure | bar | 0.78 | 0.78
93¦~46~3~22~~-11~ | ST Assembly [1]: ST Group [46] : Outlet temperature | C | 98.7738 | 98.7738
93¦~46~3~24~~-11~ | ST Assembly [1]: ST Group [46] : Outlet flow | t/h | 564.0204 | 564.0204
93¦~46~3~23~~-11~ | ST Assembly [1]: ST Group [46] : Outlet enthalpy | kJ/kg | 2676.2583 | 2676.2583
72¦79¦93¦~46~7~15~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust volume flow | m^3/s | 340.6535 | 340.6535
72¦79¦93¦~46~7~18~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~46~7~17~~-11~ | ST Assembly [1]: ST Group [46] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~46~3~7~~-11~ | ST Assembly [1]: ST Group [46] : Actual flow function | m^2 | 0.74562 | 0.74562
93¦~46~3~10~~-11~ | ST Assembly [1]: ST Group [46] : Actual pressure ratio (blading) |  | 1.7692 | 1.7692
93¦~46~3~3~~-11~ | ST Assembly [1]: ST Group [46] : Dry step efficiency | % | 92.3209 | 92.3209
93¦~46~3~1~~-11~ | ST Assembly [1]: ST Group [46] : Group overall efficiency | % | 92.3209 | 92.3209
93¦~46~3~30~~-11~ | ST Assembly [1]: ST Group [46] : Group blading efficiency | % | 92.3209 | 92.3209
93¦~46~3~50~~-11~ | ST Assembly [1]: ST Group [46] : Expansion power | kW | 14836.1377 | 14836.1377
93¦~46~3~8~~-11~ | ST Assembly [1]: ST Group [46] : Shaft power | kW | 14799.0479 | 14799.0479
93¦~46~3~9~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical loss | kW | 37.0903 | 37.0903
82¦71¦~47~10~3~~-11~ | ST Assembly [1]: ST Group [47] : Mode |  | Design | Design
82¦71¦~47~10~4~~-11~ | ST Assembly [1]: ST Group [47] : Type of inlet control |  | Sliding | Sliding
93¦~47~3~29~~-11~ | ST Assembly [1]: ST Group [47] : Steam supply pressure | bar | 0.78 | 0.78
93¦~47~3~11~~-11~ | ST Assembly [1]: ST Group [47] : Inlet pressure | bar | 0.78 | 0.78
93¦~47~3~12~~-11~ | ST Assembly [1]: ST Group [47] : Inlet temperature | C | 98.7738 | 98.7738
93¦~47~3~14~~-11~ | ST Assembly [1]: ST Group [47] : Inlet flow | t/h | 540.3494 | 540.3494
93¦~47~3~13~~-11~ | ST Assembly [1]: ST Group [47] : Inlet enthalpy | kJ/kg | 2676.2583 | 2676.2583
93¦~47~3~16~~-11~ | ST Assembly [1]: ST Group [47] : Expansion massflow | t/h | 540.3494 | 540.3494
93¦~47~3~4~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial pressure | bar | 0.78 | 0.78
93¦~47~3~15~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial enthalpy | kJ/kg | 2676.2583 | 2676.2583
93¦~47~3~6~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end pressure (before Exhaust Loss) | bar | 0.283 | 0.283
93¦~47~3~25~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2528.8608 | 2528.8608
93¦~47~3~21~~-11~ | ST Assembly [1]: ST Group [47] : Outlet pressure | bar | 0.283 | 0.283
93¦~47~3~22~~-11~ | ST Assembly [1]: ST Group [47] : Outlet temperature | C | 67.7608 | 67.7608
93¦~47~3~24~~-11~ | ST Assembly [1]: ST Group [47] : Outlet flow | t/h | 540.3494 | 540.3494
93¦~47~3~23~~-11~ | ST Assembly [1]: ST Group [47] : Outlet enthalpy | kJ/kg | 2528.8608 | 2528.8608
72¦79¦93¦~47~7~15~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust volume flow | m^3/s | 795.7714 | 795.7714
72¦79¦93¦~47~7~18~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~47~7~17~~-11~ | ST Assembly [1]: ST Group [47] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~47~3~7~~-11~ | ST Assembly [1]: ST Group [47] : Actual flow function | m^2 | 1.1867 | 1.1867
93¦~47~3~10~~-11~ | ST Assembly [1]: ST Group [47] : Actual pressure ratio (blading) |  | 2.7562 | 2.7562
93¦~47~3~3~~-11~ | ST Assembly [1]: ST Group [47] : Dry step efficiency | % | 92.25 | 92.25
93¦~47~3~1~~-11~ | ST Assembly [1]: ST Group [47] : Group overall efficiency | % | 91.9033 | 91.9033
93¦~47~3~30~~-11~ | ST Assembly [1]: ST Group [47] : Group blading efficiency | % | 91.9033 | 91.9033
93¦~47~3~50~~-11~ | ST Assembly [1]: ST Group [47] : Expansion power | kW | 22124.2656 | 22124.2656
93¦~47~3~8~~-11~ | ST Assembly [1]: ST Group [47] : Shaft power | kW | 22068.9531 | 22068.9531
93¦~47~3~9~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical loss | kW | 55.3106 | 55.3106
82¦71¦~5~10~3~~-11~ | ST Assembly [1]: ST Group [5] : Mode |  | Design | Design
82¦71¦~5~10~4~~-11~ | ST Assembly [1]: ST Group [5] : Type of inlet control |  | Sliding | Sliding
93¦~5~3~29~~-11~ | ST Assembly [1]: ST Group [5] : Steam supply pressure | bar | 0.283 | 0.283
93¦~5~3~11~~-11~ | ST Assembly [1]: ST Group [5] : Inlet pressure | bar | 0.283 | 0.283
93¦~5~3~12~~-11~ | ST Assembly [1]: ST Group [5] : Inlet temperature | C | 67.7608 | 67.7608
93¦~5~3~14~~-11~ | ST Assembly [1]: ST Group [5] : Inlet flow | t/h | 523.9552 | 523.9552
93¦~5~3~13~~-11~ | ST Assembly [1]: ST Group [5] : Inlet enthalpy | kJ/kg | 2528.8608 | 2528.8608
93¦~5~3~16~~-11~ | ST Assembly [1]: ST Group [5] : Expansion massflow | t/h | 523.9552 | 523.9552
93¦~5~3~4~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial pressure | bar | 0.283 | 0.283
93¦~5~3~15~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial enthalpy | kJ/kg | 2528.8608 | 2528.8608
93¦~5~3~6~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~5~3~25~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2395.8767 | 2395.8767
93¦~5~3~21~~-11~ | ST Assembly [1]: ST Group [5] : Outlet pressure | bar | 0.0975 | 0.0975
93¦~5~3~22~~-11~ | ST Assembly [1]: ST Group [5] : Outlet temperature | C | 45.3132 | 45.3132
93¦~5~3~24~~-11~ | ST Assembly [1]: ST Group [5] : Outlet flow | t/h | 524.2274 | 524.2274
93¦~5~3~23~~-11~ | ST Assembly [1]: ST Group [5] : Outlet enthalpy | kJ/kg | 2423.9685 | 2423.9685
72¦79¦76¦~5~6~2~~-11~ | ST Assembly [1]: ST Group [5] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~5~7~15~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust volume flow per end | m^3/s | 2015.621 | 2015.621
72¦79¦91¦~5~5~3~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus area | m^2 | 8.9548 | 8.9548
72¦79¦93¦~5~7~16~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus velocity | m/s | 225.0894 | 225.0894
72¦79¦91¦~5~5~1~~-11~ | ST Assembly [1]: ST Group [5] : Last stage pitch diameter | mm | 2823.24 | 2823.24
72¦79¦91¦~5~5~2~~-11~ | ST Assembly [1]: ST Group [5] : Last stage blade length | mm | 1009.6159 | 1009.6159
72¦79¦93¦~5~7~18~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust loss | kJ/kg | 27.9108 | 27.9108
72¦79¦93¦~5~7~17~~-11~ | ST Assembly [1]: ST Group [5] : Dry exhaust loss | kJ/kg | 27.9108 | 27.9108
93¦~5~3~7~~-11~ | ST Assembly [1]: ST Group [5] : Actual flow function | m^2 | 2.9229 | 2.9229
93¦~5~3~10~~-11~ | ST Assembly [1]: ST Group [5] : Actual pressure ratio (blading) |  | 2.9026 | 2.9026
93¦~5~3~3~~-11~ | ST Assembly [1]: ST Group [5] : Dry step efficiency | % | 92.15 | 92.15
93¦~5~3~1~~-11~ | ST Assembly [1]: ST Group [5] : Group overall efficiency | % | 69.5724 | 69.5724
93¦~5~3~30~~-11~ | ST Assembly [1]: ST Group [5] : Group blading efficiency | % | 88.053 | 88.053
93¦~5~3~50~~-11~ | ST Assembly [1]: ST Group [5] : Expansion power | kW | 15292.9326 | 15292.9326
93¦~5~3~8~~-11~ | ST Assembly [1]: ST Group [5] : Shaft power | kW | 15254.6992 | 15254.6992
93¦~5~3~9~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical loss | kW | 38.2323 | 38.2323
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (source) | bar | 152.532 | 152.532
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (sink) | bar | 30.6 | 30.6
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (source) | C | 533.1628 | 533.1628
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (sink) | C | 475.6206 | 475.6206
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Enthalpy | kJ/kg | 3401.532 | 3401.532
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (source) | bar | 117.3323 | 117.3323
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (sink) | bar | 30.6 | 30.6
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (source) | C | 518.1261 | 518.1261
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (sink) | C | 475.6206 | 475.6206
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Enthalpy | kJ/kg | 3401.532 | 3401.532
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~1~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (source) | bar | 33.585 | 33.585
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~5~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (sink) | bar | 9.246 | 9.246
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (source) | C | 325.0843 | 325.0843
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (sink) | C | 296.9314 | 296.9314
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~2~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 91.1106 | 91.1106
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.5933 | 83.5933
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 675.8881 | 675.8881
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 736.6685 | 736.6685
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 140.758 | 140.758
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 615805.5625 | 615805.5625
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 154.0573 | 154.0573
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 534.4001 | 534.4001
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 838.0318 | 838.0318
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3403.2319 | 3403.2319
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 161.9158 | 161.9158
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 268.2197 | 268.2197
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 835.3832 | 835.3832
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 1173.7863 | 1173.7863
93¦~7~3~165~~-4200~ | Boiler Assembly [1]: Hot reheat pressure | bar | 30.906 | 30.906
93¦~7~3~166~~-4200~ | Boiler Assembly [1]: Hot reheat temperature | C | 533.22 | 533.22
93¦~7~3~167~~-4200~ | Boiler Assembly [1]: Hot reheat massflow | t/h | 713.8239 | 713.8239
93¦~7~3~168~~-4200~ | Boiler Assembly [1]: Hot reheat enthalpy | kJ/kg | 3530.863 | 3530.863
93¦~7~3~161~~-4200~ | Boiler Assembly [1]: Cold reheat pressure | bar | 33.585 | 33.585
93¦~7~3~162~~-4200~ | Boiler Assembly [1]: Cold reheat temperature | C | 325.0843 | 325.0843
93¦~7~3~163~~-4200~ | Boiler Assembly [1]: Cold reheat massflow | t/h | 713.7567 | 713.7567
93¦~7~3~164~~-4200~ | Boiler Assembly [1]: Cold reheat enthalpy | kJ/kg | 3047.1497 | 3047.1497
~1~1~0~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Pressure | bar | 1.0332 | 1.0332
~1~1~1~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Temperature | C | 25.85 | 25.85
~1~1~2~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mass flow | t/h | 973.2435 | 973.2435
~1~1~22~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash flow | t/h | 0 | 0
~1~1~16~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~1~18~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Relative humidity | % | 59.24 | 59.24
~1~1~20~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Entropy | kJ/kg-C | 0.18546 | 0.18546
~1~1~3~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Enthalpy | kJ/kg | 0.86557 | 0.86557
~1~1~19~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Molecular weight | M.W. | 28.7578 | 28.7578
~1~1~4~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO2 mass flow | t/h | 0.44272 | 0.44272
~1~1~5~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Volume flow | m^3/s | 226.207 | 226.207
~1~1~101~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Density | kg/m^3 | 1.1951 | 1.1951
~1~1~6~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of N2 | % | 76.5891 | 76.5891
~1~1~7~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of O2 | % | 20.5495 | 20.5495
~1~1~8~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~1~9~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O | % | 1.9093 | 1.9093
~1~1~10~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~1~11~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of Ar | % | 0.92239 | 0.92239
~1~1~12~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of SO2 | % | 0 | 0
~1~1~14~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~1~23~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: HCl mass flow | kg/hr | 0 | 0
~1~1~24~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: NOx mass flow | kg/hr | 0 | 0
~1~1~25~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO mass flow | kg/hr | 0 | 0
~1~1~26~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: UHC mass flow | kg/hr | 0 | 0
~1~1~29~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Hg mass flow | kg/hr | 0 | 0
~1~1~32~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~1~31~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Normal volume flow | Nm^3/hr | 758583.25 | 758583.25
~1~2~0~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1254 | 1.1254
~1~2~1~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 326.0734 | 326.0734
~1~2~2~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 201.5027 | 201.5027
~1~2~22~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~2~16~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~2~18~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~2~20~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.87656 | 0.87656
~1~2~3~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 311.3847 | 311.3847
~1~2~19~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~2~4~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.091742 | 0.091742
~1~2~5~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 86.1238 | 86.1238
~1~2~101~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.64991 | 0.64991
~1~2~6~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~2~7~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~2~8~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~2~9~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~2~10~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~2~12~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~2~14~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~2~23~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~2~31~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 156977.1406 | 156977.1406
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Pressure | bar | 1.1379 | 1.1379
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Temperature | C | 28.2082 | 28.2082
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mass flow | t/h | 283.799 | 283.799
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Relative humidity | % | 52.7378 | 52.7378
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Entropy | kJ/kg-C | 0.16412 | 0.16412
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Enthalpy | kJ/kg | 3.2646 | 3.2646
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Molecular weight | M.W. | 28.7728 | 28.7728
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO2 mass flow | t/h | 0.12921 | 0.12921
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Volume flow | m^3/s | 60.3343 | 60.3343
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Density | kg/m^3 | 1.3066 | 1.3066
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of N2 | % | 76.6959 | 76.6959
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of O2 | % | 20.5782 | 20.5782
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O | % | 1.7725 | 1.7725
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of Ar | % | 0.92367 | 0.92367
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Normal volume flow | Nm^3/hr | 221088.625 | 221088.625
~1~13~0~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 1.0118 | 1.0118
~1~13~1~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 1141.4 | 1141.4
~1~13~2~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 1271.105 | 1271.105
~1~13~22~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash flow | t/h | 6.2274 | 6.2274
~1~13~16~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash enthalpy | kJ/kg | 1258.387 | 1258.387
~1~13~18~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 2.1017 | 2.1017
~1~13~3~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 1354.7609 | 1354.7609
~1~13~19~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~13~4~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~13~5~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Volume flow | m^3/s | 1413.2001 | 1413.2001
~1~13~101~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 0.24985 | 0.24985
~1~13~6~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~13~7~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~13~8~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~13~9~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~13~10~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~13~12~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~13~14~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~13~23~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~13~31~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99933 | 0.99933
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 745.5897 | 745.5897
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 1271.105 | 1271.105
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 6.2274 | 6.2274
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 788.3267 | 788.3267
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6765 | 1.6765
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 836.8634 | 836.8634
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 1030.4608 | 1030.4608
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34265 | 0.34265
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.99683 | 0.99683
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 503.6194 | 503.6194
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 1271.105 | 1271.105
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 6.2274 | 6.2274
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 487.7752 | 487.7752
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.3432 | 1.3432
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 538.4443 | 538.4443
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 29.0436 | 29.0436
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 787.6711 | 787.6711
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.44826 | 0.44826
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 69.3633 | 69.3633
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 3.7173 | 3.7173
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 13.0614 | 13.0614
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.83426 | 0.83426
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 4.2757 | 4.2757
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~16~0~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 0.99434 | 0.99434
~1~16~1~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 357.8673 | 357.8673
~1~16~2~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 1271.105 | 1271.105
~1~16~22~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 6.2274 | 6.2274
~1~16~16~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 316.9698 | 316.9698
~1~16~18~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 0 | 0
~1~16~20~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 1.0998 | 1.0998
~1~16~3~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 367.1445 | 367.1445
~1~16~19~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 29.0436 | 29.0436
~1~16~4~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~16~5~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 641.4775 | 641.4775
~1~16~101~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 0.55042 | 0.55042
~1~16~6~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 69.3633 | 69.3633
~1~16~7~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 3.7173 | 3.7173
~1~16~8~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~16~9~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 13.0614 | 13.0614
~1~16~10~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.83426 | 0.83426
~1~16~12~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~16~14~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~16~23~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 4.2757 | 4.2757
~1~16~31~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~83~0~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 1.0093 | 1.0093
~1~83~1~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 1025.739 | 1025.739
~1~83~2~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 1271.105 | 1271.105
~1~83~22~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash flow | t/h | 6.2274 | 6.2274
~1~83~16~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash enthalpy | kJ/kg | 1125.1151 | 1125.1151
~1~83~18~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Relative humidity | % | 0 | 0
~1~83~20~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 1.9885 | 1.9885
~1~83~3~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 1200.2502 | 1200.2502
~1~83~19~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~83~4~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~83~5~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Volume flow | m^3/s | 1300.8542 | 1300.8542
~1~83~101~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 0.27143 | 0.27143
~1~83~6~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~83~7~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~83~8~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~83~9~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~83~10~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O liquid | % | 0 | 0
~1~83~11~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~83~12~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~83~14~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~83~23~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: HCl mass flow | kg/hr | 0 | 0
~1~83~24~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: NOx mass flow | kg/hr | 0 | 0
~1~83~25~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO mass flow | kg/hr | 0 | 0
~1~83~26~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: UHC mass flow | kg/hr | 0 | 0
~1~83~29~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Hg mass flow | kg/hr | 0 | 0
~1~83~32~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~83~31~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~89~0~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1329 | 1.1329
~1~89~1~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 27.2082 | 27.2082
~1~89~2~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 52.0721 | 52.0721
~1~89~22~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 55.664 | 55.664
~1~89~20~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~89~3~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~89~19~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~89~4~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.023708 | 0.023708
~1~89~5~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 11.0821 | 11.0821
~1~89~101~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 1.3052 | 1.3052
~1~89~6~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~89~7~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~89~8~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~89~9~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~89~10~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~89~12~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 40565.8203 | 40565.8203
~1~90~0~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.1329 | 1.1329
~1~90~1~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 27.2082 | 27.2082
~1~90~2~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 231.7269 | 231.7269
~1~90~22~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~90~16~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~90~18~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 55.664 | 55.664
~1~90~20~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.162 | 0.162
~1~90~3~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 2.247 | 2.247
~1~90~19~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7728 | 28.7728
~1~90~4~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.1055 | 0.1055
~1~90~5~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 49.3167 | 49.3167
~1~90~101~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.3052 | 1.3052
~1~90~6~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.6959 | 76.6959
~1~90~7~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5782 | 20.5782
~1~90~8~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~90~9~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.7725 | 1.7725
~1~90~10~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~90~11~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92367 | 0.92367
~1~90~12~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~90~14~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~90~23~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~90~24~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~90~25~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~90~26~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~90~29~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~90~32~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~90~31~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 180522.7969 | 180522.7969
~1~91~0~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.98686 | 0.98686
~1~91~1~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 146.1556 | 146.1556
~1~91~2~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 1389.806 | 1389.806
~1~91~22~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 6.2274 | 6.2274
~1~91~16~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 100.0657 | 100.0657
~1~91~18~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 2.7835 | 2.7835
~1~91~20~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.64526 | 0.64526
~1~91~3~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 129.5923 | 129.5923
~1~91~19~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 29.0193 | 29.0193
~1~91~4~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 250.5383 | 250.5383
~1~91~5~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 469.9867 | 469.9867
~1~91~101~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.82142 | 0.82142
~1~91~6~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 69.9883 | 69.9883
~1~91~7~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 5.1684 | 5.1684
~1~91~8~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 11.8866 | 11.8866
~1~91~9~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 12.0974 | 12.0974
~1~91~10~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~91~11~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.84189 | 0.84189
~1~91~12~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.017419 | 0.017419
~1~91~14~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.87093 | 0.87093
~1~91~23~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~91~24~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~91~25~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~91~26~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~91~29~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~91~32~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 5.8797 | 5.8797
~1~91~31~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 1073505.5 | 1073505.5
~1~92~0~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0243 | 1.0243
~1~92~1~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 273.8889 | 273.8889
~1~92~2~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 884.7667 | 884.7667
~1~92~22~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~92~16~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~92~18~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~92~20~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.80947 | 0.80947
~1~92~3~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 256.4639 | 256.4639
~1~92~19~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7578 | 28.7578
~1~92~4~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.40247 | 0.40247
~1~92~5~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 379.5152 | 379.5152
~1~92~101~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.64759 | 0.64759
~1~92~6~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.5891 | 76.5891
~1~92~7~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5495 | 20.5495
~1~92~8~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~92~9~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.9093 | 1.9093
~1~92~10~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~92~11~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92239 | 0.92239
~1~92~12~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~92~14~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~92~23~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~92~24~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~92~25~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~92~26~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~92~29~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~92~32~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~92~31~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 689621.0625 | 689621.0625
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Pressure | bar | 0.97876 | 0.97876
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Temperature | C | 146.1556 | 146.1556
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mass flow | t/h | 1389.806 | 1389.806
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash flow | t/h | 0.023781 | 0.023781
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash enthalpy | kJ/kg | 100.0657 | 100.0657
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Relative humidity | % | 2.7606 | 2.7606
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Entropy | kJ/kg-C | 0.64762 | 0.64762
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Enthalpy | kJ/kg | 129.5923 | 129.5923
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Molecular weight | M.W. | 29.0193 | 29.0193
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO2 mass flow | t/h | 250.5387 | 250.5387
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Volume flow | m^3/s | 473.8767 | 473.8767
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Density | kg/m^3 | 0.81468 | 0.81468
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of N2 | % | 69.9883 | 69.9883
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of O2 | % | 5.1684 | 5.1684
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of CO2 | % | 11.8866 | 11.8866
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O | % | 12.0974 | 12.0974
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of Ar | % | 0.84189 | 0.84189
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of SO2 | % | 0.017419 | 0.017419
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Dry Oxygen | % | 5.8796 | 5.8796
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Normal volume flow | Nm^3/hr | 1073505.5 | 1073505.5
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.97378 | 0.97378
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 145.0445 | 145.0445
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 1389.806 | 1389.806
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.023781 | 0.023781
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 99.0575 | 99.0575
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 2.8316 | 2.8316
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.64621 | 0.64621
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 128.3885 | 128.3885
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 29.0193 | 29.0193
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 250.5387 | 250.5387
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 475.0406 | 475.0406
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.81268 | 0.81268
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 69.9883 | 69.9883
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 5.1684 | 5.1684
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 11.8866 | 11.8866
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 12.0974 | 12.0974
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.84189 | 0.84189
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.017419 | 0.017419
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 5.8796 | 5.8796
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 1073505.5 | 1073505.5
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 150.4492 | 150.4492
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 1389.806 | 1389.806
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.023781 | 0.023781
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 103.9761 | 103.9761
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 2.5423 | 2.5423
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.64898 | 0.64898
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 134.2466 | 134.2466
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 29.0193 | 29.0193
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 250.5387 | 250.5387
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 462.817 | 462.817
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.83415 | 0.83415
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 69.9883 | 69.9883
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 5.1684 | 5.1684
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 11.8866 | 11.8866
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 12.0974 | 12.0974
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.84189 | 0.84189
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.017419 | 0.017419
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 5.8796 | 5.8796
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 1073505.5 | 1073505.5
~1~96~0~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.0317 | 1.0317
~1~96~1~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 26.2127 | 26.2127
~1~96~2~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 973.2435 | 973.2435
~1~96~22~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~96~16~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~96~18~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 57.9016 | 57.9016
~1~96~20~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.1871 | 0.1871
~1~96~3~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~96~19~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7578 | 28.7578
~1~96~4~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.44272 | 0.44272
~1~96~5~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 226.7995 | 226.7995
~1~96~101~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.192 | 1.192
~1~96~6~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.5891 | 76.5891
~1~96~7~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5495 | 20.5495
~1~96~8~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~96~9~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.9093 | 1.9093
~1~96~10~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~96~11~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92239 | 0.92239
~1~96~12~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~96~14~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~96~23~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~96~24~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~96~25~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~96~26~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~96~29~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~96~32~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~96~31~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 758583.25 | 758583.25
~1~97~0~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Pressure | bar | 1.0367 | 1.0367
~1~97~1~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Temperature | C | 26.2127 | 26.2127
~1~97~2~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mass flow | t/h | 973.2435 | 973.2435
~1~97~22~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash flow | t/h | 0 | 0
~1~97~16~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~97~18~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Relative humidity | % | 58.1814 | 58.1814
~1~97~20~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Entropy | kJ/kg-C | 0.18571 | 0.18571
~1~97~3~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~97~19~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Molecular weight | M.W. | 28.7578 | 28.7578
~1~97~4~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO2 mass flow | t/h | 0.44272 | 0.44272
~1~97~5~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Volume flow | m^3/s | 225.7089 | 225.7089
~1~97~101~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Density | kg/m^3 | 1.1978 | 1.1978
~1~97~6~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of N2 | % | 76.5891 | 76.5891
~1~97~7~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of O2 | % | 20.5495 | 20.5495
~1~97~8~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~97~9~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O | % | 1.9093 | 1.9093
~1~97~10~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~97~11~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of Ar | % | 0.92239 | 0.92239
~1~97~12~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of SO2 | % | 0 | 0
~1~97~14~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~97~23~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: HCl mass flow | kg/hr | 0 | 0
~1~97~24~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: NOx mass flow | kg/hr | 0 | 0
~1~97~25~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO mass flow | kg/hr | 0 | 0
~1~97~26~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: UHC mass flow | kg/hr | 0 | 0
~1~97~29~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Hg mass flow | kg/hr | 0 | 0
~1~97~32~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~97~31~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Normal volume flow | Nm^3/hr | 758583.25 | 758583.25
~1~98~0~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Pressure | bar | 1.1329 | 1.1329
~1~98~1~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Temperature | C | 27.2082 | 27.2082
~1~98~2~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mass flow | t/h | 283.799 | 283.799
~1~98~22~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash flow | t/h | 0 | 0
~1~98~16~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~98~18~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Relative humidity | % | 55.664 | 55.664
~1~98~20~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~98~3~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~98~19~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~98~4~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO2 mass flow | t/h | 0.12921 | 0.12921
~1~98~5~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Volume flow | m^3/s | 60.3987 | 60.3987
~1~98~101~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Density | kg/m^3 | 1.3052 | 1.3052
~1~98~6~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~98~7~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~98~8~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~98~9~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~98~10~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O liquid | % | 0 | 0
~1~98~11~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~98~12~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of SO2 | % | 0 | 0
~1~98~14~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~98~23~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: HCl mass flow | kg/hr | 0 | 0
~1~98~24~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: NOx mass flow | kg/hr | 0 | 0
~1~98~25~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO mass flow | kg/hr | 0 | 0
~1~98~26~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: UHC mass flow | kg/hr | 0 | 0
~1~98~29~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Hg mass flow | kg/hr | 0 | 0
~1~98~32~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Dry Oxygen | % | 20.9495 | 20.9495
~1~98~31~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Normal volume flow | Nm^3/hr | 221088.625 | 221088.625
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Pressure | bar | 1.1129 | 1.1129
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Temperature | C | 25.85 | 25.85
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mass flow | t/h | 283.799 | 283.799
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Relative humidity | % | 59.24 | 59.24
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Entropy | kJ/kg-C | 0.16252 | 0.16252
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Enthalpy | kJ/kg | 0.86495 | 0.86495
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Molecular weight | M.W. | 28.7728 | 28.7728
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO2 mass flow | t/h | 0.12921 | 0.12921
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Volume flow | m^3/s | 61.2029 | 61.2029
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Density | kg/m^3 | 1.2881 | 1.2881
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of N2 | % | 76.6959 | 76.6959
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of O2 | % | 20.5782 | 20.5782
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O | % | 1.7725 | 1.7725
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of Ar | % | 0.92367 | 0.92367
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Normal volume flow | Nm^3/hr | 221088.625 | 221088.625
~1~113~0~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 1.0043 | 1.0043
~1~113~1~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 798.2157 | 798.2157
~1~113~2~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 1271.105 | 1271.105
~1~113~22~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash flow | t/h | 6.2274 | 6.2274
~1~113~16~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash enthalpy | kJ/kg | 853.8682 | 853.8682
~1~113~18~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Relative humidity | % | 0 | 0
~1~113~20~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 1.7391 | 1.7391
~1~113~3~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 903.8207 | 903.8207
~1~113~19~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Molecular weight | M.W. | 29.0436 | 29.0436
~1~113~4~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~113~5~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Volume flow | m^3/s | 1078.3129 | 1078.3129
~1~113~101~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 0.32744 | 0.32744
~1~113~6~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of N2 | % | 69.3633 | 69.3633
~1~113~7~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of O2 | % | 3.7173 | 3.7173
~1~113~8~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~113~9~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O | % | 13.0614 | 13.0614
~1~113~10~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of Ar | % | 0.83426 | 0.83426
~1~113~12~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~113~14~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~113~23~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dry Oxygen | % | 4.2757 | 4.2757
~1~113~31~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~114~0~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 1.0018 | 1.0018
~1~114~1~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 775.0095 | 775.0095
~1~114~2~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 1271.105 | 1271.105
~1~114~22~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 6.2274 | 6.2274
~1~114~16~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 825.0305 | 825.0305
~1~114~18~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~114~20~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.7119 | 1.7119
~1~114~3~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 874.2132 | 874.2132
~1~114~19~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~114~4~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~114~5~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 1057.5811 | 1057.5811
~1~114~101~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.33386 | 0.33386
~1~114~6~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~114~7~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~114~8~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~114~9~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~114~10~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~114~12~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~114~14~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~114~23~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~114~31~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~1~116~0~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 1.0068 | 1.0068
~1~116~1~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 985.27 | 985.27
~1~116~2~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 1271.105 | 1271.105
~1~116~22~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash flow | t/h | 6.2274 | 6.2274
~1~116~16~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash enthalpy | kJ/kg | 1079.0077 | 1079.0077
~1~116~18~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Relative humidity | % | 0 | 0
~1~116~20~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 1.9473 | 1.9473
~1~116~3~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 1146.7693 | 1146.7693
~1~116~19~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Molecular weight | M.W. | 29.0436 | 29.0436
~1~116~4~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO2 mass flow | t/h | 250.4843 | 250.4843
~1~116~5~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Volume flow | m^3/s | 1263.4442 | 1263.4442
~1~116~101~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 0.27946 | 0.27946
~1~116~6~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of N2 | % | 69.3633 | 69.3633
~1~116~7~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of O2 | % | 3.7173 | 3.7173
~1~116~8~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~116~9~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O | % | 13.0614 | 13.0614
~1~116~10~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of Ar | % | 0.83426 | 0.83426
~1~116~12~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~116~14~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~116~23~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dry Oxygen | % | 4.2757 | 4.2757
~1~116~31~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Normal volume flow | Nm^3/hr | 980997.6875 | 980997.6875
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 0.175 | 0.175
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 285.2766 | 285.2766
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 0.40748 | 0.40748
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 8.9722 | 8.9722
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | 1.1874 | 1.1874
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 0.067935 | 0.067935
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 1.9906 | 1.9906
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.041888 | 0.041888
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 1.9696e-05 | 1.9696e-05
~2~4~0~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~4~1~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Temperature | C | 285.1744 | 285.1744
~2~4~2~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 0.71488 | 0.71488
~2~4~20~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 9.242 | 9.242
~2~4~4~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~4~3~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~4~5~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Steam quality |  | 1.1939 | 1.1939
~2~4~10~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.037849 | 0.037849
~2~4~11~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 1.9894 | 1.9894
~2~4~12~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.04187 | 0.04187
~2~4~13~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.9693e-05 | 1.9693e-05
~2~5~0~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 166.8056 | 166.8056
~2~5~1~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 238.7926 | 238.7926
~2~5~2~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 835.3832 | 835.3832
~2~5~20~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 2.6631 | 2.6631
~2~5~4~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 1033.8855 | 1033.8855
~2~5~3~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | -1513.603 | -1513.603
~2~5~5~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | -0.72987 | -0.72987
~2~5~10~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 828.2706 | 828.2706
~2~5~11~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 4.6281 | 4.6281
~2~5~12~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.64572 | 0.64572
~2~5~13~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 0.00011454 | 0.00011454
~2~6~0~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Pressure | bar | 10.2423 | 10.2423
~2~6~1~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Temperature | C | 133.9796 | 133.9796
~2~6~2~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Mass flow | t/h | 650.5074 | 650.5074
~2~6~20~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 1.6758 | 1.6758
~2~6~4~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 563.8093 | 563.8093
~2~6~3~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1983.6792 | -1983.6792
~2~6~5~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Steam quality |  | -0.1012 | -0.1012
~2~6~10~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Density | kg/m^3 | 931.8362 | 931.8362
~2~6~11~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.2693 | 4.2693
~2~6~12~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.68595 | 0.68595
~2~6~13~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00020608 | 0.00020608
~2~7~0~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Pressure | bar | 9.246 | 9.246
~2~7~1~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Temperature | C | 360.8472 | 360.8472
~2~7~2~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Mass flow | t/h | 28.9328 | 28.9328
~2~7~20~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~7~4~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~7~3~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~7~5~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Steam quality |  | 1.2016 | 1.2016
~2~7~10~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Density | kg/m^3 | 3.2092 | 3.2092
~2~7~11~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~7~12~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~7~13~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~9~0~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 33.585 | 33.585
~2~9~1~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 325.0843 | 325.0843
~2~9~2~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 713.7567 | 713.7567
~2~9~20~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~9~4~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~9~3~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | 499.6609 | 499.6609
~2~9~5~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | 1.1383 | 1.1383
~2~9~10~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 13.1426 | 13.1426
~2~9~11~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~9~12~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~9~13~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~10~0~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Pressure | bar | 32.9232 | 32.9232
~2~10~1~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Temperature | C | 534.1032 | 534.1032
~2~10~2~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Mass flow | t/h | 713.8239 | 713.8239
~2~10~20~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Entropy | kJ/kg-C | 7.2871 | 7.2871
~2~10~4~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy | kJ/kg | 3530.863 | 3530.863
~2~10~3~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy H* | kJ/kg | 983.3745 | 983.3745
~2~10~5~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Steam quality |  | 1.4111 | 1.4111
~2~10~10~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Density | kg/m^3 | 9.0297 | 9.0297
~2~10~11~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Specific heat | kJ/kg-C | 2.2503 | 2.2503
~2~10~12~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Thermal conductivity | W/m-C | 0.073484 | 0.073484
~2~10~13~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Dynamic viscosity | kg/m-s | 3.0051e-05 | 3.0051e-05
~2~11~0~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Pressure | bar | 0.45641 | 0.45641
~2~11~1~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Temperature | C | 45.3184 | 45.3184
~2~11~2~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Mass flow | t/h | 648.2178 | 648.2178
~2~11~20~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Entropy | kJ/kg-C | 0.64279 | 0.64279
~2~11~4~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy | kJ/kg | 189.7462 | 189.7462
~2~11~3~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy H* | kJ/kg | -2357.7424 | -2357.7424
~2~11~5~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Steam quality |  | -0.061141 | -0.061141
~2~11~10~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Density | kg/m^3 | 990.103 | 990.103
~2~11~11~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~11~12~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Thermal conductivity | W/m-C | 0.63566 | 0.63566
~2~11~13~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Dynamic viscosity | kg/m-s | 0.0005921 | 0.0005921
~2~12~0~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Pressure | bar | 54.9755 | 54.9755
~2~12~1~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Temperature | C | 241.5728 | 241.5728
~2~12~2~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 56.1408 | 56.1408
~2~12~20~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.7117 | 2.7117
~2~12~4~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 1045.2972 | 1045.2972
~2~12~3~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1502.1913 | -1502.1913
~2~12~5~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Steam quality |  | -0.086907 | -0.086907
~2~12~10~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 813.3593 | 813.3593
~2~12~11~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.7592 | 4.7592
~2~12~12~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.63022 | 0.63022
~2~12~13~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.00011027 | 0.00011027
~2~17~0~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Pressure | bar | 163.5349 | 163.5349
~2~17~1~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Temperature | C | 268.428 | 268.428
~2~17~2~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Mass flow | t/h | 835.3832 | 835.3832
~2~17~20~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Entropy | kJ/kg-C | 2.9313 | 2.9313
~2~17~4~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy | kJ/kg | 1174.7864 | 1174.7864
~2~17~3~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy H* | kJ/kg | -1372.7021 | -1372.7021
~2~17~5~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Steam quality |  | -0.53997 | -0.53997
~2~17~10~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Density | kg/m^3 | 784.6912 | 784.6912
~2~17~11~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Specific heat | kJ/kg-C | 4.9034 | 4.9034
~2~17~12~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Thermal conductivity | W/m-C | 0.61094 | 0.61094
~2~17~13~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Dynamic viscosity | kg/m-s | 0.00010122 | 0.00010122
~2~18~0~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Pressure | bar | 152.532 | 152.532
~2~18~1~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Temperature | C | 533.1628 | 533.1628
~2~18~2~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Mass flow | t/h | 838.0318 | 838.0318
~2~18~20~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Entropy | kJ/kg-C | 6.456 | 6.456
~2~18~4~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~18~3~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~18~5~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Steam quality |  | 1.8114 | 1.8114
~2~18~10~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Density | kg/m^3 | 45.7963 | 45.7963
~2~18~11~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Specific heat | kJ/kg-C | 2.7355 | 2.7355
~2~18~12~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Thermal conductivity | W/m-C | 0.084604 | 0.084604
~2~18~13~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Dynamic viscosity | kg/m-s | 3.0709e-05 | 3.0709e-05
~2~19~0~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 11.4366 | 11.4366
~2~19~1~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 45.3698 | 45.3698
~2~19~2~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 650.5074 | 650.5074
~2~19~20~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 0.64299 | 0.64299
~2~19~4~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 190.9263 | 190.9263
~2~19~3~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | -2356.5623 | -2356.5623
~2~19~5~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | -0.3 | -0.3
~2~19~10~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 990.5593 | 990.5593
~2~19~11~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 4.177 | 4.177
~2~19~12~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.63629 | 0.63629
~2~19~13~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 0.0005917 | 0.0005917
~2~20~0~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Pressure | bar | 56.075 | 56.075
~2~20~1~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Temperature | C | 383.3184 | 383.3184
~2~20~2~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Mass flow | t/h | 837.5533 | 837.5533
~2~20~20~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Entropy | kJ/kg-C | 6.5186 | 6.5186
~2~20~4~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy | kJ/kg | 3142.9241 | 3142.9241
~2~20~3~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy H* | kJ/kg | 595.4355 | 595.4355
~2~20~5~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Steam quality |  | 1.2218 | 1.2218
~2~20~10~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Density | kg/m^3 | 20.2746 | 20.2746
~2~20~11~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Specific heat | kJ/kg-C | 2.5745 | 2.5745
~2~20~12~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Thermal conductivity | W/m-C | 0.0588 | 0.0588
~2~20~13~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Dynamic viscosity | kg/m-s | 2.3649e-05 | 2.3649e-05
~2~21~0~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Pressure | bar | 56.075 | 56.075
~2~21~1~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Temperature | C | 383.3184 | 383.3184
~2~21~2~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Mass flow | t/h | 781.4125 | 781.4125
~2~21~20~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Entropy | kJ/kg-C | 6.5186 | 6.5186
~2~21~4~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy | kJ/kg | 3142.9241 | 3142.9241
~2~21~3~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy H* | kJ/kg | 595.4355 | 595.4355
~2~21~5~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Steam quality |  | 1.2218 | 1.2218
~2~21~10~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Density | kg/m^3 | 20.2746 | 20.2746
~2~21~11~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Specific heat | kJ/kg-C | 2.5745 | 2.5745
~2~21~12~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Thermal conductivity | W/m-C | 0.0588 | 0.0588
~2~21~13~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Dynamic viscosity | kg/m-s | 2.3649e-05 | 2.3649e-05
~2~22~0~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Pressure | bar | 56.075 | 56.075
~2~22~1~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Temperature | C | 383.3184 | 383.3184
~2~22~2~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Mass flow | t/h | 56.1408 | 56.1408
~2~22~20~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Entropy | kJ/kg-C | 6.5186 | 6.5186
~2~22~4~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy | kJ/kg | 3142.9241 | 3142.9241
~2~22~3~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy H* | kJ/kg | 595.4355 | 595.4355
~2~22~5~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Steam quality |  | 1.2218 | 1.2218
~2~22~10~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Density | kg/m^3 | 20.2746 | 20.2746
~2~22~11~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Specific heat | kJ/kg-C | 2.5745 | 2.5745
~2~22~12~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Thermal conductivity | W/m-C | 0.0588 | 0.0588
~2~22~13~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Dynamic viscosity | kg/m-s | 2.3649e-05 | 2.3649e-05
~2~23~0~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 33.585 | 33.585
~2~23~1~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Temperature | C | 325.0843 | 325.0843
~2~23~2~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Mass flow | t/h | 781.4125 | 781.4125
~2~23~20~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~23~4~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~23~3~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~23~5~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Steam quality |  | 1.1383 | 1.1383
~2~23~10~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Density | kg/m^3 | 13.1426 | 13.1426
~2~23~11~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~23~12~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~23~13~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~24~0~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Pressure | bar | 33.585 | 33.585
~2~24~1~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Temperature | C | 325.0843 | 325.0843
~2~24~2~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Mass flow | t/h | 714.879 | 714.879
~2~24~20~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~24~4~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~24~3~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~24~5~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Steam quality |  | 1.1383 | 1.1383
~2~24~10~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Density | kg/m^3 | 13.1426 | 13.1426
~2~24~11~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~24~12~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~24~13~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~25~0~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Pressure | bar | 33.585 | 33.585
~2~25~1~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Temperature | C | 325.0843 | 325.0843
~2~25~2~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Mass flow | t/h | 713.7567 | 713.7567
~2~25~20~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~25~4~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~25~3~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~25~5~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Steam quality |  | 1.1383 | 1.1383
~2~25~10~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Density | kg/m^3 | 13.1426 | 13.1426
~2~25~11~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~25~12~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~25~13~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Pressure | bar | 33.585 | 33.585
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Temperature | C | 325.0843 | 325.0843
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Mass flow | t/h | 61.3925 | 61.3925
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Steam quality |  | 1.1383 | 1.1383
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Density | kg/m^3 | 13.1426 | 13.1426
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~27~0~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Pressure | bar | 152.532 | 152.532
~2~27~1~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Temperature | C | 533.1628 | 533.1628
~2~27~2~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Mass flow | t/h | 838.0318 | 838.0318
~2~27~20~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Entropy | kJ/kg-C | 6.456 | 6.456
~2~27~4~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~27~3~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~27~5~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Steam quality |  | 1.8114 | 1.8114
~2~27~10~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Density | kg/m^3 | 45.7963 | 45.7963
~2~27~11~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Specific heat | kJ/kg-C | 2.7355 | 2.7355
~2~27~12~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Thermal conductivity | W/m-C | 0.084604 | 0.084604
~2~27~13~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Dynamic viscosity | kg/m-s | 3.0709e-05 | 3.0709e-05
~2~28~0~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 32.9265 | 32.9265
~2~28~1~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 323.9767 | 323.9767
~2~28~2~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 61.3925 | 61.3925
~2~28~20~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 6.5901 | 6.5901
~2~28~4~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 3046.1497 | 3046.1497
~2~28~3~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | 498.661 | 498.661
~2~28~5~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | 1.1373 | 1.1373
~2~28~10~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 12.8948 | 12.8948
~2~28~11~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 2.5034 | 2.5034
~2~28~12~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.050252 | 0.050252
~2~28~13~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 2.1069e-05 | 2.1069e-05
~2~29~0~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 170.1417 | 170.1417
~2~29~1~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 201.1583 | 201.1583
~2~29~2~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 835.3832 | 835.3832
~2~29~20~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.3181 | 2.3181
~2~29~4~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 864.0815 | 864.0815
~2~29~3~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1683.407 | -1683.407
~2~29~5~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | -0.96554 | -0.96554
~2~29~10~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 874.6553 | 874.6553
~2~29~11~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.4198 | 4.4198
~2~29~12~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.6763 | 0.6763
~2~29~13~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.0001366 | 0.0001366
~2~30~0~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Pressure | bar | 32.9265 | 32.9265
~2~30~1~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Temperature | C | 206.7609 | 206.7609
~2~30~2~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 117.5333 | 117.5333
~2~30~20~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.3919 | 2.3919
~2~30~4~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 883.5219 | 883.5219
~2~30~3~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1663.9667 | -1663.9667
~2~30~5~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Steam quality |  | -0.084517 | -0.084517
~2~30~10~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 857.8881 | 857.8881
~2~30~11~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.5226 | 4.5226
~2~30~12~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.66058 | 0.66058
~2~30~13~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00012942 | 0.00012942
~2~31~0~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Pressure | bar | 9.246 | 9.246
~2~31~1~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Temperature | C | 360.8472 | 360.8472
~2~31~2~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Mass flow | t/h | 617.8905 | 617.8905
~2~31~20~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~31~4~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~31~3~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~31~5~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Steam quality |  | 1.2016 | 1.2016
~2~31~10~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Density | kg/m^3 | 3.2092 | 3.2092
~2~31~11~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~31~12~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~31~13~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~32~0~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 30.6 | 30.6
~2~32~1~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Temperature | C | 532.3315 | 532.3315
~2~32~2~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Mass flow | t/h | 706.2162 | 706.2162
~2~32~20~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Entropy | kJ/kg-C | 7.318 | 7.318
~2~32~4~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy | kJ/kg | 3529.1628 | 3529.1628
~2~32~3~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy H* | kJ/kg | 981.6744 | 981.6744
~2~32~5~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Steam quality |  | 1.4056 | 1.4056
~2~32~10~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Density | kg/m^3 | 8.3994 | 8.3994
~2~32~11~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Specific heat | kJ/kg-C | 2.2426 | 2.2426
~2~32~12~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Thermal conductivity | W/m-C | 0.073093 | 0.073093
~2~32~13~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Dynamic viscosity | kg/m-s | 2.9971e-05 | 2.9971e-05
~2~33~0~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Pressure | bar | 30.6 | 30.6
~2~33~1~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Temperature | C | 532.3315 | 532.3315
~2~33~2~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Mass flow | t/h | 706.2162 | 706.2162
~2~33~20~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Entropy | kJ/kg-C | 7.318 | 7.318
~2~33~4~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy | kJ/kg | 3529.1628 | 3529.1628
~2~33~3~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy H* | kJ/kg | 981.6744 | 981.6744
~2~33~5~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Steam quality |  | 1.4056 | 1.4056
~2~33~10~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Density | kg/m^3 | 8.3994 | 8.3994
~2~33~11~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Specific heat | kJ/kg-C | 2.2426 | 2.2426
~2~33~12~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Thermal conductivity | W/m-C | 0.073093 | 0.073093
~2~33~13~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.9971e-05 | 2.9971e-05
~2~34~0~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 16.37 | 16.37
~2~34~1~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Temperature | C | 439.0564 | 439.0564
~2~34~2~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Mass flow | t/h | 706.2162 | 706.2162
~2~34~20~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.3505 | 7.3505
~2~34~4~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3339.0439 | 3339.0439
~2~34~3~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 791.5554 | 791.5554
~2~34~5~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Steam quality |  | 1.2827 | 1.2827
~2~34~10~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Density | kg/m^3 | 5.0683 | 5.0683
~2~34~11~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1635 | 2.1635
~2~34~12~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.060597 | 0.060597
~2~34~13~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.6065e-05 | 2.6065e-05
~2~35~0~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Pressure | bar | 16.37 | 16.37
~2~35~1~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Temperature | C | 439.0564 | 439.0564
~2~35~2~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Mass flow | t/h | 688.465 | 688.465
~2~35~20~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Entropy | kJ/kg-C | 7.3505 | 7.3505
~2~35~4~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy | kJ/kg | 3339.0439 | 3339.0439
~2~35~3~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy H* | kJ/kg | 791.5554 | 791.5554
~2~35~5~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Steam quality |  | 1.2827 | 1.2827
~2~35~10~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Density | kg/m^3 | 5.0683 | 5.0683
~2~35~11~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Specific heat | kJ/kg-C | 2.1635 | 2.1635
~2~35~12~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Thermal conductivity | W/m-C | 0.060597 | 0.060597
~2~35~13~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Dynamic viscosity | kg/m-s | 2.6065e-05 | 2.6065e-05
~2~36~0~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Pressure | bar | 16.37 | 16.37
~2~36~1~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Temperature | C | 439.0564 | 439.0564
~2~36~2~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Mass flow | t/h | 17.7512 | 17.7512
~2~36~20~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Entropy | kJ/kg-C | 7.3505 | 7.3505
~2~36~4~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy | kJ/kg | 3339.0439 | 3339.0439
~2~36~3~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy H* | kJ/kg | 791.5554 | 791.5554
~2~36~5~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Steam quality |  | 1.2827 | 1.2827
~2~36~10~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Density | kg/m^3 | 5.0683 | 5.0683
~2~36~11~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Specific heat | kJ/kg-C | 2.1635 | 2.1635
~2~36~12~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Thermal conductivity | W/m-C | 0.060597 | 0.060597
~2~36~13~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.6065e-05 | 2.6065e-05
~2~37~0~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Pressure | bar | 16.37 | 16.37
~2~37~1~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Temperature | C | 525.9728 | 525.9728
~2~37~2~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Mass flow | t/h | 7.6077 | 7.6077
~2~37~20~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Entropy | kJ/kg-C | 7.6024 | 7.6024
~2~37~4~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy | kJ/kg | 3529.1628 | 3529.1628
~2~37~3~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy H* | kJ/kg | 981.6744 | 981.6744
~2~37~5~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Steam quality |  | 1.3812 | 1.3812
~2~37~10~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Density | kg/m^3 | 4.4879 | 4.4879
~2~37~11~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Specific heat | kJ/kg-C | 2.1962 | 2.1962
~2~37~12~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Thermal conductivity | W/m-C | 0.071286 | 0.071286
~2~37~13~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.9672e-05 | 2.9672e-05
~2~38~0~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Pressure | bar | 16.37 | 16.37
~2~38~1~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Temperature | C | 465.2428 | 465.2428
~2~38~2~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Mass flow | t/h | 25.3589 | 25.3589
~2~38~20~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Entropy | kJ/kg-C | 7.4292 | 7.4292
~2~38~4~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy | kJ/kg | 3396.0796 | 3396.0796
~2~38~3~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy H* | kJ/kg | 848.5912 | 848.5912
~2~38~5~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Steam quality |  | 1.3122 | 1.3122
~2~38~10~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Density | kg/m^3 | 4.8771 | 4.8771
~2~38~11~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Specific heat | kJ/kg-C | 2.1705 | 2.1705
~2~38~12~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Thermal conductivity | W/m-C | 0.063741 | 0.063741
~2~38~13~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Dynamic viscosity | kg/m-s | 2.716e-05 | 2.716e-05
~2~39~0~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Pressure | bar | 16.049 | 16.049
~2~39~1~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Temperature | C | 181.8336 | 181.8336
~2~39~2~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 142.8921 | 142.8921
~2~39~20~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 2.1565 | 2.1565
~2~39~4~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 771.4897 | 771.4897
~2~39~3~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1775.9988 | -1775.9988
~2~39~5~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Steam quality |  | -0.045398 | -0.045398
~2~39~10~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 885.4507 | 885.4507
~2~39~11~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.412 | 4.412
~2~39~12~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.6747 | 0.6747
~2~39~13~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00014794 | 0.00014794
~2~40~0~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Pressure | bar | 10.1442 | 10.1442
~2~40~1~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Temperature | C | 175.6707 | 175.6707
~2~40~2~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Mass flow | t/h | 840.1822 | 840.1822
~2~40~20~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Entropy | kJ/kg-C | 2.0973 | 2.0973
~2~40~4~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy | kJ/kg | 744.0652 | 744.0652
~2~40~3~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy H* | kJ/kg | -1803.4232 | -1803.4232
~2~40~5~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Steam quality |  | -0.01062 | -0.01062
~2~40~10~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Density | kg/m^3 | 891.6901 | 891.6901
~2~40~11~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Specific heat | kJ/kg-C | 4.3904 | 4.3904
~2~40~12~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Thermal conductivity | W/m-C | 0.67711 | 0.67711
~2~40~13~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Dynamic viscosity | kg/m-s | 0.00015339 | 0.00015339
~2~41~0~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 9.246 | 9.246
~2~41~1~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Temperature | C | 360.8472 | 360.8472
~2~41~2~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Mass flow | t/h | 688.465 | 688.465
~2~41~20~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~41~4~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~41~3~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~41~5~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Steam quality |  | 1.2016 | 1.2016
~2~41~10~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Density | kg/m^3 | 3.2092 | 3.2092
~2~41~11~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~41~12~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~41~13~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~42~0~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Pressure | bar | 9.246 | 9.246
~2~42~1~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Temperature | C | 360.8472 | 360.8472
~2~42~2~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Mass flow | t/h | 41.6417 | 41.6417
~2~42~20~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~42~4~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~42~3~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~42~5~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Steam quality |  | 1.2016 | 1.2016
~2~42~10~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Density | kg/m^3 | 3.2092 | 3.2092
~2~42~11~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~42~12~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~42~13~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~43~0~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Pressure | bar | 9.246 | 9.246
~2~43~1~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Temperature | C | 353.8114 | 353.8114
~2~43~2~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Mass flow | t/h | 46.7826 | 46.7826
~2~43~20~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Entropy | kJ/kg-C | 7.3537 | 7.3537
~2~43~4~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy | kJ/kg | 3167.7363 | 3167.7363
~2~43~3~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy H* | kJ/kg | 620.2478 | 620.2478
~2~43~5~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Steam quality |  | 1.1943 | 1.1943
~2~43~10~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Density | kg/m^3 | 3.2475 | 3.2475
~2~43~11~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Specific heat | kJ/kg-C | 2.11 | 2.11
~2~43~12~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Thermal conductivity | W/m-C | 0.050189 | 0.050189
~2~43~13~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Dynamic viscosity | kg/m-s | 2.2491e-05 | 2.2491e-05
~2~44~0~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Pressure | bar | 173.5446 | 173.5446
~2~44~1~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Temperature | C | 179.3151 | 179.3151
~2~44~2~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Mass flow | t/h | 840.1822 | 840.1822
~2~44~20~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~44~4~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~44~3~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~44~5~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Steam quality |  | -1.1281 | -1.1281
~2~44~10~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Density | kg/m^3 | 898.2387 | 898.2387
~2~44~11~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~44~12~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~44~13~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~45~0~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Pressure | bar | 33.585 | 33.585
~2~45~1~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Temperature | C | 325.0843 | 325.0843
~2~45~2~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Mass flow | t/h | 5.141 | 5.141
~2~45~20~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Entropy | kJ/kg-C | 6.5833 | 6.5833
~2~45~4~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy | kJ/kg | 3047.1497 | 3047.1497
~2~45~3~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy H* | kJ/kg | 499.661 | 499.661
~2~45~5~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Steam quality |  | 1.1383 | 1.1383
~2~45~10~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Density | kg/m^3 | 13.1426 | 13.1426
~2~45~11~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Specific heat | kJ/kg-C | 2.5109 | 2.5109
~2~45~12~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Thermal conductivity | W/m-C | 0.050457 | 0.050457
~2~45~13~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.1115e-05 | 2.1115e-05
~2~46~0~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Pressure | bar | 30.6 | 30.6
~2~46~1~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Temperature | C | 475.6206 | 475.6206
~2~46~2~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~46~20~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Entropy | kJ/kg-C | 7.1537 | 7.1537
~2~46~4~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~46~3~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~46~5~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Steam quality |  | 1.3343 | 1.3343
~2~46~10~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Density | kg/m^3 | 9.0994 | 9.0994
~2~46~11~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Specific heat | kJ/kg-C | 2.2323 | 2.2323
~2~46~12~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Thermal conductivity | W/m-C | 0.066118 | 0.066118
~2~46~13~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.761e-05 | 2.761e-05
~2~47~0~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 54.9755 | 54.9755
~2~47~1~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 382.0591 | 382.0591
~2~47~2~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 56.1408 | 56.1408
~2~47~20~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 6.5254 | 6.5254
~2~47~4~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 3141.9241 | 3141.9241
~2~47~3~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | 594.4355 | 594.4355
~2~47~5~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | 1.2194 | 1.2194
~2~47~10~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 19.8901 | 19.8901
~2~47~11~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 2.5663 | 2.5663
~2~47~12~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.058529 | 0.058529
~2~47~13~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 2.3593e-05 | 2.3593e-05
~2~48~0~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Pressure | bar | 33.585 | 33.585
~2~48~1~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Temperature | C | 477.2355 | 477.2355
~2~48~2~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~48~20~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Entropy | kJ/kg-C | 7.112 | 7.112
~2~48~4~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~48~3~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~48~5~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Steam quality |  | 1.3392 | 1.3392
~2~48~10~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Density | kg/m^3 | 9.9904 | 9.9904
~2~48~11~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Specific heat | kJ/kg-C | 2.2451 | 2.2451
~2~48~12~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Thermal conductivity | W/m-C | 0.066555 | 0.066555
~2~48~13~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Dynamic viscosity | kg/m-s | 2.7683e-05 | 2.7683e-05
~2~49~0~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 16.049 | 16.049
~2~49~1~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 464.6011 | 464.6011
~2~49~2~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 25.3589 | 25.3589
~2~49~20~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 7.4368 | 7.4368
~2~49~4~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 3395.0796 | 3395.0796
~2~49~3~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | 847.5912 | 847.5912
~2~49~5~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | 1.3114 | 1.3114
~2~49~10~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 4.7844 | 4.7844
~2~49~11~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 2.169 | 2.169
~2~49~12~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.063639 | 0.063639
~2~49~13~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 2.7133e-05 | 2.7133e-05
~2~50~0~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~50~1~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~50~2~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Mass flow | t/h | 28.9328 | 28.9328
~2~50~20~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Entropy | kJ/kg-C | 7.718 | 7.718
~2~50~4~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy | kJ/kg | 2442.9553 | 2442.9553
~2~50~3~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy H* | kJ/kg | -104.5332 | -104.5332
~2~50~5~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Steam quality |  | 0.94148 | 0.94148
~2~50~10~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Density | kg/m^3 | 0.070699 | 0.070699
~2~50~11~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~50~12~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~50~13~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~51~0~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Pressure | bar | 3.642 | 3.642
~2~51~1~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Temperature | C | 247.8567 | 247.8567
~2~51~2~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Mass flow | t/h | 617.8905 | 617.8905
~2~51~20~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.4171 | 7.4171
~2~51~4~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2961.3867 | 2961.3867
~2~51~3~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | 413.8981 | 413.8981
~2~51~5~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Steam quality |  | 1.1062 | 1.1062
~2~51~10~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Density | kg/m^3 | 1.5344 | 1.5344
~2~51~11~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 2.0534 | 2.0534
~2~51~12~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.038437 | 0.038437
~2~51~13~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.8094e-05 | 1.8094e-05
~2~52~0~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Pressure | bar | 30.6 | 30.6
~2~52~1~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Temperature | C | 532.3315 | 532.3315
~2~52~2~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Mass flow | t/h | 713.8239 | 713.8239
~2~52~20~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Entropy | kJ/kg-C | 7.318 | 7.318
~2~52~4~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy | kJ/kg | 3529.1628 | 3529.1628
~2~52~3~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy H* | kJ/kg | 981.6744 | 981.6744
~2~52~5~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Steam quality |  | 1.4056 | 1.4056
~2~52~10~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Density | kg/m^3 | 8.3994 | 8.3994
~2~52~11~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Specific heat | kJ/kg-C | 2.2426 | 2.2426
~2~52~12~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Thermal conductivity | W/m-C | 0.073093 | 0.073093
~2~52~13~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Dynamic viscosity | kg/m-s | 2.9971e-05 | 2.9971e-05
~2~53~0~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 160.3127 | 160.3127
~2~53~1~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 317.0161 | 317.0161
~2~53~2~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 835.3832 | 835.3832
~2~53~20~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 3.3897 | 3.3897
~2~53~4~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 1433.7714 | 1433.7714
~2~53~3~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | -1113.7172 | -1113.7172
~2~53~5~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Steam quality |  | -0.23377 | -0.23377
~2~53~10~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 689.3078 | 689.3078
~2~53~11~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Specific heat | kJ/kg-C | 5.9917 | 5.9917
~2~53~12~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Thermal conductivity | W/m-C | 0.52727 | 0.52727
~2~53~13~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dynamic viscosity | kg/m-s | 8.1939e-05 | 8.1939e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 160.3127 | 160.3127
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 347.5211 | 347.5211
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 833.2999 | 833.2999
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.2444 | 5.2444
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2579.814 | 2579.814
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 32.3255 | 32.3255
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 107.7781 | 107.7781
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 15.6035 | 15.6035
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.12779 | 0.12779
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.3401e-05 | 2.3401e-05
~2~55~0~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 158.7254 | 158.7254
~2~55~1~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 420.0035 | 420.0035
~2~55~2~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 833.2999 | 833.2999
~2~55~20~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 5.9471 | 5.9471
~2~55~4~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 3033.8652 | 3033.8652
~2~55~3~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | 486.3768 | 486.3768
~2~55~5~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | 1.4776 | 1.4776
~2~55~10~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 63.9111 | 63.9111
~2~55~11~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 3.8374 | 3.8374
~2~55~12~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.080782 | 0.080782
~2~55~13~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 2.5902e-05 | 2.5902e-05
~2~56~0~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 155.5979 | 155.5979
~2~56~1~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 514.9985 | 514.9985
~2~56~2~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 838.0318 | 838.0318
~2~56~20~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.3791 | 6.3791
~2~56~4~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3346.7295 | 3346.7295
~2~56~3~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 799.2411 | 799.2411
~2~56~5~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.7819 | 1.7819
~2~56~10~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 48.5413 | 48.5413
~2~56~11~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.8207 | 2.8207
~2~56~12~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.083396 | 0.083396
~2~56~13~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.9967e-05 | 2.9967e-05
~2~57~0~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Pressure | bar | 1.38 | 1.38
~2~57~1~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Temperature | C | 148.594 | 148.594
~2~57~2~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Mass flow | t/h | 583.5057 | 583.5057
~2~57~20~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Entropy | kJ/kg-C | 7.4541 | 7.4541
~2~57~4~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy | kJ/kg | 2770.9521 | 2770.9521
~2~57~3~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy H* | kJ/kg | 223.4636 | 223.4636
~2~57~5~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Steam quality |  | 1.0366 | 1.0366
~2~57~10~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Density | kg/m^3 | 0.71743 | 0.71743
~2~57~11~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Specific heat | kJ/kg-C | 2.0168 | 2.0168
~2~57~12~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Thermal conductivity | W/m-C | 0.028824 | 0.028824
~2~57~13~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Dynamic viscosity | kg/m-s | 1.412e-05 | 1.412e-05
~2~58~0~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Pressure | bar | 0.78 | 0.78
~2~58~1~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Temperature | C | 98.7738 | 98.7738
~2~58~2~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Mass flow | t/h | 564.0204 | 564.0204
~2~58~20~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Entropy | kJ/kg-C | 7.4754 | 7.4754
~2~58~4~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy | kJ/kg | 2676.2583 | 2676.2583
~2~58~3~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy H* | kJ/kg | 128.7697 | 128.7697
~2~58~5~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Steam quality |  | 1.0054 | 1.0054
~2~58~10~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Density | kg/m^3 | 0.45992 | 0.45992
~2~58~11~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Specific heat | kJ/kg-C | 1.9959 | 1.9959
~2~58~12~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Thermal conductivity | W/m-C | 0.024534 | 0.024534
~2~58~13~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Dynamic viscosity | kg/m-s | 1.2252e-05 | 1.2252e-05
~2~59~0~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Pressure | bar | 3.642 | 3.642
~2~59~1~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Temperature | C | 247.8567 | 247.8567
~2~59~2~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Mass flow | t/h | 34.3848 | 34.3848
~2~59~20~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Entropy | kJ/kg-C | 7.4171 | 7.4171
~2~59~4~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy | kJ/kg | 2961.3867 | 2961.3867
~2~59~3~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy H* | kJ/kg | 413.8981 | 413.8981
~2~59~5~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Steam quality |  | 1.1062 | 1.1062
~2~59~10~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Density | kg/m^3 | 1.5344 | 1.5344
~2~59~11~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Specific heat | kJ/kg-C | 2.0534 | 2.0534
~2~59~12~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Thermal conductivity | W/m-C | 0.038437 | 0.038437
~2~59~13~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Dynamic viscosity | kg/m-s | 1.8094e-05 | 1.8094e-05
~2~60~0~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Pressure | bar | 3.642 | 3.642
~2~60~1~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Temperature | C | 247.8567 | 247.8567
~2~60~2~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Mass flow | t/h | 583.5057 | 583.5057
~2~60~20~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Entropy | kJ/kg-C | 7.4171 | 7.4171
~2~60~4~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy | kJ/kg | 2961.3867 | 2961.3867
~2~60~3~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy H* | kJ/kg | 413.8981 | 413.8981
~2~60~5~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Steam quality |  | 1.1062 | 1.1062
~2~60~10~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Density | kg/m^3 | 1.5344 | 1.5344
~2~60~11~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Specific heat | kJ/kg-C | 2.0534 | 2.0534
~2~60~12~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Thermal conductivity | W/m-C | 0.038437 | 0.038437
~2~60~13~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Dynamic viscosity | kg/m-s | 1.8094e-05 | 1.8094e-05
~2~61~0~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Pressure | bar | 1.38 | 1.38
~2~61~1~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Temperature | C | 148.594 | 148.594
~2~61~2~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Mass flow | t/h | 19.4853 | 19.4853
~2~61~20~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Entropy | kJ/kg-C | 7.4541 | 7.4541
~2~61~4~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy | kJ/kg | 2770.9521 | 2770.9521
~2~61~3~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy H* | kJ/kg | 223.4636 | 223.4636
~2~61~5~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Steam quality |  | 1.0366 | 1.0366
~2~61~10~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Density | kg/m^3 | 0.71743 | 0.71743
~2~61~11~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Specific heat | kJ/kg-C | 2.0168 | 2.0168
~2~61~12~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Thermal conductivity | W/m-C | 0.028824 | 0.028824
~2~61~13~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Dynamic viscosity | kg/m-s | 1.412e-05 | 1.412e-05
~2~62~0~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Pressure | bar | 1.38 | 1.38
~2~62~1~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Temperature | C | 148.594 | 148.594
~2~62~2~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Mass flow | t/h | 564.0204 | 564.0204
~2~62~20~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Entropy | kJ/kg-C | 7.4541 | 7.4541
~2~62~4~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy | kJ/kg | 2770.9521 | 2770.9521
~2~62~3~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy H* | kJ/kg | 223.4636 | 223.4636
~2~62~5~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Steam quality |  | 1.0366 | 1.0366
~2~62~10~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Density | kg/m^3 | 0.71743 | 0.71743
~2~62~11~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Specific heat | kJ/kg-C | 2.0168 | 2.0168
~2~62~12~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Thermal conductivity | W/m-C | 0.028824 | 0.028824
~2~62~13~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Dynamic viscosity | kg/m-s | 1.412e-05 | 1.412e-05
~2~63~0~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Pressure | bar | 0.283 | 0.283
~2~63~1~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Temperature | C | 67.7608 | 67.7608
~2~63~2~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Mass flow | t/h | 540.3494 | 540.3494
~2~63~20~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Entropy | kJ/kg-C | 7.5135 | 7.5135
~2~63~4~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy | kJ/kg | 2528.8608 | 2528.8608
~2~63~3~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy H* | kJ/kg | -18.6277 | -18.6277
~2~63~5~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Steam quality |  | 0.96006 | 0.96006
~2~63~10~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Density | kg/m^3 | 0.18862 | 0.18862
~2~63~11~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~63~12~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~63~13~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~64~0~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Pressure | bar | 0.78 | 0.78
~2~64~1~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Temperature | C | 98.7738 | 98.7738
~2~64~2~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Mass flow | t/h | 23.6711 | 23.6711
~2~64~20~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Entropy | kJ/kg-C | 7.4754 | 7.4754
~2~64~4~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy | kJ/kg | 2676.2583 | 2676.2583
~2~64~3~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy H* | kJ/kg | 128.7697 | 128.7697
~2~64~5~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Steam quality |  | 1.0054 | 1.0054
~2~64~10~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Density | kg/m^3 | 0.45992 | 0.45992
~2~64~11~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Specific heat | kJ/kg-C | 1.9959 | 1.9959
~2~64~12~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Thermal conductivity | W/m-C | 0.024534 | 0.024534
~2~64~13~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Dynamic viscosity | kg/m-s | 1.2252e-05 | 1.2252e-05
~2~65~0~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Pressure | bar | 0.283 | 0.283
~2~65~1~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Temperature | C | 67.7608 | 67.7608
~2~65~2~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Mass flow | t/h | 16.3942 | 16.3942
~2~65~20~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Entropy | kJ/kg-C | 7.5135 | 7.5135
~2~65~4~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy | kJ/kg | 2528.8608 | 2528.8608
~2~65~3~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy H* | kJ/kg | -18.6277 | -18.6277
~2~65~5~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Steam quality |  | 0.96006 | 0.96006
~2~65~10~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Density | kg/m^3 | 0.18862 | 0.18862
~2~65~11~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~65~12~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~65~13~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~66~0~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Pressure | bar | 0.78 | 0.78
~2~66~1~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Temperature | C | 98.7738 | 98.7738
~2~66~2~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Mass flow | t/h | 540.3494 | 540.3494
~2~66~20~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Entropy | kJ/kg-C | 7.4754 | 7.4754
~2~66~4~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy | kJ/kg | 2676.2583 | 2676.2583
~2~66~3~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy H* | kJ/kg | 128.7697 | 128.7697
~2~66~5~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Steam quality |  | 1.0054 | 1.0054
~2~66~10~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Density | kg/m^3 | 0.45992 | 0.45992
~2~66~11~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Specific heat | kJ/kg-C | 1.9959 | 1.9959
~2~66~12~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Thermal conductivity | W/m-C | 0.024534 | 0.024534
~2~66~13~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Dynamic viscosity | kg/m-s | 1.2252e-05 | 1.2252e-05
~2~67~0~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~67~1~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~67~2~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 524.2274 | 524.2274
~2~67~20~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.6584 | 7.6584
~2~67~4~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2423.9685 | 2423.9685
~2~67~3~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | -123.5199 | -123.5199
~2~67~5~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Steam quality |  | 0.93355 | 0.93355
~2~67~10~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 0.071299 | 0.071299
~2~67~11~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~67~12~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~67~13~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~68~0~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~68~1~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Temperature | C | 27.3223 | 27.3223
~2~68~2~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Mass flow | t/h | 14812.7949 | 14812.7949
~2~68~20~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~68~4~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~68~3~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~68~5~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Steam quality |  | -0.13493 | -0.13493
~2~68~10~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Density | kg/m^3 | 996.4656 | 996.4656
~2~68~11~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~68~12~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~68~13~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~69~0~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Pressure | bar | 3.5 | 3.5
~2~69~1~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Temperature | C | 37.3673 | 37.3673
~2~69~2~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Mass flow | t/h | 29625.5898 | 29625.5898
~2~69~20~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Entropy | kJ/kg-C | 0.53702 | 0.53702
~2~69~4~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy | kJ/kg | 156.774 | 156.774
~2~69~3~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy H* | kJ/kg | -2390.7146 | -2390.7146
~2~69~5~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Steam quality |  | -0.19907 | -0.19907
~2~69~10~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Density | kg/m^3 | 993.3504 | 993.3504
~2~69~11~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Specific heat | kJ/kg-C | 4.1775 | 4.1775
~2~69~12~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Thermal conductivity | W/m-C | 0.62587 | 0.62587
~2~69~13~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Dynamic viscosity | kg/m-s | 0.00068574 | 0.00068574
~2~70~0~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Pressure | bar | 0.283 | 0.283
~2~70~1~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Temperature | C | 67.7608 | 67.7608
~2~70~2~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Mass flow | t/h | 523.9552 | 523.9552
~2~70~20~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Entropy | kJ/kg-C | 7.5135 | 7.5135
~2~70~4~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy | kJ/kg | 2528.8608 | 2528.8608
~2~70~3~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy H* | kJ/kg | -18.6277 | -18.6277
~2~70~5~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Steam quality |  | 0.96006 | 0.96006
~2~70~10~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Density | kg/m^3 | 0.18862 | 0.18862
~2~70~11~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~70~12~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~70~13~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~71~0~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Temperature | C | 48.6109 | 48.6109
~2~71~2~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Mass flow | t/h | 93.9353 | 93.9353
~2~71~20~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Entropy | kJ/kg-C | 0.68579 | 0.68579
~2~71~4~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy | kJ/kg | 203.4898 | 203.4898
~2~71~3~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy H* | kJ/kg | -2343.9988 | -2343.9988
~2~71~5~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Steam quality |  | -0.015206 | -0.015206
~2~71~10~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Density | kg/m^3 | 988.6699 | 988.6699
~2~71~11~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~71~12~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Thermal conductivity | W/m-C | 0.63946 | 0.63946
~2~71~13~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00055933 | 0.00055933
~2~72~0~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 11.0866 | 11.0866
~2~72~1~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 45.798 | 45.798
~2~72~2~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 650.5074 | 650.5074
~2~72~20~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.64862 | 0.64862
~2~72~4~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 192.6851 | 192.6851
~2~72~3~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2354.8035 | -2354.8035
~2~72~5~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.29529 | -0.29529
~2~72~10~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 990.3632 | 990.3632
~2~72~11~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1771 | 4.1771
~2~72~12~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.63678 | 0.63678
~2~72~13~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00058726 | 0.00058726
~2~73~0~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Pressure | bar | 0.45641 | 0.45641
~2~73~1~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Temperature | C | 45.247 | 45.247
~2~73~2~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Mass flow | t/h | 650.5074 | 650.5074
~2~73~20~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Entropy | kJ/kg-C | 0.64185 | 0.64185
~2~73~4~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy | kJ/kg | 189.4477 | 189.4477
~2~73~3~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy H* | kJ/kg | -2358.0408 | -2358.0408
~2~73~5~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Steam quality |  | -0.06127 | -0.06127
~2~73~10~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Density | kg/m^3 | 990.1331 | 990.1331
~2~73~11~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~73~12~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Thermal conductivity | W/m-C | 0.63558 | 0.63558
~2~73~13~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Dynamic viscosity | kg/m-s | 0.00059284 | 0.00059284
~2~74~0~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.175 | 0.175
~2~74~1~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 48.6479 | 48.6479
~2~74~2~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 94.3428 | 94.3428
~2~74~20~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.68627 | 0.68627
~2~74~4~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 203.6446 | 203.6446
~2~74~3~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2343.844 | -2343.844
~2~74~5~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.01514 | -0.01514
~2~74~10~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 988.6534 | 988.6534
~2~74~11~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~74~12~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.6395 | 0.6395
~2~74~13~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.00055898 | 0.00055898
~2~75~0~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~75~1~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Temperature | C | 57.2007 | 57.2007
~2~75~2~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Mass flow | t/h | 0.40748 | 0.40748
~2~75~20~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~75~4~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~75~3~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~75~5~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~75~10~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Density | kg/m^3 | 984.2903 | 984.2903
~2~75~11~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~75~12~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~75~13~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~76~0~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.0975 | 0.0975
~2~76~1~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 45.3132 | 45.3132
~2~76~2~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 553.8749 | 553.8749
~2~76~20~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 7.664 | 7.664
~2~76~4~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 2425.7646 | 2425.7646
~2~76~3~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -121.7238 | -121.7238
~2~76~5~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | 0.9343 | 0.9343
~2~76~10~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 0.071242 | 0.071242
~2~76~11~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~76~12~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~76~13~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~78~0~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 10.8692 | 10.8692
~2~78~1~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 61.7129 | 61.7129
~2~78~2~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 650.5074 | 650.5074
~2~78~20~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 0.85209 | 0.85209
~2~78~4~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 259.2017 | 259.2017
~2~78~3~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2288.2869 | -2288.2869
~2~78~5~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.25965 | -0.25965
~2~78~10~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 982.7878 | 982.7878
~2~78~11~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.183 | 4.183
~2~78~12~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.65348 | 0.65348
~2~78~13~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.00045481 | 0.00045481
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.70449 | 0.70449
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Temperature | C | 64.5155 | 64.5155
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 77.5411 | 77.5411
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.88752 | 0.88752
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 270.0786 | 270.0786
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2277.4099 | -2277.4099
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.047019 | -0.047019
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 980.8521 | 980.8521
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1866 | 4.1866
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.6555 | 0.6555
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00043641 | 0.00043641
~2~80~0~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 10.6561 | 10.6561
~2~80~1~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 84.4978 | 84.4978
~2~80~2~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 650.5074 | 650.5074
~2~80~20~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.1278 | 1.1278
~2~80~4~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 354.6382 | 354.6382
~2~80~3~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2192.8503 | -2192.8503
~2~80~5~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.2097 | -0.2097
~2~80~10~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 969.4186 | 969.4186
~2~80~11~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.1976 | 4.1976
~2~80~12~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.67094 | 0.67094
~2~80~13~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.00033609 | 0.00033609
~2~81~0~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Pressure | bar | 1.3529 | 1.3529
~2~81~1~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Temperature | C | 87.2968 | 87.2968
~2~81~2~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 53.8701 | 53.8701
~2~81~20~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 1.1612 | 1.1612
~2~81~4~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 365.6601 | 365.6601
~2~81~3~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2181.8284 | -2181.8284
~2~81~5~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.039577 | -0.039577
~2~81~10~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 967.1719 | 967.1719
~2~81~11~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.2021 | 4.2021
~2~81~12~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.67209 | 0.67209
~2~81~13~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.00032491 | 0.00032491
~2~82~0~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 10.4472 | 10.4472
~2~82~1~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 102.5831 | 102.5831
~2~82~2~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 650.5074 | 650.5074
~2~82~20~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 1.3354 | 1.3354
~2~82~4~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 430.6918 | 430.6918
~2~82~3~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | -2116.7966 | -2116.7966
~2~82~5~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | -0.16957 | -0.16957
~2~82~10~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 956.961 | 956.961
~2~82~11~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 4.2164 | 4.2164
~2~82~12~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.67986 | 0.67986
~2~82~13~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 0.00027492 | 0.00027492
~2~84~0~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Pressure | bar | 3.5706 | 3.5706
~2~84~1~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Temperature | C | 105.3864 | 105.3864
~2~84~2~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 34.3848 | 34.3848
~2~84~20~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.3673 | 1.3673
~2~84~4~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 442.0053 | 442.0053
~2~84~3~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2105.4832 | -2105.4832
~2~84~5~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.067731 | -0.067731
~2~84~10~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 954.5691 | 954.5691
~2~84~11~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.2216 | 4.2216
~2~84~12~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.68049 | 0.68049
~2~84~13~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.00026699 | 0.00026699
~2~85~0~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 3.5706 | 3.5706
~2~85~1~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 247.248 | 247.248
~2~85~2~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 34.3848 | 34.3848
~2~85~20~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 7.4242 | 7.4242
~2~85~4~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 2960.3867 | 2960.3867
~2~85~3~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | 412.8981 | 412.8981
~2~85~5~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | 1.106 | 1.106
~2~85~10~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 1.5058 | 1.5058
~2~85~11~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 2.0518 | 2.0518
~2~85~12~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.038366 | 0.038366
~2~85~13~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 1.807e-05 | 1.807e-05
~2~86~0~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 1.3529 | 1.3529
~2~86~1~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 147.9962 | 147.9962
~2~86~2~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 19.4853 | 19.4853
~2~86~20~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 7.4608 | 7.4608
~2~86~4~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 2769.9521 | 2769.9521
~2~86~3~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | 222.4636 | 222.4636
~2~86~5~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | 1.0365 | 1.0365
~2~86~10~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 0.70424 | 0.70424
~2~86~11~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 2.0151 | 2.0151
~2~86~12~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.028764 | 0.028764
~2~86~13~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 1.4098e-05 | 1.4098e-05
~2~87~0~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 0.76471 | 0.76471
~2~87~1~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 98.1786 | 98.1786
~2~87~2~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 23.6711 | 23.6711
~2~87~20~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 7.4818 | 7.4818
~2~87~4~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 2675.2583 | 2675.2583
~2~87~3~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | 127.7697 | 127.7697
~2~87~5~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | 1.0053 | 1.0053
~2~87~10~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 0.45156 | 0.45156
~2~87~11~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 1.9943 | 1.9943
~2~87~12~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.024478 | 0.024478
~2~87~13~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 1.2231e-05 | 1.2231e-05
~2~88~0~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.27745 | 0.27745
~2~88~1~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 67.3104 | 67.3104
~2~88~2~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 16.3942 | 16.3942
~2~88~20~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 7.5193 | 7.5193
~2~88~4~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 2527.8608 | 2527.8608
~2~88~3~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -19.6277 | -19.6277
~2~88~5~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | 0.95998 | 0.95998
~2~88~10~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 0.18516 | 0.18516
~2~88~11~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1881 | 4.1881
~2~88~12~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.021747 | 0.021747
~2~88~13~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 1.1177e-05 | 1.1177e-05
~2~99~0~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 33.585 | 33.585
~2~99~1~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 324.9984 | 324.9984
~2~99~2~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 713.8239 | 713.8239
~2~99~20~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 6.5829 | 6.5829
~2~99~4~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 3046.9353 | 3046.9353
~2~99~3~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy H* | kJ/kg | 499.4466 | 499.4466
~2~99~5~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Steam quality |  | 1.1382 | 1.1382
~2~99~10~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 13.1451 | 13.1451
~2~99~11~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Specific heat | kJ/kg-C | 2.5114 | 2.5114
~2~99~12~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Thermal conductivity | W/m-C | 0.05045 | 0.05045
~2~99~13~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dynamic viscosity | kg/m-s | 2.1111e-05 | 2.1111e-05
~2~100~0~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 33.2525 | 33.2525
~2~100~1~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 511.0024 | 511.0024
~2~100~2~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 713.8239 | 713.8239
~2~100~20~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 7.2165 | 7.2165
~2~100~4~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 3478.2825 | 3478.2825
~2~100~3~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy H* | kJ/kg | 930.7939 | 930.7939
~2~100~5~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Steam quality |  | 1.382 | 1.382
~2~100~10~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 9.4168 | 9.4168
~2~100~11~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Specific heat | kJ/kg-C | 2.2461 | 2.2461
~2~100~12~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Thermal conductivity | W/m-C | 0.070633 | 0.070633
~2~100~13~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dynamic viscosity | kg/m-s | 2.9095e-05 | 2.9095e-05
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 158.7254 | 158.7254
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 418.0032 | 418.0032
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 836.1783 | 836.1783
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 5.9358 | 5.9358
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 3026.0681 | 3026.0681
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy H* | kJ/kg | 478.5795 | 478.5795
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Steam quality |  | 1.4693 | 1.4693
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 64.3772 | 64.3772
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Specific heat | kJ/kg-C | 3.8844 | 3.8844
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Thermal conductivity | W/m-C | 0.080915 | 0.080915
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dynamic viscosity | kg/m-s | 2.5816e-05 | 2.5816e-05
~2~102~0~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 157.1539 | 157.1539
~2~102~1~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 489.997 | 489.997
~2~102~2~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 836.1783 | 836.1783
~2~102~20~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 6.278 | 6.278
~2~102~4~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 3271.4119 | 3271.4119
~2~102~3~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy H* | kJ/kg | 723.9235 | 723.9235
~2~102~5~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Steam quality |  | 1.7166 | 1.7166
~2~102~10~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 51.822 | 51.822
~2~102~11~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Specific heat | kJ/kg-C | 2.9635 | 2.9635
~2~102~12~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Thermal conductivity | W/m-C | 0.081752 | 0.081752
~2~102~13~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dynamic viscosity | kg/m-s | 2.8914e-05 | 2.8914e-05
~2~103~0~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Pressure | bar | 9.0647 | 9.0647
~2~103~1~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Temperature | C | 353.1704 | 353.1704
~2~103~2~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 46.7826 | 46.7826
~2~103~20~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 7.3611 | 7.3611
~2~103~4~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 3166.7363 | 3166.7363
~2~103~3~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | 619.2479 | 619.2479
~2~103~5~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Steam quality |  | 1.1939 | 1.1939
~2~103~10~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 3.1862 | 3.1862
~2~103~11~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 2.1083 | 2.1083
~2~103~12~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.0501 | 0.0501
~2~103~13~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 2.2465e-05 | 2.2465e-05
~2~104~0~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 173.5446 | 173.5446
~2~104~1~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 179.3151 | 179.3151
~2~104~2~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 2.8783 | 2.8783
~2~104~20~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~104~4~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~104~3~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~104~5~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | -1.1281 | -1.1281
~2~104~10~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 898.2387 | 898.2387
~2~104~11~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~104~12~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~104~13~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~105~0~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 173.5446 | 173.5446
~2~105~1~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 179.3151 | 179.3151
~2~105~2~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 1.8535 | 1.8535
~2~105~20~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~105~4~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~105~3~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~105~5~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | -1.1281 | -1.1281
~2~105~10~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 898.2387 | 898.2387
~2~105~11~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~105~12~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~105~13~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~106~0~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 173.5446 | 173.5446
~2~106~1~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 179.3151 | 179.3151
~2~106~2~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 835.3832 | 835.3832
~2~106~20~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~106~4~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~106~3~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~106~5~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | -1.1281 | -1.1281
~2~106~10~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 898.2387 | 898.2387
~2~106~11~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~106~12~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~106~13~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~107~0~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Pressure | bar | 173.5446 | 173.5446
~2~107~1~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Temperature | C | 179.3151 | 179.3151
~2~107~2~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Mass flow | t/h | 4.7318 | 4.7318
~2~107~20~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~107~4~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~107~3~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~107~5~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Steam quality |  | -1.1281 | -1.1281
~2~107~10~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Density | kg/m^3 | 898.2387 | 898.2387
~2~107~11~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~107~12~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~107~13~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~108~0~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 173.5446 | 173.5446
~2~108~1~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 179.3151 | 179.3151
~2~108~2~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 0.067146 | 0.067146
~2~108~20~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~108~4~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 768.6778 | 768.6778
~2~108~3~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | -1778.8108 | -1778.8108
~2~108~5~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | -1.1281 | -1.1281
~2~108~10~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 898.2387 | 898.2387
~2~108~11~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~108~12~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~108~13~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Pressure | bar | 154.0573 | 154.0573
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Temperature | C | 534.4016 | 534.4016
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Mass flow | t/h | 838.0318 | 838.0318
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Entropy | kJ/kg-C | 6.454 | 6.454
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy | kJ/kg | 3403.2319 | 3403.2319
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy H* | kJ/kg | 855.7435 | 855.7435
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Steam quality |  | 1.8266 | 1.8266
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Density | kg/m^3 | 46.2038 | 46.2038
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Specific heat | kJ/kg-C | 2.7393 | 2.7393
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Thermal conductivity | W/m-C | 0.084899 | 0.084899
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Dynamic viscosity | kg/m-s | 3.0775e-05 | 3.0775e-05
~2~111~0~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Pressure | bar | 30.906 | 30.906
~2~111~1~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Temperature | C | 533.22 | 533.22
~2~111~2~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Mass flow | t/h | 713.8239 | 713.8239
~2~111~20~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Entropy | kJ/kg-C | 7.3157 | 7.3157
~2~111~4~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy | kJ/kg | 3530.863 | 3530.863
~2~111~3~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy H* | kJ/kg | 983.3745 | 983.3745
~2~111~5~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Steam quality |  | 1.4071 | 1.4071
~2~111~10~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Density | kg/m^3 | 8.475 | 8.475
~2~111~11~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Specific heat | kJ/kg-C | 2.2438 | 2.2438
~2~111~12~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Thermal conductivity | W/m-C | 0.073227 | 0.073227
~2~111~13~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Dynamic viscosity | kg/m-s | 3.0008e-05 | 3.0008e-05
~2~112~0~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 161.9158 | 161.9158
~2~112~1~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 268.2197 | 268.2197
~2~112~2~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 835.3832 | 835.3832
~2~112~20~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.9298 | 2.9298
~2~112~4~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 1173.7864 | 1173.7864
~2~112~3~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1373.7021 | -1373.7021
~2~112~5~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.52708 | -0.52708
~2~112~10~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 784.8233 | 784.8233
~2~112~11~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.9034 | 4.9034
~2~112~12~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.611 | 0.611
~2~112~13~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00010126 | 0.00010126
~2~115~0~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 155.5979 | 155.5979
~2~115~1~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 516.9989 | 516.9989
~2~115~2~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 836.1783 | 836.1783
~2~115~20~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 6.3863 | 6.3863
~2~115~4~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 3352.4443 | 3352.4443
~2~115~3~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | 804.9557 | 804.9557
~2~115~5~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | 1.7878 | 1.7878
~2~115~10~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 48.3445 | 48.3445
~2~115~11~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 2.8121 | 2.8121
~2~115~12~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.083562 | 0.083562
~2~115~13~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 3.0052e-05 | 3.0052e-05
~2~117~0~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Pressure | bar | 33.585 | 33.585
~2~117~1~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Temperature | C | 477.2355 | 477.2355
~2~117~2~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~117~20~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Entropy | kJ/kg-C | 7.112 | 7.112
~2~117~4~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~117~3~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~117~5~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Steam quality |  | 1.3392 | 1.3392
~2~117~10~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Density | kg/m^3 | 9.9904 | 9.9904
~2~117~11~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Specific heat | kJ/kg-C | 2.2451 | 2.2451
~2~117~12~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Thermal conductivity | W/m-C | 0.066555 | 0.066555
~2~117~13~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.7683e-05 | 2.7683e-05
~2~118~0~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Pressure | bar | 30.6 | 30.6
~2~118~1~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Temperature | C | 475.6206 | 475.6206
~2~118~2~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~118~20~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Entropy | kJ/kg-C | 7.1537 | 7.1537
~2~118~4~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy | kJ/kg | 3401.532 | 3401.532
~2~118~3~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy H* | kJ/kg | 854.0434 | 854.0434
~2~118~5~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Steam quality |  | 1.3343 | 1.3343
~2~118~10~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Density | kg/m^3 | 9.0994 | 9.0994
~2~118~11~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Specific heat | kJ/kg-C | 2.2323 | 2.2323
~2~118~12~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Thermal conductivity | W/m-C | 0.066118 | 0.066118
~2~118~13~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Dynamic viscosity | kg/m-s | 2.761e-05 | 2.761e-05
~2~119~0~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~119~1~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Temperature | C | 27.3223 | 27.3223
~2~119~2~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Mass flow | t/h | 14812.7949 | 14812.7949
~2~119~20~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~119~4~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~119~3~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~119~5~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Steam quality |  | -0.13493 | -0.13493
~2~119~10~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Density | kg/m^3 | 996.4656 | 996.4656
~2~119~11~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~119~12~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~119~13~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~120~0~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Pressure | bar | 1.0135 | 1.0135
~2~120~1~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Temperature | C | 27.3223 | 27.3223
~2~120~2~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Mass flow | t/h | 29625.5898 | 29625.5898
~2~120~20~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~120~4~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~120~3~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~120~5~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Steam quality |  | -0.13493 | -0.13493
~2~120~10~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Density | kg/m^3 | 996.4656 | 996.4656
~2~120~11~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~120~12~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~120~13~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~121~0~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~121~1~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~121~2~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Mass flow | t/h | 14812.7949 | 14812.7949
~2~121~20~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~121~4~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~121~3~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~121~5~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~121~10~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~121~11~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~121~12~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~121~13~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~122~0~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~122~1~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~122~2~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Mass flow | t/h | 14812.7949 | 14812.7949
~2~122~20~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~122~4~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~122~3~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~122~5~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~122~10~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~122~11~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~122~12~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~122~13~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~123~0~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 3.8447 | 3.8447
~2~123~1~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 27.3502 | 27.3502
~2~123~2~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 29625.5898 | 29625.5898
~2~123~20~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~123~4~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~123~3~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~123~5~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.22627 | -0.22627
~2~123~10~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 996.5845 | 996.5845
~2~123~11~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~123~12~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~123~13~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~124~0~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~124~1~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~124~2~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Mass flow | t/h | 14.4332 | 14.4332
~2~124~20~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Entropy | kJ/kg-C | 7.7127 | 7.7127
~2~124~4~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy | kJ/kg | 2441.2544 | 2441.2544
~2~124~3~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy H* | kJ/kg | -106.2342 | -106.2342
~2~124~5~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Steam quality |  | 0.94077 | 0.94077
~2~124~10~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Density | kg/m^3 | 0.070752 | 0.070752
~2~124~11~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~124~12~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~124~13~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~125~0~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~125~1~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~125~2~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Mass flow | t/h | 14.4996 | 14.4996
~2~125~20~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Entropy | kJ/kg-C | 7.7233 | 7.7233
~2~125~4~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy | kJ/kg | 2444.6487 | 2444.6487
~2~125~3~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy H* | kJ/kg | -102.8399 | -102.8399
~2~125~5~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Steam quality |  | 0.94219 | 0.94219
~2~125~10~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Density | kg/m^3 | 0.070646 | 0.070646
~2~125~11~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~125~12~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~125~13~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~126~0~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 10.1442 | 10.1442
~2~126~1~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 175.6707 | 175.6707
~2~126~2~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 420.0911 | 420.0911
~2~126~20~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 2.0973 | 2.0973
~2~126~4~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 744.0652 | 744.0652
~2~126~3~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | -1803.4232 | -1803.4232
~2~126~5~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | -0.01062 | -0.01062
~2~126~10~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 891.6901 | 891.6901
~2~126~11~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 4.3904 | 4.3904
~2~126~12~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.67711 | 0.67711
~2~126~13~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 0.00015339 | 0.00015339
~2~127~0~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 10.1442 | 10.1442
~2~127~1~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 175.6707 | 175.6707
~2~127~2~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 420.0911 | 420.0911
~2~127~20~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 2.0973 | 2.0973
~2~127~4~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 744.0652 | 744.0652
~2~127~3~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | -1803.4232 | -1803.4232
~2~127~5~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | -0.01062 | -0.01062
~2~127~10~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 891.6901 | 891.6901
~2~127~11~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 4.3904 | 4.3904
~2~127~12~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.67711 | 0.67711
~2~127~13~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 0.00015339 | 0.00015339
~2~128~0~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 9.246 | 9.246
~2~128~1~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 360.8472 | 360.8472
~2~128~2~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 14.4996 | 14.4996
~2~128~20~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~128~4~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~128~3~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~128~5~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | 1.2016 | 1.2016
~2~128~10~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 3.2092 | 3.2092
~2~128~11~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~128~12~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~128~13~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~129~0~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 9.246 | 9.246
~2~129~1~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 360.8472 | 360.8472
~2~129~2~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 14.4332 | 14.4332
~2~129~20~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 7.3773 | 7.3773
~2~129~4~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 3182.6235 | 3182.6235
~2~129~3~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | 635.1351 | 635.1351
~2~129~5~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | 1.2016 | 1.2016
~2~129~10~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 3.2092 | 3.2092
~2~129~11~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 2.1097 | 2.1097
~2~129~12~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.05097 | 0.05097
~2~129~13~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 2.2788e-05 | 2.2788e-05
~2~130~0~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Pressure | bar | 173.5446 | 173.5446
~2~130~1~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Temperature | C | 179.3151 | 179.3151
~2~130~2~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Mass flow | t/h | 420.0911 | 420.0911
~2~130~20~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~130~4~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy | kJ/kg | 768.6779 | 768.6779
~2~130~3~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy H* | kJ/kg | -1778.8107 | -1778.8107
~2~130~5~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Steam quality |  | -1.1281 | -1.1281
~2~130~10~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Density | kg/m^3 | 898.2387 | 898.2387
~2~130~11~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~130~12~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~130~13~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~2~131~0~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Pressure | bar | 173.5446 | 173.5446
~2~131~1~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Temperature | C | 179.3151 | 179.3151
~2~131~2~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Mass flow | t/h | 420.0911 | 420.0911
~2~131~20~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Entropy | kJ/kg-C | 2.1114 | 2.1114
~2~131~4~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy | kJ/kg | 768.6779 | 768.6779
~2~131~3~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy H* | kJ/kg | -1778.8107 | -1778.8107
~2~131~5~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Steam quality |  | -1.1281 | -1.1281
~2~131~10~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Density | kg/m^3 | 898.2387 | 898.2387
~2~131~11~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Specific heat | kJ/kg-C | 4.3384 | 4.3384
~2~131~12~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Thermal conductivity | W/m-C | 0.68775 | 0.68775
~2~131~13~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015404 | 0.00015404
~3~77~0~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0135 | 1.0135
~3~77~1~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 30 | 30
~3~77~2~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 140.758 | 140.758
~3~77~3~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | 17296.6797 | 17296.6797
~3~77~4~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: LHV | kJ/kg | 17286.1191 | 17286.1191
~3~77~5~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HHV | kJ/kg | 18840.5996 | 18840.5996
~3~77~8~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 6.9862 | 6.9862
~3~77~6~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (LHV) | kW | 675888.125 | 675888.125
~3~77~7~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (HHV) | kW | 736668.4375 | 736668.4375
~3~77~120~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fuel LHV price | USD/GJ | 2.362 | 2.362
~3~77~20~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Ash | % | 5.36 | 5.36
~3~77~21~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Moisture | % | 27.99 | 27.99
~3~77~22~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Carbon | % | 48.63 | 48.63
~3~77~23~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Hydrogen | % | 3.99 | 3.99
~3~77~24~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Oxygen | % | 13.04 | 13.04
~3~77~25~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Nitrogen | % | 0.8 | 0.8
~3~77~26~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Sulfur | % | 0.19 | 0.19
~3~77~27~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Chlorine | % | 0 | 0
~3~77~28~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [24] - HPH-3 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,6
Note on E6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [24] - HPH-3 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,6

## ELINK
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTAW_What if_100%_RevB.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 6.9 | 6.9 | #N/A | 6.9
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 26.95 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 75.41 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 23.5477 | 23.5477 | #N/A | 23.5477
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
~31~1~7~~-27~ | Deaerator [31] - DAER : Deaerator design pressure | bar | 9.25 | 9.25 | #N/A | 9.25
~31~1~8~~-27~ | Deaerator [31] - DAER : Deaerator outlet temperature @ design | C | 176.5256 | 176.5256 | #N/A | 176.5256
~31~1~5~~-27~ | Deaerator [31] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 12 | 12 | #N/A | 12
~31~1~6~~-27~ | Deaerator [31] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 11 | 11 | #N/A | 11
~67~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Specified outlet temperature | C | 325 | 325 | #N/A | 325
~67~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Specified outlet temperature | C | 418 | 418 | #N/A | 418
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~69~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Specified outlet temperature | C | 515 | 515 | #N/A | 515
~69~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Assumed gas temperature drop | C | 1.1111 | 1.1111 | #N/A | 1.1111
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 317 | 317 | #N/A | 317
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.6181 | 99.6181 | #N/A | 99.6181
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.47992 | 0.47992 | #N/A | 0.47992
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 0 | 0 | #N/A | 0
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 38.6052 | 38.6052 | #N/A | 38.6052
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 29.6004 | 29.6004 | #N/A | 29.6004
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 615.5439 | 615.5439 | #N/A | 615.5439
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 57.2227 | 57.2227 | #N/A | 57.2227
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~66~1~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan design point overall pressure rise | millibar | 3.5334 | 3.5334 | #N/A | 3.5334
91¦~66~1~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~66~1~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~66~1~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~66~1~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~7~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~66~1~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~66~1~16~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss | kW | 1.3234 | 1.3234 | #N/A | 1.3234
91¦~66~1~13~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~66~1~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~66~1~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 296.824 | 296.824 | #N/A | 296.824
91¦~66~1~12~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 3.608 | 3.608 | #N/A | 3.608
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan design point overall pressure rise | millibar | 24.9066 | 24.9066 | #N/A | 24.9066
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss | kW | 2.5106 | 2.5106 | #N/A | 2.5106
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan off-design control damper dP | millibar | 2.0531e-06 | 2.0531e-06 | #N/A | 2.0531e-06
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal inlet volume flow for off-design fan curve | m^3/s | 80.4119 | 80.4119 | #N/A | 80.4119
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Nominal corrected pressure rise for off-design fan curve | millibar | 23.5974 | 23.5974 | #N/A | 23.5974
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~16~1~2~~-38~ | Feedwater Heater [16] - HPH-1 : Design point FW temperature @ heater exit | C | 272 | 272 | #N/A | 272
91¦~16~1~3~~-38~ | Feedwater Heater [16] - HPH-1 : Design point terminal difference | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~4~~-38~ | Feedwater Heater [16] - HPH-1 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~16~1~19~~-38~ | Feedwater Heater [16] - HPH-1 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~16~1~5~~-38~ | Feedwater Heater [16] - HPH-1 : Design point minimum pinch | C | 1.5 | 1.5 | #N/A | 1.5
91¦~16~1~6~~-38~ | Feedwater Heater [16] - HPH-1 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~16~2~2~~-38~ | Feedwater Heater [16] - HPH-1 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~16~1~16~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature @ heater exit at off-design | C | 272 | 272 | #N/A | 272
91¦~16~1~8~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~16~1~9~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~16~1~10~~-38~ | Feedwater Heater [16] - HPH-1 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~16~1~11~~-38~ | Feedwater Heater [16] - HPH-1 : Design point steam mass flow | t/h | 75.4708 | 75.4708 | #N/A | 75.4708
91¦~16~1~12~~-38~ | Feedwater Heater [16] - HPH-1 : Design point water mass flow | t/h | 1108.6648 | 1108.6648 | #N/A | 1108.6648
91¦~16~1~13~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of condensing section | kW/C | 4359.603 | 4359.603 | #N/A | 4359.603
91¦~16~1~20~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of drain cooling section | kW/C | 262.0872 | 262.0872 | #N/A | 262.0872
91¦~16~1~21~~-38~ | Feedwater Heater [16] - HPH-1 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~16~1~14~~-38~ | Feedwater Heater [16] - HPH-1 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~16~1~15~~-38~ | Feedwater Heater [16] - HPH-1 : Water-side flow resistance coefficient | m^-4 | 0.012703 | 0.012703 | #N/A | 0.012703
91¦~16~1~17~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~16~1~18~~-38~ | Feedwater Heater [16] - HPH-1 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~2~~-38~ | Feedwater Heater [17] - HPH-2 : Design point FW temperature @ heater exit | C | 242.4124 | 242.4124 | #N/A | 242.4124
91¦~17~1~3~~-38~ | Feedwater Heater [17] - HPH-2 : Design point terminal difference | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~4~~-38~ | Feedwater Heater [17] - HPH-2 : Design point drain cooler approach | C | 5.6 | 5.6 | #N/A | 5.6
91¦~17~1~19~~-38~ | Feedwater Heater [17] - HPH-2 : Design point residual superheat | C | 2.8 | 2.8 | #N/A | 2.8
91¦~17~1~5~~-38~ | Feedwater Heater [17] - HPH-2 : Design point minimum pinch | C | 0.278 | 0.278 | #N/A | 0.278
91¦~17~1~6~~-38~ | Feedwater Heater [17] - HPH-2 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~17~2~2~~-38~ | Feedwater Heater [17] - HPH-2 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~17~1~16~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature @ heater exit at off-design | C | 242.4124 | 242.4124 | #N/A | 242.4124
91¦~17~1~8~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~17~1~9~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~17~1~10~~-38~ | Feedwater Heater [17] - HPH-2 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~17~1~11~~-38~ | Feedwater Heater [17] - HPH-2 : Design point steam mass flow | t/h | 163.7123 | 163.7123 | #N/A | 163.7123
91¦~17~1~12~~-38~ | Feedwater Heater [17] - HPH-2 : Design point water mass flow | t/h | 1108.6648 | 1108.6648 | #N/A | 1108.6648
91¦~17~1~13~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of condensing section | kW/C | 6750.708 | 6750.708 | #N/A | 6750.708
91¦~17~1~20~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of drain cooling section | kW/C | 460.7218 | 460.7218 | #N/A | 460.7218
91¦~17~1~21~~-38~ | Feedwater Heater [17] - HPH-2 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~17~1~14~~-38~ | Feedwater Heater [17] - HPH-2 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~17~1~15~~-38~ | Feedwater Heater [17] - HPH-2 : Water-side flow resistance coefficient | m^-4 | 0.012957 | 0.012957 | #N/A | 0.012957
91¦~17~1~17~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~17~1~18~~-38~ | Feedwater Heater [17] - HPH-2 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~24~1~2~~-38~ | Feedwater Heater [24] - HPH-3 : Design point FW temperature @ heater exit | C | 201.67 | 201.67 | #N/A | 201.67
91¦~24~1~3~~-38~ | Feedwater Heater [24] - HPH-3 : Design point terminal difference | C | 0.38 | 0.38 | #N/A | 0.38
91¦~24~1~4~~-38~ | Feedwater Heater [24] - HPH-3 : Design point drain cooler approach | C | 2.5 | 2.5 | #N/A | 2.5
91¦~24~1~19~~-38~ | Feedwater Heater [24] - HPH-3 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~24~1~5~~-38~ | Feedwater Heater [24] - HPH-3 : Design point minimum pinch | C | 0.3 | 0.3 | #N/A | 0.3
91¦~24~1~6~~-38~ | Feedwater Heater [24] - HPH-3 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~24~2~2~~-38~ | Feedwater Heater [24] - HPH-3 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~24~1~16~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature @ heater exit at off-design | C | 201.67 | 201.67 | #N/A | 201.67
91¦~24~1~8~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~24~1~9~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~24~1~10~~-38~ | Feedwater Heater [24] - HPH-3 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~24~1~11~~-38~ | Feedwater Heater [24] - HPH-3 : Design point steam mass flow | t/h | 196.1428 | 196.1428 | #N/A | 196.1428
91¦~24~1~12~~-38~ | Feedwater Heater [24] - HPH-3 : Design point water mass flow | t/h | 1108.6648 | 1108.6648 | #N/A | 1108.6648
91¦~24~1~13~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of condensing section | kW/C | 5201.0454 | 5201.0454 | #N/A | 5201.0454
91¦~24~1~20~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of drain cooling section | kW/C | 587.6343 | 587.6343 | #N/A | 587.6343
91¦~24~1~21~~-38~ | Feedwater Heater [24] - HPH-3 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~24~1~14~~-38~ | Feedwater Heater [24] - HPH-3 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~24~1~15~~-38~ | Feedwater Heater [24] - HPH-3 : Water-side flow resistance coefficient | m^-4 | 0.013216 | 0.013216 | #N/A | 0.013216
91¦~24~1~17~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~24~1~18~~-38~ | Feedwater Heater [24] - HPH-3 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~53~1~2~~-38~ | Feedwater Heater [53] - LPH-8 : Design point FW temperature @ heater exit | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~3~~-38~ | Feedwater Heater [53] - LPH-8 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~53~1~4~~-38~ | Feedwater Heater [53] - LPH-8 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~53~1~19~~-38~ | Feedwater Heater [53] - LPH-8 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~53~1~5~~-38~ | Feedwater Heater [53] - LPH-8 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~53~1~6~~-38~ | Feedwater Heater [53] - LPH-8 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~53~2~2~~-38~ | Feedwater Heater [53] - LPH-8 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~53~1~16~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature @ heater exit at off-design | C | 61.7104 | 61.7104 | #N/A | 61.7104
91¦~53~1~8~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~53~1~9~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~53~1~10~~-38~ | Feedwater Heater [53] - LPH-8 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~53~1~11~~-38~ | Feedwater Heater [53] - LPH-8 : Design point steam mass flow | t/h | 127.8596 | 127.8596 | #N/A | 127.8596
91¦~53~1~12~~-38~ | Feedwater Heater [53] - LPH-8 : Design point water mass flow | t/h | 861.8255 | 861.8255 | #N/A | 861.8255
91¦~53~1~13~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of condensing section | kW/C | 1208.4103 | 1208.4103 | #N/A | 1208.4103
91¦~53~1~20~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of drain cooling section | kW/C | 331.5611 | 331.5611 | #N/A | 331.5611
91¦~53~1~21~~-38~ | Feedwater Heater [53] - LPH-8 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~53~1~14~~-38~ | Feedwater Heater [53] - LPH-8 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~53~1~15~~-38~ | Feedwater Heater [53] - LPH-8 : Water-side flow resistance coefficient | m^-4 | 0.0013352 | 0.0013352 | #N/A | 0.0013352
91¦~53~1~17~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~53~1~18~~-38~ | Feedwater Heater [53] - LPH-8 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~54~1~2~~-38~ | Feedwater Heater [54] - LPH-7 : Design point FW temperature @ heater exit | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~3~~-38~ | Feedwater Heater [54] - LPH-7 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~54~1~4~~-38~ | Feedwater Heater [54] - LPH-7 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~54~1~19~~-38~ | Feedwater Heater [54] - LPH-7 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~54~1~5~~-38~ | Feedwater Heater [54] - LPH-7 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~54~1~6~~-38~ | Feedwater Heater [54] - LPH-7 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~54~2~2~~-38~ | Feedwater Heater [54] - LPH-7 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~54~1~16~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature @ heater exit at off-design | C | 84.5 | 84.5 | #N/A | 84.5
91¦~54~1~8~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~54~1~9~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~54~1~10~~-38~ | Feedwater Heater [54] - LPH-7 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~54~1~11~~-38~ | Feedwater Heater [54] - LPH-7 : Design point steam mass flow | t/h | 106.1517 | 106.1517 | #N/A | 106.1517
91¦~54~1~12~~-38~ | Feedwater Heater [54] - LPH-7 : Design point water mass flow | t/h | 861.8255 | 861.8255 | #N/A | 861.8255
91¦~54~1~13~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of condensing section | kW/C | 1509.2788 | 1509.2788 | #N/A | 1509.2788
91¦~54~1~20~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of drain cooling section | kW/C | 310.1291 | 310.1291 | #N/A | 310.1291
91¦~54~1~21~~-38~ | Feedwater Heater [54] - LPH-7 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~54~1~14~~-38~ | Feedwater Heater [54] - LPH-7 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~54~1~15~~-38~ | Feedwater Heater [54] - LPH-7 : Water-side flow resistance coefficient | m^-4 | 0.001309 | 0.001309 | #N/A | 0.001309
91¦~54~1~17~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~54~1~18~~-38~ | Feedwater Heater [54] - LPH-7 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~55~1~2~~-38~ | Feedwater Heater [55] - LPH-6 : Design point FW temperature @ heater exit | C | 104.4537 | 104.4537 | #N/A | 104.4537
91¦~55~1~3~~-38~ | Feedwater Heater [55] - LPH-6 : Design point terminal difference | C | 5.7 | 5.7 | #N/A | 5.7
91¦~55~1~4~~-38~ | Feedwater Heater [55] - LPH-6 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~55~1~19~~-38~ | Feedwater Heater [55] - LPH-6 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~55~1~5~~-38~ | Feedwater Heater [55] - LPH-6 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~55~1~6~~-38~ | Feedwater Heater [55] - LPH-6 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~55~2~2~~-38~ | Feedwater Heater [55] - LPH-6 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~55~1~16~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature @ heater exit at off-design | C | 104.4537 | 104.4537 | #N/A | 104.4537
91¦~55~1~8~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~55~1~9~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~55~1~10~~-38~ | Feedwater Heater [55] - LPH-6 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~55~1~11~~-38~ | Feedwater Heater [55] - LPH-6 : Design point steam mass flow | t/h | 74.788 | 74.788 | #N/A | 74.788
91¦~55~1~12~~-38~ | Feedwater Heater [55] - LPH-6 : Design point water mass flow | t/h | 861.8255 | 861.8255 | #N/A | 861.8255
91¦~55~1~13~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of condensing section | kW/C | 1433.8065 | 1433.8065 | #N/A | 1433.8065
91¦~55~1~20~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of drain cooling section | kW/C | 204.7327 | 204.7327 | #N/A | 204.7327
91¦~55~1~21~~-38~ | Feedwater Heater [55] - LPH-6 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~55~1~14~~-38~ | Feedwater Heater [55] - LPH-6 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~55~1~15~~-38~ | Feedwater Heater [55] - LPH-6 : Water-side flow resistance coefficient | m^-4 | 0.0012833 | 0.0012833 | #N/A | 0.0012833
91¦~55~1~17~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~55~1~18~~-38~ | Feedwater Heater [55] - LPH-6 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~56~1~2~~-38~ | Feedwater Heater [56] - LPH-5 : Design point FW temperature @ heater exit | C | 136.2094 | 136.2094 | #N/A | 136.2094
91¦~56~1~3~~-38~ | Feedwater Heater [56] - LPH-5 : Design point terminal difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~56~1~4~~-38~ | Feedwater Heater [56] - LPH-5 : Design point drain cooler approach | C | 2.8 | 2.8 | #N/A | 2.8
91¦~56~1~19~~-38~ | Feedwater Heater [56] - LPH-5 : Design point residual superheat | C | 20 | 20 | #N/A | 20
91¦~56~1~5~~-38~ | Feedwater Heater [56] - LPH-5 : Design point minimum pinch | C | 2.5 | 2.5 | #N/A | 2.5
91¦~56~1~6~~-38~ | Feedwater Heater [56] - LPH-5 : Design point dP/P across feedwater-side | % | 2 | 2 | #N/A | 2
76¦~56~2~2~~-38~ | Feedwater Heater [56] - LPH-5 : Off-design status 0:Working 2:Out-of-service |  | 0 | 0 | #N/A | 0
91¦~56~1~16~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature @ heater exit at off-design | C | 136.2094 | 136.2094 | #N/A | 136.2094
91¦~56~1~8~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam-side thermal res./total res. |  | 0.1 | 0.1 | #N/A | 0.1
91¦~56~1~9~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water-side thermal res./total res. |  | 0.75 | 0.75 | #N/A | 0.75
91¦~56~1~10~~-38~ | Feedwater Heater [56] - LPH-5 : Design point tube wall & fouling res./total res. |  | 0.15 | 0.15 | #N/A | 0.15
91¦~56~1~11~~-38~ | Feedwater Heater [56] - LPH-5 : Design point steam mass flow | t/h | 46.3054 | 46.3054 | #N/A | 46.3054
91¦~56~1~12~~-38~ | Feedwater Heater [56] - LPH-5 : Design point water mass flow | t/h | 861.8255 | 861.8255 | #N/A | 861.8255
91¦~56~1~13~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of condensing section | kW/C | 1876.8569 | 1876.8569 | #N/A | 1876.8569
91¦~56~1~20~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of drain cooling section | kW/C | 146.9249 | 146.9249 | #N/A | 146.9249
91¦~56~1~21~~-38~ | Feedwater Heater [56] - LPH-5 : Design point UA of desuperheating section | kW/C | 0 | 0 | #N/A | 0
91¦~56~1~14~~-38~ | Feedwater Heater [56] - LPH-5 : Correction factor for overall h.t.c. |  | 1 | 1 | #N/A | 1
91¦~56~1~15~~-38~ | Feedwater Heater [56] - LPH-5 : Water-side flow resistance coefficient | m^-4 | 0.0012582 | 0.0012582 | #N/A | 0.0012582
91¦~56~1~17~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for steam-side h.t.c. |  | 0.8 | 0.8 | #N/A | 0.8
91¦~56~1~18~~-38~ | Feedwater Heater [56] - LPH-5 : Scaling exponent for water-side h.t.c. |  | 0.72 | 0.72 | #N/A | 0.72
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30 | #N/A | 30
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 215 | 215 | #N/A | 215
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100 | #N/A | TJA_Whatif100
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 27.99 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 5.36 | 5.36 | #N/A | 5.36
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 48.63 | 48.63 | #N/A | 48.63
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 3.99 | 3.99 | #N/A | 3.99
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.8 | 0.8 | #N/A | 0.8
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.19 | 0.19 | #N/A | 0.19
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 13.04 | 13.04 | #N/A | 13.04
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 4500 | 4500 | 4500
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 32.75 | 32.75 | #N/A | 32.75
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~7~1~10~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam production rate | t/h | 1105.9 | 945.59 | 945.59 | 945.59
91¦~7~1~18~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1151 | 1145.33 | 1145.33 | 1145.33
91¦~7~1~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25 | 25 | 25
91¦~7~1~7~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Minor heat loss | % | 3.25 | 3.25 | #N/A | 3.25
91¦~7~1~8~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gage pressure | millibar | -0.62267 | -0.62267 | #N/A | -0.62267
91¦~7~1~6~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Secondary air pressure drop | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
91¦~7~1~39~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | % | 20 | 20 | #N/A | 20
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content (for emission level definition) | % | 5.3 | 5.3 | #N/A | 5.3
91¦~7~1~152~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
91¦~7~1~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit temperature @ design | C | 60.8 | 60.8 | #N/A | 60.8
91¦~7~1~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inlet air/fuel mass ratio in pulverizer @ design |  | 1.8 | 1.8 | #N/A | 1.8
91¦~7~1~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverized fuel fineness @ design | % | 65 | 65 | #N/A | 65
91¦~7~1~8~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Power consumption converted into heat in pulverizer @ design | % | 80 | 80 | #N/A | 80
91¦~7~1~7~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : % of as-received fuel moisture evaporated in pulverizer | % | 60 | 60 | #N/A | 60
91¦~7~1~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pressure drop in pulverizer | millibar | 20 | 20 | #N/A | 20
91¦~7~1~18~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exit gauge pressure | millibar | 99.6264 | 99.6264 | #N/A | 99.6264
91¦~7~1~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer nameplate specific power | kWh/tonne | 22.0462 | 22.0462 | #N/A | 22.0462
91¦~3~1~2~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332 | #N/A | 1.0332
91¦~3~1~3~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~3~1~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 695.23 | 695.23 | #N/A | 695.23
91¦~3~1~5~~-1~ | Gas/Air Source [3] - Sec.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~3~1~18~~-1~ | Gas/Air Source [3] - Sec.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~3~1~21~~-1~ | Gas/Air Source [3] - Sec.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~3~1~22~~-1~ | Gas/Air Source [3] - Sec.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~11~1~2~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129 | #N/A | 1.1129
91¦~11~1~3~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85 | #N/A | 25.85
91¦~11~1~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 579.01 | 579.01 | #N/A | 579.01
91¦~11~1~5~~-1~ | Gas/Air Source [11] - Prim.Air : Relative humidity | % | 59.24 | 59.24 | #N/A | 59.24
91¦~11~1~18~~-1~ | Gas/Air Source [11] - Prim.Air : Maximum H2O mole % | % | 80 | 80 | #N/A | 80
91¦~11~1~21~~-1~ | Gas/Air Source [11] - Prim.Air : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - Prim.Air : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~40~1~12~~-168~ | General Pump [40] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Rating / design point load |  | 1.0212 | 1.0212 | #N/A | 1.0212
91¦~6~1~1~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25 | #N/A | 25
91¦~6~1~2~~-46~ | Makeup / Blowdown [6] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99 | #N/A | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01 | #N/A | 0.01
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3 | #N/A | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7 | #N/A | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989 | #N/A | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011 | #N/A | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761 | #N/A | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239 | #N/A | 0.79239
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~35~1~4~~-107~ | Pipe (PCE) [35] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~35~1~9~~-107~ | Pipe (PCE) [35] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~36~1~4~~-107~ | Pipe (PCE) [36] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~36~1~9~~-107~ | Pipe (PCE) [36] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~37~1~4~~-107~ | Pipe (PCE) [37] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~37~1~9~~-107~ | Pipe (PCE) [37] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~60~1~4~~-107~ | Pipe (PCE) [60] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~60~1~9~~-107~ | Pipe (PCE) [60] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~61~1~4~~-107~ | Pipe (PCE) [61] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~61~1~9~~-107~ | Pipe (PCE) [61] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~63~1~4~~-107~ | Pipe (PCE) [63] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~63~1~9~~-107~ | Pipe (PCE) [63] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~64~1~4~~-107~ | Pipe (PCE) [64] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~64~1~9~~-107~ | Pipe (PCE) [64] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~73~1~4~~-107~ | Pipe (PCE) [73] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~73~1~9~~-107~ | Pipe (PCE) [73] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~74~1~4~~-107~ | Pipe (PCE) [74] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~74~1~9~~-107~ | Pipe (PCE) [74] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~75~1~4~~-107~ | Pipe (PCE) [75] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~75~1~9~~-107~ | Pipe (PCE) [75] : Heat Loss | kJ/kg | 1.7 | 1.7 | #N/A | 1.7
~76~1~4~~-107~ | Pipe (PCE) [76] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~76~1~9~~-107~ | Pipe (PCE) [76] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
83¦91¦~82~1~12~~-100~ | Pump (PCE) [82] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~83~1~12~~-100~ | Pump (PCE) [83] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
91¦~8~1~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air outlet temperature | C | 273.8889 | 273.8889 | #N/A | 273.8889
91¦~8~1~3~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path cold end leakage | % | 7 | 7 | #N/A | 7
91¦~8~1~4~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Air path hot end leakage | % | 3 | 3 | #N/A | 3
91¦~8~1~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air outlet temperature | C | 343.3334 | 343.3334 | #N/A | 343.3334
91¦~8~1~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air cold end leakage | % | 10 | 10 | #N/A | 10
91¦~8~1~14~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air hot end leakage | % | 5 | 5 | #N/A | 5
91¦~1~1~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump design point overall pressure rise | bar | 174.5563 | 174.5563 | #N/A | 174.5563
91¦~1~1~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~1~1~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Flow margin | % | 10 | 10 | #N/A | 10
91¦~1~1~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~1~1~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600.0005 | 3600.0005 | #N/A | 3600.0005
91¦~1~1~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Design point RPM |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~1~1~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~1~1~16~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss | kW | 132.0026 | 132.0026 | #N/A | 132.0026
91¦~1~1~13~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~1~1~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal RPM for off-design pump curve |  | 3600 | 3600 | #N/A | 3600
91¦~1~1~11~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal rating flow for off-design pump curve | t/h | 621.0208 | 621.0208 | #N/A | 621.0208
91¦~1~1~12~~-85~ | ST-Driven Pump [1] - BFPT-A : Nominal pressure rise for off-design pump curve | bar | 165.2995 | 165.2995 | #N/A | 165.2995
91¦~1~1~2~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 8.98 | 8.98 | #N/A | 8.98
91¦~1~1~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~1~1~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~1~1~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~1~1~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~1~1~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~1~5~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~1~1~5~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~1~1~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~86~1~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump design point overall pressure rise | bar | 174.5563 | 174.5563 | #N/A | 174.5563
91¦~86~1~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump head margin | % | -5.6 | -5.6 | #N/A | -5.6
91¦~86~1~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Flow margin | % | 10 | 10 | #N/A | 10
91¦~86~1~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump nominal isentropic efficiency | % | 75 | 75 | #N/A | 75
91¦~86~1~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000.0002 | 3000.0002 | #N/A | 3000.0002
91¦~86~1~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Design point RPM |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 97 | 97 | #N/A | 97
91¦~86~1~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~86~1~16~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss | kW | 132.0026 | 132.0026 | #N/A | 132.0026
91¦~86~1~13~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump off-design control valve dP | bar | 0 | 0 | #N/A | 0
91¦~86~1~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal RPM for off-design pump curve |  | 3000 | 3000 | #N/A | 3000
91¦~86~1~11~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal rating flow for off-design pump curve | t/h | 621.0208 | 621.0208 | #N/A | 621.0208
91¦~86~1~12~~-85~ | ST-Driven Pump [86] - BFPT-B : Nominal pressure rise for off-design pump curve | bar | 165.2995 | 165.2995 | #N/A | 165.2995
91¦~86~1~2~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point Inlet pressure (upstream of any stop or control valves) | bar | 9.36 | 9.36 | #N/A | 9.36
91¦~86~1~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry step efficiency | % | 85 | 85 | #N/A | 85
91¦~86~1~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~86~1~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~86~1~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~86~1~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~86~5~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~86~1~5~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~86~1~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~34~1~84~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~34~1~72~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Assumed water-side pressure drop for TD mode | bar | 0.35 | 0.35 | #N/A | 0.35
91¦~34~1~34~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Min. pinch temp. difference | C | 2.5 | 2.5 | #N/A | 2.5
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001 | #N/A | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998 | #N/A | 0.9998
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8 | #N/A | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195 | #N/A | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005 | #N/A | 0.005
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001 | #N/A | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057 | #N/A | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843 | #N/A | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999 | #N/A | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002 | #N/A | 0.00010002
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668 | #N/A | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332 | #N/A | 0.0332
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417 | #N/A | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005 | #N/A | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578 | #N/A | 0.1578
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 536.8 | 534.17 | 534.17 | 534.17
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 420 | 420 | #N/A | 420
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~77~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Desired steam outlet temperature | C | 511 | 511 | #N/A | 511
~77~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~77~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~77~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~78~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Desired steam outlet temperature | C | 534.1 | 534.1 | #N/A | 534.1
~78~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~78~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~78~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~23~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Desired steam outlet temperature | C | 490 | 490 | #N/A | 490
~23~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~23~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~23~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
91¦~79~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Desired steam outlet temperature | C | 517 | 517 | #N/A | 517
~79~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~79~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~79~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Assumed steam side pressure drop for TD mode | % | 1 | 1 | #N/A | 1
~14~2~2~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~14~1~5~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~14~1~6~~-32~ | Boiler Assembly [1]: Valve [14] : Upstream set point | bar | 36.6 | 36.6 | #N/A | 36.6
~14~1~8~~-32~ | Boiler Assembly [1]: Valve [14] : Downstream set point | bar | 36.6045 | 36.6045 | #N/A | 36.6045
~14~1~7~~-32~ | Boiler Assembly [1]: Valve [14] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~80~2~2~~-32~ | Valve [80] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~80~1~5~~-32~ | Valve [80] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~80~1~6~~-32~ | Valve [80] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~8~~-32~ | Valve [80] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~80~1~7~~-32~ | Valve [80] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~81~2~2~~-32~ | Valve [81] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~81~1~5~~-32~ | Valve [81] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~81~1~6~~-32~ | Valve [81] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~8~~-32~ | Valve [81] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~81~1~7~~-32~ | Valve [81] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~58~1~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5 | #N/A | 3.5
91¦~58~1~21~~-14~ | Water Sink [58] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~58~1~22~~-14~ | Water Sink [58] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~57~1~2~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~57~1~3~~-9~ | Water Source [57] : Temperature | C | 27.3 | 29 | 29 | 29
91¦~57~1~4~~-9~ | Water Source [57] : Steam quality |  | -2 | -2 | #N/A | -2
91¦~57~1~5~~-9~ | Water Source [57] : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~57~1~21~~-9~ | Water Source [57] : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~57~1~22~~-9~ | Water Source [57] : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~59~1~53~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975 | #N/A | 0.0975
~59~1~5~~-104~ | Water-cooled Condenser (PCE) [59] : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~59~1~9~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
~2~32~1~~-10100~ | Fix Pressure Stream 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 32.6 | 31.4223 | 31.4223 | 31.4223
~2~23~1~~-10100~ | Fix Pressure Stream 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 35.78 | 34.4868 | 34.4868 | 34.4868
~2~34~1~~-10100~ | Fix Pressure Stream 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 17.44 | 16.81 | 16.81 | 16.81
~2~41~1~~-10100~ | Fix Pressure Stream 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 9.85 | 9.4941 | 9.4941 | 9.4941
91¦~1~1~4~~-20000~ | Generator [1]: Design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~1~1~5~~-20000~ | Generator [1]: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~1~3~18~~-20000~ | Generator [1]: Generator mech loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~13~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [13] - G[1] |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~66~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [66] - SA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan : aux |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux |  | 1 | 1 | #N/A | 1
91¦~40~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [40] - CP |  | 1 | 1 | #N/A | 1
91¦~82~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [82] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~83~1~1~4~-7000~ | Auxiliary Device: Multiplier of Pump (PCE) [83] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~13~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~13~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~13~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to IPT inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~1~-4100~ | ST Assembly [1]: Leakage flow (HPT LP leak 1 to LPT crossover) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~13~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~13~1~2~~-11~ | ST Assembly [1]: ST Group [13] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 162.5 | 156.63 | 156.63 | 156.63
91¦~13~1~3~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry step efficiency | % | 85.1821 | 85.1821 | #N/A | 85.1821
91¦~13~1~7~~-11~ | ST Assembly [1]: ST Group [13] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~13~5~15~~-11~ | ST Assembly [1]: ST Group [13] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~13~1~4~~-11~ | ST Assembly [1]: ST Group [13] : Reference pressure ratio for steam turbine expansion step |  | 1.1 | 1.1 | #N/A | 1.1
91¦~13~1~5~~-11~ | ST Assembly [1]: ST Group [13] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~13~1~6~~-11~ | ST Assembly [1]: ST Group [13] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~13~1~11~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~13~1~12~~-11~ | ST Assembly [1]: ST Group [13] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~15~1~2~~-11~ | ST Assembly [1]: ST Group [15] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 59.74 | 57.582 | 57.582 | 57.582
91¦~15~1~20~~-11~ | ST Assembly [1]: ST Group [15] : Outlet specific enthalpy (before exhaust loss if any) | kJ/kg | 3047.1499 | 3047.1499 | #N/A | 3047.1499
91¦~15~1~7~~-11~ | ST Assembly [1]: ST Group [15] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~15~5~15~~-11~ | ST Assembly [1]: ST Group [15] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~15~1~4~~-11~ | ST Assembly [1]: ST Group [15] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~15~1~5~~-11~ | ST Assembly [1]: ST Group [15] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~15~1~6~~-11~ | ST Assembly [1]: ST Group [15] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~15~1~11~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~15~1~12~~-11~ | ST Assembly [1]: ST Group [15] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~26~1~2~~-11~ | ST Assembly [1]: ST Group [26] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 32.6 | 31.4223 | 31.4223 | 31.4223
91¦~26~1~3~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry step efficiency | % | 88.6914 | 88.6914 | #N/A | 88.6914
91¦~26~1~7~~-11~ | ST Assembly [1]: ST Group [26] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~26~5~15~~-11~ | ST Assembly [1]: ST Group [26] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~26~1~4~~-11~ | ST Assembly [1]: ST Group [26] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~26~1~5~~-11~ | ST Assembly [1]: ST Group [26] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~26~1~6~~-11~ | ST Assembly [1]: ST Group [26] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~26~1~11~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~26~1~12~~-11~ | ST Assembly [1]: ST Group [26] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~28~1~2~~-11~ | ST Assembly [1]: ST Group [28] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 17.44 | 16.81 | 16.81 | 16.81
91¦~28~1~3~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry step efficiency | % | 89.8737 | 89.8737 | #N/A | 89.8737
91¦~28~1~7~~-11~ | ST Assembly [1]: ST Group [28] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~28~5~15~~-11~ | ST Assembly [1]: ST Group [28] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~28~1~4~~-11~ | ST Assembly [1]: ST Group [28] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~28~1~5~~-11~ | ST Assembly [1]: ST Group [28] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~6~~-11~ | ST Assembly [1]: ST Group [28] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~28~1~11~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~28~1~12~~-11~ | ST Assembly [1]: ST Group [28] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~44~1~2~~-11~ | ST Assembly [1]: ST Group [44] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 9.36 | 9.4941 | 9.4941 | 9.4941
91¦~44~1~3~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry step efficiency | % | 90.9151 | 90.9151 | #N/A | 90.9151
91¦~44~1~7~~-11~ | ST Assembly [1]: ST Group [44] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~44~5~15~~-11~ | ST Assembly [1]: ST Group [44] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~44~1~4~~-11~ | ST Assembly [1]: ST Group [44] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~44~1~5~~-11~ | ST Assembly [1]: ST Group [44] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~44~1~6~~-11~ | ST Assembly [1]: ST Group [44] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~44~1~11~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~44~1~12~~-11~ | ST Assembly [1]: ST Group [44] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~45~1~2~~-11~ | ST Assembly [1]: ST Group [45] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 3.88 | 3.7398 | 3.7398 | 3.7398
91¦~45~1~3~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry step efficiency | % | 92.0601 | 92.0601 | #N/A | 92.0601
91¦~45~1~7~~-11~ | ST Assembly [1]: ST Group [45] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~45~5~15~~-11~ | ST Assembly [1]: ST Group [45] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~45~1~4~~-11~ | ST Assembly [1]: ST Group [45] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~45~1~5~~-11~ | ST Assembly [1]: ST Group [45] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~45~1~6~~-11~ | ST Assembly [1]: ST Group [45] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~45~1~11~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~45~1~12~~-11~ | ST Assembly [1]: ST Group [45] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~46~1~2~~-11~ | ST Assembly [1]: ST Group [46] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.47 | 1.4169 | 1.4169 | 1.4169
91¦~46~1~3~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry step efficiency | % | 92.3209 | 92.3209 | #N/A | 92.3209
91¦~46~1~7~~-11~ | ST Assembly [1]: ST Group [46] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~46~5~15~~-11~ | ST Assembly [1]: ST Group [46] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~46~1~4~~-11~ | ST Assembly [1]: ST Group [46] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~46~1~5~~-11~ | ST Assembly [1]: ST Group [46] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~46~1~6~~-11~ | ST Assembly [1]: ST Group [46] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~46~1~11~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~46~1~12~~-11~ | ST Assembly [1]: ST Group [46] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~47~1~2~~-11~ | ST Assembly [1]: ST Group [47] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.78 | 0.78 | #N/A | 0.78
91¦~47~1~3~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry step efficiency | % | 92.25 | 92.25 | #N/A | 92.25
91¦~47~1~7~~-11~ | ST Assembly [1]: ST Group [47] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~47~5~15~~-11~ | ST Assembly [1]: ST Group [47] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~47~1~4~~-11~ | ST Assembly [1]: ST Group [47] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~47~1~5~~-11~ | ST Assembly [1]: ST Group [47] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~47~1~6~~-11~ | ST Assembly [1]: ST Group [47] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~47~1~11~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~47~1~12~~-11~ | ST Assembly [1]: ST Group [47] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~5~1~2~~-11~ | ST Assembly [1]: ST Group [5] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.283 | 0.283 | #N/A | 0.283
91¦~5~1~3~~-11~ | ST Assembly [1]: ST Group [5] : Design point dry step efficiency | % | 92.15 | 92.15 | #N/A | 92.15
91¦~5~1~7~~-11~ | ST Assembly [1]: ST Group [5] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~5~5~6~~-11~ | ST Assembly [1]: ST Group [5] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~5~1~4~~-11~ | ST Assembly [1]: ST Group [5] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~5~1~5~~-11~ | ST Assembly [1]: ST Group [5] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~5~1~6~~-11~ | ST Assembly [1]: ST Group [5] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~5~1~11~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~5~1~12~~-11~ | ST Assembly [1]: ST Group [5] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~2~1~~~-5007~ | HIP Turbin: Label 1 |  | BFPT-A | BFPT-A | #N/A | BFPT-A
~2~2~~~-5007~ | HIP Turbin: Label 2 |  | BFPT-B | BFPT-B | #N/A | BFPT-B
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 26.95 | 26.95
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 75.41 | 75.41
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 23.5477 | 23.5477
~~~4~~-5000~ | Plant Summary: Gross power | kW | 350067.5938 | 350067.5938
~~~7~~-5000~ | Plant Summary: Net power | kW | 328299.4375 | 328299.4375
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 21768.1523 | 21768.1523
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 20017.8145 | 20017.8145
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 1750.3379 | 1750.3379
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 39.4715 | 39.4715
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 9120.4961 | 9120.4961
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 37.0171 | 37.0171
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 9725.2393 | 9725.2393
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 886886.125 | 886886.125
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 37.0171 | 37.0171
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 37.0171 | 37.0171
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 33.9629 | 33.9629
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 10599.7949 | 10599.7949
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 966640.8125 | 966640.8125
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 886886.125 | 886886.125
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 37.0171 | 37.0171
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 2.9718 | 2.9718
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 2.7648 | 2.7648
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 886886.125 | 886886.125
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 966640.8125 | 966640.8125
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.362 | 2.362
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 7541.2842 | 7541.2842
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 60995604 | 60995604
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 77217576 | 77217576
~1~3~1~~-2005~ | Shaft 1: Shaft net power | kW | 353770.6562 | 353770.6562
~1~3~2~~-2005~ | Shaft 1: Shaft speed | RPM | 3000 | 3000
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 2659.2253 | 2659.2253
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 25861.6016 | 25861.6016
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 24.35 | 24.35
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 2656.8037 | 2656.8037
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 77217.5781 | 77217.5781
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 235.2047 | 235.2047
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 1700825.375 | 1700825.375
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 23165.2734 | 23165.2734
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 89.1044 | 89.1044
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 272.258 | 272.258
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.37146 | 0.37146
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 894502.0625 | 894502.0625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.029461 | 0.029461
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 6.0163 | 6.0163
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 60995604 | 60995604
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 60995604 | 60995604
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 10732365 | 10732365
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 71727968 | 71727968
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 77217576 | 77217576
~1~9~13~~-5003~ | Generator / Motor Power: Generator [1] of ST Assembly [1] power | kW | 350067.5938 | 350067.5938
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 1202.7231 | 1202.7231
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 3052.4128 | 3052.4128
~4~66~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [66] - SA Fan : aux | kW | 139.3719 | 139.3719
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan : aux | kW | 262.7296 | 262.7296
~4~7~158~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux | kW | 6365.7266 | 6365.7266
~4~40~168~~-5003~ | Generator / Motor Power: General Pump [40] - CP | kW | 387.63 | 387.63
~4~82~100~~-5003~ | Generator / Motor Power: Pump (PCE) [82] - CWP-1 | kW | 2185.7017 | 2185.7017
~4~83~100~~-5003~ | Generator / Motor Power: Pump (PCE) [83] - CWP-2 | kW | 2185.7017 | 2185.7017
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 735.142 | 735.142
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 3500.6758 | 3500.6758
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 1750.3379 | 1750.3379
~5~9~13~1~-5003~ | Generator / Motor Power: Shaft-1 net power | kW | 353770.6562 | 353770.6562
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 20017.8145 | 20017.8145
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 886886.125 | 886886.125
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~3~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer | kW | -400.1209 | -400.1209
91¦~3~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [3] - Sec.Air status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer | kW | -116.8898 | -116.8898
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - Prim.Air status |  | Ignored | Ignored
93¦~6~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer | kW | 86.6209 | 86.6209
91¦~6~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~57~3~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer | kW | 1241652.375 | 1241652.375
91¦~57~1~1~1~-7000~ | Energy Inflow: Water Source [57] heat transfer multiplier |  | 1 | 1
82¦71¦~57~5~10~1~-7000~ | Energy Inflow: Water Source [57] status |  | Ignored | Ignored
93¦~6~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer | kW | 0 | 0
91¦~6~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] heat transfer multiplier |  | 1 | 1
82¦71¦~6~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [6] status |  | Ignored | Ignored
93¦~58~3~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer | kW | 1699384.125 | 1699384.125
91¦~58~1~1~2~-7000~ | Energy Outflow: Water Sink [58] heat transfer multiplier |  | 1 | 1
82¦71¦~58~5~10~2~-7000~ | Energy Outflow: Water Sink [58] status |  | Ignored | Ignored
93¦~13~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [13] shaft power | kW | 79384.3125 | 79384.3125
93¦~15~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [15] shaft power | kW | 26431.0625 | 26431.0625
93¦~26~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [26] shaft power | kW | 49082.2656 | 49082.2656
93¦~28~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [28] shaft power | kW | 39403.9531 | 39403.9531
93¦~44~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [44] shaft power | kW | 49947.25 | 49947.25
93¦~45~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [45] shaft power | kW | 40562.2617 | 40562.2617
93¦~46~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [46] shaft power | kW | 21420.5391 | 21420.5391
93¦~47~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [47] shaft power | kW | 28742.9082 | 28742.9082
93¦~5~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [5] shaft power | kW | 18796.0918 | 18796.0918
82¦71¦~5~5~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] power | kW | 350067.5938 | 350067.5938
91¦~5~1~1~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] multiplier |  | 1 | 1
93¦~5~3~3~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] efficiency | % | 98.9533 | 98.9533
82¦71¦~5~5~10~3~-7000~ | Power Device: Generator [1] of ST Assembly [1] status |  | power producer | power producer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 1202.7231 | 1202.7231
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 3052.4128 | 3052.4128
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~66~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux power | kW | 139.3719 | 139.3719
91¦~66~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux multiplier |  | 1 | 1
82¦71¦~66~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [66] - SA Fan : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux power | kW | 262.7296 | 262.7296
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan : aux status |  | power consumer | power consumer
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux power | kW | 6365.7266 | 6365.7266
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Furnace w/ Pulverizer [7] : aux status |  | power consumer | power consumer
93¦~40~3~2~4~-7000~ | Auxiliary Device: General Pump [40] - CP power | kW | 387.63 | 387.63
91¦~40~1~1~4~-7000~ | Auxiliary Device: General Pump [40] - CP multiplier |  | 1 | 1
82¦71¦~40~5~10~4~-7000~ | Auxiliary Device: General Pump [40] - CP status |  | power consumer | power consumer
93¦~82~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 power | kW | 2185.7017 | 2185.7017
91¦~82~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 multiplier |  | 1 | 1
82¦71¦~82~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [82] - CWP-1 status |  | power consumer | power consumer
93¦~83~3~2~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 power | kW | 2185.7017 | 2185.7017
91¦~83~1~1~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 multiplier |  | 1 | 1
82¦71¦~83~5~10~4~-7000~ | Auxiliary Device: Pump (PCE) [83] - CWP-2 status |  | power consumer | power consumer
~31~6~1~~-27~ | Deaerator [31] - DAER : Mode |  | TD | TD
~31~6~3~~-27~ | Deaerator [31] - DAER : DA pressure specification |  | Specified by user | Specified by user
~31~4~4~~-27~ | Deaerator [31] - DAER : Operating pressure | bar | 9.25 | 9.25
~31~4~5~~-27~ | Deaerator [31] - DAER : Temperature | C | 176.5256 | 176.5256
93¦~31~4~7~~-27~ | Deaerator [31] - DAER : FW inlet pressure | bar | 10.4276 | 10.4276
93¦~31~4~8~~-27~ | Deaerator [31] - DAER : FW inlet temperature | C | 136.2265 | 136.2265
93¦~31~4~28~~-27~ | Deaerator [31] - DAER : FW inlet enthalpy | kJ/kg | 573.419 | 573.419
93¦~31~4~9~~-27~ | Deaerator [31] - DAER : FW inlet mass flow | t/h | 861.8255 | 861.8255
93¦~31~4~23~~-27~ | Deaerator [31] - DAER : Additional water head at inlet | bar | 1.1775 | 1.1775
93¦~31~4~10~~-27~ | Deaerator [31] - DAER : Heating stream pressure | bar | 9.6569 | 9.6569
93¦~31~4~12~~-27~ | Deaerator [31] - DAER : Heating stream temperature | C | 353.0348 | 353.0348
93¦~31~4~11~~-27~ | Deaerator [31] - DAER : Heating stream enthalpy | kJ/kg | 3165.2844 | 3165.2844
93¦~31~4~13~~-27~ | Deaerator [31] - DAER : Heating stream mass flow | t/h | 59.8692 | 59.8692
93¦~31~4~17~~-27~ | Deaerator [31] - DAER : Flash in pressure | bar | 16.2246 | 16.2246
93¦~31~4~18~~-27~ | Deaerator [31] - DAER : Flash in temperature | C | 182.9617 | 182.9617
93¦~31~4~19~~-27~ | Deaerator [31] - DAER : Flash in enthalpy | kJ/kg | 776.4781 | 776.4781
93¦~31~4~20~~-27~ | Deaerator [31] - DAER : Flash in mass flow | t/h | 196.1428 | 196.1428
93¦~31~4~14~~-27~ | Deaerator [31] - DAER : FW outlet pressure | bar | 10.3295 | 10.3295
93¦~31~4~15~~-27~ | Deaerator [31] - DAER : FW outlet temperature | C | 176.5336 | 176.5336
93¦~31~4~29~~-27~ | Deaerator [31] - DAER : FW outlet enthalpy | kJ/kg | 747.8646 | 747.8646
93¦~31~4~16~~-27~ | Deaerator [31] - DAER : FW outlet mass flow | t/h | 1117.8375 | 1117.8375
93¦~31~4~24~~-27~ | Deaerator [31] - DAER : Additional water head at outlet | bar | 1.0794 | 1.0794
~67~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Temperature drop | C | 2.4129 | 2.4129
~67~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet pressure | bar | 35.78 | 35.78
~67~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet temperature | C | 327.4125 | 327.4125
~67~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet mass flow | t/h | 940.2924 | 940.2924
~67~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Inlet enthalpy | kJ/kg | 3047.1467 | 3047.1467
~67~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet pressure | bar | 35.78 | 35.78
~67~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet temperature | C | 324.9996 | 324.9996
~67~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet mass flow | t/h | 942.8235 | 942.8235
~67~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Outlet enthalpy | kJ/kg | 3041.0444 | 3041.0444
~67~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray mass flow | t/h | 2.5312 | 2.5312
~67~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [67] - RH Desup : Spray water enthalpy | kJ/kg | 774.1844 | 774.1844
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Temperature drop | C | 2.0007 | 2.0007
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet pressure | bar | 169.0981 | 169.0981
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet temperature | C | 420.0016 | 420.0016
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet mass flow | t/h | 1105.8999 | 1105.8999
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Inlet enthalpy | kJ/kg | 3009.0886 | 3009.0886
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet pressure | bar | 169.0981 | 169.0981
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet temperature | C | 418.001 | 418.001
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet mass flow | t/h | 1110.0084 | 1110.0084
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Outlet enthalpy | kJ/kg | 3000.8169 | 3000.8169
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray mass flow | t/h | 4.1084 | 4.1084
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup : Spray water enthalpy | kJ/kg | 774.1844 | 774.1844
~69~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Temperature drop | C | 2.0002 | 2.0002
~69~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet pressure | bar | 165.7662 | 165.7662
~69~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet temperature | C | 516.9982 | 516.9982
~69~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet mass flow | t/h | 1110.0084 | 1110.0084
~69~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Inlet enthalpy | kJ/kg | 3339.772 | 3339.772
~69~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet pressure | bar | 165.7662 | 165.7662
~69~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet temperature | C | 514.998 | 514.998
~69~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet mass flow | t/h | 1112.5415 | 1112.5415
~69~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Outlet enthalpy | kJ/kg | 3333.9304 | 3333.9304
~69~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray mass flow | t/h | 2.5331 | 2.5331
~69~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup : Spray water enthalpy | kJ/kg | 774.1844 | 774.1844
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct : Heat loss | kW | 105.3989 | 105.3989
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Temperature drop | C | 1.1111 | 1.1111
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct : Heat loss | kW | 609.2505 | 609.2505
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Temperature drop | C | 0 | 0
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Heat loss | kW | 0 | 0
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 1108.6648 | 1108.6648
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 172.497 | 172.497
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 1191.1445 | 1191.1445
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 271.7824 | 271.7824
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 1108.6648 | 1108.6648
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 170.7891 | 170.7891
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 317 | 317
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1432.1023 | 1432.1023
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 1667.9181 | 1667.9181
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 8.1714 | 8.1714
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 489.3696 | 489.3696
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 352.373 | 352.373
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 51.0935 | 51.0935
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1690.9503 | 1690.9503
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 74207.0938 | 74207.0938
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 74207.0938 | 74207.0938
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 556.5532 | 556.5532
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 1.7079 | 1.7079
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.6181 | 99.6181
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 1202.7231 | 1202.7231
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.98686 | 0.98686
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 140.7547 | 140.7547
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 2192458.5 | 2192458.5
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 1824.4261 | 1824.4261
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 8.1714 | 8.1714
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 8.1402 | 8.1402
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.031206 | 0.031206
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 2348.2092 | 2348.2092
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 6546.4443 | 6546.4443
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 8.9675 | 8.9675
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 25.0001 | 25.0001
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 0 | 0
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.214 | 1.214
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 2960.0461 | 2960.0461
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 2960.0461 | 2960.0461
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 2930.4458 | 2930.4458
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 615.5439 | 615.5439
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 38.6052 | 38.6052
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 38.6052 | 38.6052
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.0992 | 80.0992
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 29.6004 | 29.6004
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 3205.0334 | 3205.0334
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.989 | 96.989
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 3052.4128 | 3052.4128
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 2960.0461 | 2960.0461
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.974 | 96.974
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 92.3666 | 92.3666
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 3108.0481 | 3108.0481
82¦71¦~66~5~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~66~5~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~66~1~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of existing units |  | 1 | 1
93¦~66~3~20~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Number of operating units |  | 1 | 1
93¦~66~3~19~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Total shaft power | kW | 132.3443 | 132.3443
93¦~66~3~1~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Shaft power per unit | kW | 132.3443 | 132.3443
93¦~66~3~2~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan compression power per unit | kW | 131.0209 | 131.0209
93¦~66~3~3~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan inlet volume flow per unit | m^3/s | 296.824 | 296.824
93¦~66~3~4~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan pressure rise (before control damper) | millibar | 3.5334 | 3.5334
93¦~66~3~5~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan overall pressure rise | millibar | 3.5334 | 3.5334
93¦~66~3~6~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~66~3~11~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Fan polytropic efficiency | % | 80.0232 | 80.0232
93¦~66~3~8~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Current RPM |  | 1200 | 1200
93¦~66~3~9~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical loss per unit | kW | 1.3234 | 1.3234
93¦~66~3~10~~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~66~6~1~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Mode |  | Design | Design
91¦~66~1~7~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate power | kW | 146.3405 | 146.3405
91¦~66~1~19~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate efficiency | % | 94.9828 | 94.9828
91¦~66~1~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~66~2~8~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Number of operating units |  | 1 | 1
93¦~66~7~2~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electricity consumption | kW | 139.3719 | 139.3719
93¦~66~7~6~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Shaft power | kW | 132.3443 | 132.3443
93¦~66~7~4~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Efficiency | % | 94.9577 | 94.9577
93¦~66~7~3~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Electrical loss | kW | 7.0276 | 7.0276
89¦~66~3~5~2~-65~ | Boiler Assembly [1]: Fan [66] - SA Fan : Motor: Nameplate motor shaft power | kW | 138.9615 | 138.9615
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Total shaft power | kW | 251.0621 | 251.0621
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Shaft power per unit | kW | 251.0621 | 251.0621
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan compression power per unit | kW | 248.5515 | 248.5515
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan inlet volume flow per unit | m^3/s | 80.4119 | 80.4119
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan pressure rise (before control damper) | millibar | 24.9066 | 24.9066
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan overall pressure rise | millibar | 24.9066 | 24.9066
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Fan polytropic efficiency | % | 80.0643 | 80.0643
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical loss per unit | kW | 2.5106 | 2.5106
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate power | kW | 275.8661 | 275.8661
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate efficiency | % | 95.5812 | 95.5812
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electricity consumption | kW | 262.7296 | 262.7296
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Shaft power | kW | 251.0621 | 251.0621
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Efficiency | % | 95.5591 | 95.5591
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Electrical loss | kW | 11.6675 | 11.6675
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan : Motor: Nameplate motor shaft power | kW | 263.6152 | 263.6152
82¦71¦~16~5~1~~-38~ | Feedwater Heater [16] - HPH-1 : Mode |  | Design | Design
89¦~16~3~7~~-38~ | Feedwater Heater [16] - HPH-1 : Heat transfer | kW | 43513.707 | 43513.707
89¦~16~3~8~~-38~ | Feedwater Heater [16] - HPH-1 : Shell pressure | bar | 58.1048 | 58.1048
89¦~16~3~9~~-38~ | Feedwater Heater [16] - HPH-1 : Saturation temperature | C | 273.5001 | 273.5001
89¦~16~3~13~~-38~ | Feedwater Heater [16] - HPH-1 : FW temperature at heater exit | C | 272 | 272
89¦~16~3~11~~-38~ | Feedwater Heater [16] - HPH-1 : Terminal difference | C | 1.5 | 1.5
89¦~16~3~12~~-38~ | Feedwater Heater [16] - HPH-1 : Drain cooler approach | C | 2.8 | 2.8
89¦~16~3~3~~-38~ | Feedwater Heater [16] - HPH-1 : UA of drain cooler section | kW/C | 262.0872 | 262.0872
89¦~16~3~1~~-38~ | Feedwater Heater [16] - HPH-1 : UA of condensing section | kW/C | 4359.603 | 4359.603
82¦71¦~17~5~1~~-38~ | Feedwater Heater [17] - HPH-2 : Mode |  | Design | Design
89¦~17~3~7~~-38~ | Feedwater Heater [17] - HPH-2 : Heat transfer | kW | 56652.2344 | 56652.2344
89¦~17~3~8~~-38~ | Feedwater Heater [17] - HPH-2 : Shell pressure | bar | 35.0784 | 35.0784
89¦~17~3~9~~-38~ | Feedwater Heater [17] - HPH-2 : Saturation temperature | C | 242.6904 | 242.6904
89¦~17~3~13~~-38~ | Feedwater Heater [17] - HPH-2 : FW temperature at heater exit | C | 242.4124 | 242.4124
89¦~17~3~11~~-38~ | Feedwater Heater [17] - HPH-2 : Terminal difference | C | 0.27802 | 0.27802
89¦~17~3~12~~-38~ | Feedwater Heater [17] - HPH-2 : Drain cooler approach | C | 5.6 | 5.6
89¦~17~3~3~~-38~ | Feedwater Heater [17] - HPH-2 : UA of drain cooler section | kW/C | 460.7218 | 460.7218
89¦~17~3~1~~-38~ | Feedwater Heater [17] - HPH-2 : UA of condensing section | kW/C | 6750.708 | 6750.708
82¦71¦~24~5~1~~-38~ | Feedwater Heater [24] - HPH-3 : Mode |  | Design | Design
89¦~24~3~7~~-38~ | Feedwater Heater [24] - HPH-3 : Heat transfer | kW | 28552.0293 | 28552.0293
89¦~24~3~8~~-38~ | Feedwater Heater [24] - HPH-3 : Shell pressure | bar | 16.2246 | 16.2246
89¦~24~3~9~~-38~ | Feedwater Heater [24] - HPH-3 : Saturation temperature | C | 202.05 | 202.05
89¦~24~3~13~~-38~ | Feedwater Heater [24] - HPH-3 : FW temperature at heater exit | C | 201.67 | 201.67
89¦~24~3~11~~-38~ | Feedwater Heater [24] - HPH-3 : Terminal difference | C | 0.38001 | 0.38001
89¦~24~3~12~~-38~ | Feedwater Heater [24] - HPH-3 : Drain cooler approach | C | 2.5 | 2.5
89¦~24~3~3~~-38~ | Feedwater Heater [24] - HPH-3 : UA of drain cooler section | kW/C | 587.6343 | 587.6343
89¦~24~3~1~~-38~ | Feedwater Heater [24] - HPH-3 : UA of condensing section | kW/C | 5201.0454 | 5201.0454
82¦71¦~53~5~1~~-38~ | Feedwater Heater [53] - LPH-8 : Mode |  | Design | Design
89¦~53~3~7~~-38~ | Feedwater Heater [53] - LPH-8 : Heat transfer | kW | 15922.4248 | 15922.4248
89¦~53~3~8~~-38~ | Feedwater Heater [53] - LPH-8 : Shell pressure | bar | 0.27745 | 0.27745
89¦~53~3~9~~-38~ | Feedwater Heater [53] - LPH-8 : Saturation temperature | C | 67.3104 | 67.3104
89¦~53~3~13~~-38~ | Feedwater Heater [53] - LPH-8 : FW temperature at heater exit | C | 61.7104 | 61.7104
89¦~53~3~11~~-38~ | Feedwater Heater [53] - LPH-8 : Terminal difference | C | 5.6 | 5.6
89¦~53~3~12~~-38~ | Feedwater Heater [53] - LPH-8 : Drain cooler approach | C | 2.8 | 2.8
89¦~53~3~3~~-38~ | Feedwater Heater [53] - LPH-8 : UA of drain cooler section | kW/C | 331.5611 | 331.5611
89¦~53~3~1~~-38~ | Feedwater Heater [53] - LPH-8 : UA of condensing section | kW/C | 1208.4103 | 1208.4103
82¦71¦~54~5~1~~-38~ | Feedwater Heater [54] - LPH-7 : Mode |  | Design | Design
89¦~54~3~7~~-38~ | Feedwater Heater [54] - LPH-7 : Heat transfer | kW | 22847.1895 | 22847.1895
89¦~54~3~8~~-38~ | Feedwater Heater [54] - LPH-7 : Shell pressure | bar | 0.70449 | 0.70449
89¦~54~3~9~~-38~ | Feedwater Heater [54] - LPH-7 : Saturation temperature | C | 90.1 | 90.1
89¦~54~3~13~~-38~ | Feedwater Heater [54] - LPH-7 : FW temperature at heater exit | C | 84.5 | 84.5
89¦~54~3~11~~-38~ | Feedwater Heater [54] - LPH-7 : Terminal difference | C | 5.6 | 5.6
89¦~54~3~12~~-38~ | Feedwater Heater [54] - LPH-7 : Drain cooler approach | C | 2.8 | 2.8
89¦~54~3~3~~-38~ | Feedwater Heater [54] - LPH-7 : UA of drain cooler section | kW/C | 310.1291 | 310.1291
89¦~54~3~1~~-38~ | Feedwater Heater [54] - LPH-7 : UA of condensing section | kW/C | 1509.2788 | 1509.2788
82¦71¦~55~5~1~~-38~ | Feedwater Heater [55] - LPH-6 : Mode |  | Design | Design
89¦~55~3~7~~-38~ | Feedwater Heater [55] - LPH-6 : Heat transfer | kW | 20097.916 | 20097.916
89¦~55~3~8~~-38~ | Feedwater Heater [55] - LPH-6 : Shell pressure | bar | 1.4412 | 1.4412
89¦~55~3~9~~-38~ | Feedwater Heater [55] - LPH-6 : Saturation temperature | C | 110.1537 | 110.1537
89¦~55~3~13~~-38~ | Feedwater Heater [55] - LPH-6 : FW temperature at heater exit | C | 104.4537 | 104.4537
89¦~55~3~11~~-38~ | Feedwater Heater [55] - LPH-6 : Terminal difference | C | 5.7 | 5.7
89¦~55~3~12~~-38~ | Feedwater Heater [55] - LPH-6 : Drain cooler approach | C | 2.8 | 2.8
89¦~55~3~3~~-38~ | Feedwater Heater [55] - LPH-6 : UA of drain cooler section | kW/C | 204.7327 | 204.7327
89¦~55~3~1~~-38~ | Feedwater Heater [55] - LPH-6 : UA of condensing section | kW/C | 1433.8065 | 1433.8065
82¦71¦~56~5~1~~-38~ | Feedwater Heater [56] - LPH-5 : Mode |  | Design | Design
89¦~56~3~7~~-38~ | Feedwater Heater [56] - LPH-5 : Heat transfer | kW | 32274.5195 | 32274.5195
89¦~56~3~8~~-38~ | Feedwater Heater [56] - LPH-5 : Shell pressure | bar | 3.8039 | 3.8039
89¦~56~3~9~~-38~ | Feedwater Heater [56] - LPH-5 : Saturation temperature | C | 141.8094 | 141.8094
89¦~56~3~13~~-38~ | Feedwater Heater [56] - LPH-5 : FW temperature at heater exit | C | 136.2094 | 136.2094
89¦~56~3~11~~-38~ | Feedwater Heater [56] - LPH-5 : Terminal difference | C | 5.6 | 5.6
89¦~56~3~12~~-38~ | Feedwater Heater [56] - LPH-5 : Drain cooler approach | C | 2.8 | 2.8
89¦~56~3~3~~-38~ | Feedwater Heater [56] - LPH-5 : UA of drain cooler section | kW/C | 146.9249 | 146.9249
89¦~56~3~1~~-38~ | Feedwater Heater [56] - LPH-5 : UA of condensing section | kW/C | 1876.8569 | 1876.8569
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0135 | 1.0135
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 30 | 30
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 17296.6777 | 17296.6777
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 184.6997 | 184.6997
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 886886.125 | 886886.125
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 966640.8125 | 966640.8125
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.362 | 2.362
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 7541.2842 | 7541.2842
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | TJA_Whatif100 | TJA_Whatif100
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 17286.1191 | 17286.1191
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 18840.5996 | 18840.5996
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 30 | 30
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 17296.6777 | 17296.6777
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 18922.1328 | 18922.1328
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 48.63 | 48.63
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 3.99 | 3.99
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 13.04 | 13.04
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.8 | 0.8
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.19 | 0.19
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 5.36 | 5.36
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 27.99 | 27.99
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9862 | 6.9862
93¦~7~4~57~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total steam produced | t/h | 1105.9 | 1105.9
93¦~7~4~54~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam pressure | bar | 170.7891 | 170.7891
93¦~7~4~55~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam temperature | C | 352.6726 | 352.6726
93¦~7~4~56~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam enthalpy | kJ/kg | 2544.8325 | 2544.8325
93¦~7~4~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Adiabatic temperature | C | 1707.3339 | 1707.3339
93¦~7~4~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Effective radiating temperature | C | 1431.2524 | 1431.2524
93¦~7~4~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | C | 1150.9436 | 1150.9436
93¦~7~4~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Waterwall surface temperature | C | 1085.9188 | 1085.9188
93¦~7~4~19~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | % | 25 | 25
82¦71¦~7~6~1~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas N2 mol% | % | 69.3633 | 69.3633
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas O2 mol% | % | 3.7173 | 3.7173
93¦~7~4~104~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas CO2 mol% | % | 13.0047 | 13.0047
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas H2O mol% | % | 13.0614 | 13.0614
93¦~7~4~191~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas SO2 mol% | % | 0.019061 | 0.019061
82¦71¦~7~6~2~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Flue gas Ar mol% | % | 0.83426 | 0.83426
93¦~7~4~289~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total heat transfer to water/steam side | kW | 342064.3438 | 342064.3438
93¦~7~4~5~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat transfer to waterwall | kW | 342064.3438 | 342064.3438
82¦71¦~7~6~3~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon in ash | kW | 2945.0488 | 2945.0488
93¦~7~4~13~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat losses | kW | 11114.7891 | 11114.7891
93¦~7~4~109~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Radiant flux past screen | kW | 3855.5435 | 3855.5435
93¦~7~4~321~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash (bed drain) sensible heat | kW | 720.7422 | 720.7422
93¦~7~4~322~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash sensible heat | kW | 2882.9695 | 2882.9695
93¦~7~4~43~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat absorption rate | kW/m^2 | 108.028 | 108.028
93¦~7~4~41~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Heat release rate | kW/m^2 | 305.3845 | 305.3845
93¦~7~4~42~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Volumetric fuel release rate | kW/m^3 | 93.8565 | 93.8565
93¦~7~4~305~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : SO2 removal efficiency | % | 0 | 0
93¦~7~4~302~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Sulfur removed | t/h | 0 | 0
93¦~7~4~301~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reagent consumption | t/h | 0 | 0
93¦~7~4~32~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas mass flux @ aperture | t/h-m^2 | 9.5457 | 9.5457
93¦~7~4~46~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Gas velocity leaving aperture @ exit temperature | m/s | 10.682 | 10.682
93¦~7~4~247~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace gas mass flux | t/h-m^2 | 7.7924 | 7.7924
93¦~7~4~33~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace velocity @ effective radiating temperature | m/s | 10.4364 | 10.4364
93¦~7~4~339~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel mass flow | t/h | 184.6997 | 184.6997
82¦71¦~7~6~4~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel consumption per day | tonne/day | 4432.7896 | 4432.7896
93¦~7~4~17~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (LHV) | kW | 886886.125 | 886886.125
93¦~7~4~49~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel input (HHV) | kW | 966640.8125 | 966640.8125
93¦~7~4~28~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel delivery power | kW | 5211.1792 | 5211.1792
93¦~7~4~246~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Ash handling power | kW | 450.3717 | 450.3717
93¦~7~4~47~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Forced circulation pump power | kW | 704.1751 | 704.1751
93¦~7~4~16~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel ash flow | t/h | 9.8999 | 9.8999
93¦~7~4~24~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Unburnt carbon flow | t/h | 0.31437 | 0.31437
93¦~7~4~312~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solids added to ash due to reagent addition | t/h | 0 | 0
93¦~7~4~326~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Inert bed material feed | t/h | 0 | 0
93¦~7~4~327~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Total solid produced from combustion | t/h | 10.2143 | 10.2143
93¦~7~4~314~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Bottom ash flow | t/h | 2.0429 | 2.0429
93¦~7~4~317~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fly ash flow | t/h | 8.1714 | 8.1714
91¦~7~1~150~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Reference O2 content | % | 5.3 | 5.3
93¦~7~4~103~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas O2 content | % | 3.7173 | 3.7173
93¦~7~4~105~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Exit flue gas H2O content | % | 13.0614 | 13.0614
93¦~7~4~431~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
76¦~7~2~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of existing pulverizers |  | 6 | 6
76¦~7~2~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Number of operating pulverizers |  | 5 | 5
91¦~7~1~92~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow | t/h | 184.6997 | 184.6997
93¦~7~3~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel flow (each) | t/h | 36.9399 | 36.9399
91¦~7~1~80~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel temperature | C | 30 | 30
91¦~7~1~89~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet fuel moisture percent | % | 27.99 | 27.99
93¦~7~3~20~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel flow (each) | t/h | 30.7362 | 30.7362
93¦~7~3~19~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet fuel moisture percent | % | 13.4558 | 13.4558
93¦~7~3~6~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet temperature | C | 60.8 | 60.8
93¦~7~3~33~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total moisture evaporated | t/h | 31.0185 | 31.0185
93¦~7~3~34~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percent of moisture evaporated | % | 60 | 60
82¦71¦~7~10~1~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow | t/h | 269.4123 | 269.4123
82¦71¦~7~10~11~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet mass flow (each) | t/h | 53.8825 | 53.8825
91¦~7~1~41~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer hot gas inlet temperature | C | 320.6714 | 320.6714
82¦71¦~7~10~2~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow | t/h | 63.0472 | 63.0472
82¦71¦~7~10~12~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air mass flow (each) | t/h | 12.6094 | 12.6094
91¦~7~1~51~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer tempering air temperature | C | 27.2082 | 27.2082
82¦71¦~7~10~3~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow | t/h | 332.4594 | 332.4594
82¦71¦~7~10~13~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air mass flow (each) | t/h | 66.4919 | 66.4919
91¦~7~1~61~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air temperature | C | 266.1162 | 266.1162
91¦~7~1~60~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Drying air pressure | bar | 1.1254 | 1.1254
93¦~7~3~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer percentage of tempering air over total drying air | % | 18.9639 | 18.9639
93¦~7~3~35~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer inlet air/fuel mass ratio |  | 1.8 | 1.8
82¦71¦~7~10~4~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow | t/h | 363.4779 | 363.4779
82¦71¦~7~10~14~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas mass flow (each) | t/h | 72.6956 | 72.6956
93¦~7~3~37~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas dew point | C | 55.521 | 55.521
93¦~7~3~38~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer outlet gas relative humidity | % | 78.0768 | 78.0768
93¦~7~3~5~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer power (each) | kW | 1026.3816 | 1026.3816
82¦71¦~7~10~10~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer exhaust fan power (each) | kW | 15.8542 | 15.8542
93¦~7~3~30~100~-158~ | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Pulverizer total power consumption | kW | 5211.1792 | 5211.1792
93¦~3~3~1~~-1~ | Gas/Air Source [3] - Sec.Air : Pressure | bar | 1.0332 | 1.0332
93¦~3~3~2~~-1~ | Gas/Air Source [3] - Sec.Air : Temperature | C | 25.85 | 25.85
93¦~3~3~3~~-1~ | Gas/Air Source [3] - Sec.Air : Enthalpy | kJ/kg | 0.86557 | 0.86557
93¦~3~3~4~~-1~ | Gas/Air Source [3] - Sec.Air : Mass flow | t/h | 1277.0692 | 1277.0692
93¦~3~3~5~~-1~ | Gas/Air Source [3] - Sec.Air : Molecular weight |  | 28.7578 | 28.7578
93¦~3~3~11~~-1~ | Gas/Air Source [3] - Sec.Air : N2 mole percent | % | 76.5891 | 76.5891
93¦~3~3~12~~-1~ | Gas/Air Source [3] - Sec.Air : O2 mole percent | % | 20.5495 | 20.5495
93¦~3~3~13~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mole percent | % | 0.029724 | 0.029724
93¦~3~3~14~~-1~ | Gas/Air Source [3] - Sec.Air : H2O mole percent | % | 1.9093 | 1.9093
93¦~3~3~15~~-1~ | Gas/Air Source [3] - Sec.Air : SO2 mole percent | % | 0 | 0
93¦~3~3~16~~-1~ | Gas/Air Source [3] - Sec.Air : Ar mole percent | % | 0.92239 | 0.92239
93¦~3~3~20~~-1~ | Gas/Air Source [3] - Sec.Air : Liquid H2O mole percent | % | 0 | 0
93¦~3~3~21~~-1~ | Gas/Air Source [3] - Sec.Air : CO2 mass flow | t/h | 0.58093 | 0.58093
93¦~11~3~1~~-1~ | Gas/Air Source [11] - Prim.Air : Pressure | bar | 1.1129 | 1.1129
93¦~11~3~2~~-1~ | Gas/Air Source [11] - Prim.Air : Temperature | C | 25.85 | 25.85
93¦~11~3~3~~-1~ | Gas/Air Source [11] - Prim.Air : Enthalpy | kJ/kg | 0.86495 | 0.86495
93¦~11~3~4~~-1~ | Gas/Air Source [11] - Prim.Air : Mass flow | t/h | 372.8713 | 372.8713
93¦~11~3~5~~-1~ | Gas/Air Source [11] - Prim.Air : Molecular weight |  | 28.7728 | 28.7728
93¦~11~3~11~~-1~ | Gas/Air Source [11] - Prim.Air : N2 mole percent | % | 76.6959 | 76.6959
93¦~11~3~12~~-1~ | Gas/Air Source [11] - Prim.Air : O2 mole percent | % | 20.5782 | 20.5782
93¦~11~3~13~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mole percent | % | 0.029766 | 0.029766
93¦~11~3~14~~-1~ | Gas/Air Source [11] - Prim.Air : H2O mole percent | % | 1.7725 | 1.7725
93¦~11~3~15~~-1~ | Gas/Air Source [11] - Prim.Air : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - Prim.Air : Ar mole percent | % | 0.92367 | 0.92367
93¦~11~3~20~~-1~ | Gas/Air Source [11] - Prim.Air : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - Prim.Air : CO2 mass flow | t/h | 0.16976 | 0.16976
82¦71¦~40~10~3~~-168~ | General Pump [40] - CP : Mode |  | TD | TD
82¦71¦~40~10~7~~-168~ | General Pump [40] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~40~10~6~~-168~ | General Pump [40] - CP : Pump head | m | 115.1506 | 115.1506
83¦93¦~40~3~15~~-168~ | General Pump [40] - CP : Pressure rise before control valve | bar | 11.1808 | 11.1808
83¦93¦~40~3~18~~-168~ | General Pump [40] - CP : Pressure rise after valve pressure drop | bar | 11.1808 | 11.1808
83¦93¦~40~3~16~~-168~ | General Pump [40] - CP : Pressure drop across valve | bar | 2.6301e-07 | 2.6301e-07
83¦93¦~40~3~12~~-168~ | General Pump [40] - CP : Apparent isentropic efficiency | % | 74.9999 | 74.9999
83¦93¦~40~3~13~~-168~ | General Pump [40] - CP : Shaft work per station | kW | 371.5825 | 371.5825
82¦71¦~40~10~1~~-168~ | General Pump [40] - CP : Hydraulic work per station | kW | 360.4351 | 360.4351
82¦71¦~40~10~2~~-168~ | General Pump [40] - CP : Electricity consumption per station | kW | 387.63 | 387.63
83¦93¦~40~3~5~~-168~ | General Pump [40] - CP : Suction flow | t/h | 861.8255 | 861.8255
83¦93¦~40~3~27~~-168~ | General Pump [40] - CP : Suction pressure | bar | 0.45641 | 0.45641
83¦93¦~40~3~28~~-168~ | General Pump [40] - CP : Suction temperature | C | 45.2485 | 45.2485
83¦93¦~40~3~4~~-168~ | General Pump [40] - CP : Suction enthalpy | kJ/kg | 189.4536 | 189.4536
83¦93¦~40~3~8~~-168~ | General Pump [40] - CP : Discharge flow | t/h | 861.8255 | 861.8255
83¦93¦~40~3~29~~-168~ | General Pump [40] - CP : Discharge pressure | bar | 11.6372 | 11.6372
83¦93¦~40~3~6~~-168~ | General Pump [40] - CP : Discharge temperature | C | 45.3735 | 45.3735
83¦93¦~40~3~7~~-168~ | General Pump [40] - CP : Discharge enthalpy | kJ/kg | 190.9592 | 190.9592
82¦71¦~40~6~1~1000~-168~ | General Pump [40] - CP : Motor: Mode |  | Design | Design
91¦~40~1~7~1000~-168~ | General Pump [40] - CP : Motor: Nameplate power | kW | 395.8567 | 395.8567
91¦~40~1~19~1000~-168~ | General Pump [40] - CP : Motor: Nameplate efficiency | % | 95.8689 | 95.8689
91¦~40~1~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate / Design point load |  | 1.0212 | 1.0212
76¦~40~2~8~1000~-168~ | General Pump [40] - CP : Motor: Number of operating units |  | 1 | 1
93¦~40~7~2~1000~-168~ | General Pump [40] - CP : Motor: Electricity consumption | kW | 387.63 | 387.63
93¦~40~7~6~1000~-168~ | General Pump [40] - CP : Motor: Shaft power | kW | 371.5825 | 371.5825
93¦~40~7~4~1000~-168~ | General Pump [40] - CP : Motor: Efficiency | % | 95.8601 | 95.8601
93¦~40~7~3~1000~-168~ | General Pump [40] - CP : Motor: Electrical loss | kW | 16.0475 | 16.0475
89¦~40~3~5~1000~-168~ | General Pump [40] - CP : Motor: Nameplate motor shaft power | kW | 379.4686 | 379.4686
93¦~6~3~1~~-46~ | Makeup / Blowdown [6] : Makeup flow | t/h | 2.9718 | 2.9718
93¦~6~3~3~~-46~ | Makeup / Blowdown [6] : Makeup temperature | C | 25 | 25
93¦~6~3~2~~-46~ | Makeup / Blowdown [6] : Makeup enthalpy | kJ/kg | 104.9292 | 104.9292
93¦~6~3~4~~-46~ | Makeup / Blowdown [6] : Blowdown flow | t/h | 0 | 0
93¦~6~3~6~~-46~ | Makeup / Blowdown [6] : Blowdown temperature | C | 45.3184 | 45.3184
93¦~6~3~5~~-46~ | Makeup / Blowdown [6] : Blowdown enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~11~~-46~ | Makeup / Blowdown [6] : Inlet pressure | bar | 0.45641 | 0.45641
93¦~6~3~12~~-46~ | Makeup / Blowdown [6] : Inlet flow | t/h | 858.8537 | 858.8537
93¦~6~3~14~~-46~ | Makeup / Blowdown [6] : Inlet temperature | C | 45.3184 | 45.3184
93¦~6~3~13~~-46~ | Makeup / Blowdown [6] : Inlet enthalpy | kJ/kg | 189.7461 | 189.7461
93¦~6~3~22~~-46~ | Makeup / Blowdown [6] : Outlet flow | t/h | 861.8255 | 861.8255
93¦~6~3~24~~-46~ | Makeup / Blowdown [6] : Outlet temperature | C | 45.2485 | 45.2485
93¦~6~3~23~~-46~ | Makeup / Blowdown [6] : Outlet enthalpy | kJ/kg | 189.4536 | 189.4536
91¦~21~1~1~~-6~ | Mixer [21] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~21~1~3~~-6~ | Mixer [21] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~21~3~1~~-6~ | Mixer [21] : Actual mass flow fraction of 1st clockwise inlet |  | 3.1287e-10 | 3.1287e-10
93¦~21~3~3~~-6~ | Mixer [21] : Actual mass flow fraction of 3rd clockwise inlet |  | 1 | 1
91¦~25~1~1~~-6~ | Mixer [25] : Desired mass flow fraction into 1st clockwise node |  | 0.99 | 0.99
91¦~25~1~3~~-6~ | Mixer [25] : Desired mass flow fraction into 3rd clockwise node |  | 0.01 | 0.01
93¦~25~3~1~~-6~ | Mixer [25] : Actual mass flow fraction of 1st clockwise inlet |  | 1 | 1
93¦~25~3~3~~-6~ | Mixer [25] : Actual mass flow fraction of 3rd clockwise inlet |  | 3.1528e-10 | 3.1528e-10
91¦~30~1~1~~-6~ | Mixer [30] : Desired mass flow fraction into 1st clockwise node |  | 0.3 | 0.3
91¦~30~1~3~~-6~ | Mixer [30] : Desired mass flow fraction into 3rd clockwise node |  | 0.7 | 0.7
93¦~30~3~1~~-6~ | Mixer [30] : Actual mass flow fraction of 1st clockwise inlet |  | 0.3 | 0.3
93¦~30~3~3~~-6~ | Mixer [30] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.7 | 0.7
91¦~33~1~1~~-6~ | Mixer [33] : Desired mass flow fraction into 1st clockwise node |  | 0.10989 | 0.10989
91¦~33~1~2~~-6~ | Mixer [33] : Desired mass flow fraction into 2nd clockwise node |  | 0.89011 | 0.89011
93¦~33~3~1~~-6~ | Mixer [33] : Actual mass flow fraction of 1st clockwise inlet |  | 0.10989 | 0.10989
93¦~33~3~2~~-6~ | Mixer [33] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.89011 | 0.89011
91¦~39~1~2~~-6~ | Mixer [39] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
91¦~39~1~3~~-6~ | Mixer [39] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~39~3~2~~-6~ | Mixer [39] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99582 | 0.99582
93¦~39~3~3~~-6~ | Mixer [39] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.0041809 | 0.0041809
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.10761 | 0.10761
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.1 | 0.1
91¦~62~1~3~~-6~ | Mixer [62] : Desired mass flow fraction into 3rd clockwise node |  | 0.79239 | 0.79239
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.94235 | 0.94235
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.0012893 | 0.0012893
93¦~62~3~3~~-6~ | Mixer [62] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.056364 | 0.056364
91¦~85~1~1~~-6~ | Mixer [85] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~85~1~3~~-6~ | Mixer [85] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~85~3~1~~-6~ | Mixer [85] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~85~3~3~~-6~ | Mixer [85] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~87~1~1~~-6~ | Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.50163 | 0.50163
93¦~87~3~3~~-6~ | Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.49837 | 0.49837
91¦~90~1~1~~-6~ | Mixer [90] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~90~1~3~~-6~ | Mixer [90] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~90~3~1~~-6~ | Mixer [90] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~90~3~3~~-6~ | Mixer [90] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
~35~6~5~~-107~ | Pipe (PCE) [35] : Mode |  | TD | TD
~35~6~1~~-107~ | Pipe (PCE) [35] : Pressure drop from inlet to exit | bar | 1.1714 | 1.1714
~35~6~2~~-107~ | Pipe (PCE) [35] : Pressure drop as percent of exit pressure | % | 2 | 2
~35~6~4~~-107~ | Pipe (PCE) [35] : Heat loss | kW | 20.9635 | 20.9635
~36~6~5~~-107~ | Pipe (PCE) [36] : Mode |  | TD | TD
~36~6~1~~-107~ | Pipe (PCE) [36] : Pressure drop from inlet to exit | bar | 0.70157 | 0.70157
~36~6~2~~-107~ | Pipe (PCE) [36] : Pressure drop as percent of exit pressure | % | 2 | 2
~36~6~4~~-107~ | Pipe (PCE) [36] : Heat loss | kW | 24.5109 | 24.5109
~37~6~5~~-107~ | Pipe (PCE) [37] : Mode |  | TD | TD
~37~6~1~~-107~ | Pipe (PCE) [37] : Pressure drop from inlet to exit | bar | 0.34196 | 0.34196
~37~6~2~~-107~ | Pipe (PCE) [37] : Pressure drop as percent of exit pressure | % | 2 | 2
~37~6~4~~-107~ | Pipe (PCE) [37] : Heat loss | kW | 9.0082 | 9.0082
~60~6~5~~-107~ | Pipe (PCE) [60] : Mode |  | TD | TD
~60~6~1~~-107~ | Pipe (PCE) [60] : Pressure drop from inlet to exit | bar | 0.076078 | 0.076078
~60~6~2~~-107~ | Pipe (PCE) [60] : Pressure drop as percent of exit pressure | % | 2 | 2
~60~6~4~~-107~ | Pipe (PCE) [60] : Heat loss | kW | 12.8623 | 12.8623
~61~6~5~~-107~ | Pipe (PCE) [61] : Mode |  | TD | TD
~61~6~1~~-107~ | Pipe (PCE) [61] : Pressure drop from inlet to exit | bar | 0.028824 | 0.028824
~61~6~2~~-107~ | Pipe (PCE) [61] : Pressure drop as percent of exit pressure | % | 2 | 2
~61~6~4~~-107~ | Pipe (PCE) [61] : Heat loss | kW | 7.9116 | 7.9116
~63~6~5~~-107~ | Pipe (PCE) [63] : Mode |  | TD | TD
~63~6~1~~-107~ | Pipe (PCE) [63] : Pressure drop from inlet to exit | bar | 0.015294 | 0.015294
~63~6~2~~-107~ | Pipe (PCE) [63] : Pressure drop as percent of exit pressure | % | 2 | 2
~63~6~4~~-107~ | Pipe (PCE) [63] : Heat loss | kW | 8.7119 | 8.7119
~64~6~5~~-107~ | Pipe (PCE) [64] : Mode |  | TD | TD
~64~6~1~~-107~ | Pipe (PCE) [64] : Pressure drop from inlet to exit | bar | 0.005549 | 0.005549
~64~6~2~~-107~ | Pipe (PCE) [64] : Pressure drop as percent of exit pressure | % | 2 | 2
~64~6~4~~-107~ | Pipe (PCE) [64] : Heat loss | kW | 6.0298 | 6.0298
~73~6~5~~-107~ | Pipe (PCE) [73] : Mode |  | TD | TD
~73~6~1~~-107~ | Pipe (PCE) [73] : Pressure drop from inlet to exit | bar | 0.19314 | 0.19314
~73~6~2~~-107~ | Pipe (PCE) [73] : Pressure drop as percent of exit pressure | % | 2 | 2
~73~6~4~~-107~ | Pipe (PCE) [73] : Heat loss | kW | 16.6299 | 16.6299
~74~6~5~~-107~ | Pipe (PCE) [74] : Mode |  | TD | TD
~74~6~1~~-107~ | Pipe (PCE) [74] : Pressure drop from inlet to exit | bar | 1.625 | 1.625
~74~6~2~~-107~ | Pipe (PCE) [74] : Pressure drop as percent of exit pressure | % | 1 | 1
~74~6~4~~-107~ | Pipe (PCE) [74] : Heat loss | kW | 525.4052 | 525.4052
~75~6~5~~-107~ | Pipe (PCE) [75] : Mode |  | TD | TD
~75~6~1~~-107~ | Pipe (PCE) [75] : Pressure drop from inlet to exit | bar | 0.326 | 0.326
~75~6~2~~-107~ | Pipe (PCE) [75] : Pressure drop as percent of exit pressure | % | 1 | 1
~75~6~4~~-107~ | Pipe (PCE) [75] : Heat loss | kW | 445.2547 | 445.2547
~76~6~5~~-107~ | Pipe (PCE) [76] : Mode |  | TD | TD
~76~6~1~~-107~ | Pipe (PCE) [76] : Pressure drop from inlet to exit | bar | 1.725 | 1.725
~76~6~2~~-107~ | Pipe (PCE) [76] : Pressure drop as percent of exit pressure | % | 1 | 1
~76~6~4~~-107~ | Pipe (PCE) [76] : Heat loss | kW | 307.954 | 307.954
82¦71¦~82~10~3~~-100~ | Pump (PCE) [82] - CWP-1 : Mode |  | TD | TD
82¦71¦~82~10~7~~-100~ | Pump (PCE) [82] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~82~10~6~~-100~ | Pump (PCE) [82] - CWP-1 : Pump head | m | 28.9733 | 28.9733
83¦93¦~82~3~15~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~82~3~18~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~82~3~16~~-100~ | Pump (PCE) [82] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~82~3~12~~-100~ | Pump (PCE) [82] - CWP-1 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~82~3~13~~-100~ | Pump (PCE) [82] - CWP-1 : Shaft work per station | kW | 2116.6816 | 2116.6816
82¦71¦~82~10~1~~-100~ | Pump (PCE) [82] - CWP-1 : Hydraulic work per station | kW | 2053.1814 | 2053.1814
82¦71¦~82~10~2~~-100~ | Pump (PCE) [82] - CWP-1 : Electricity consumption per station | kW | 2185.7017 | 2185.7017
83¦93¦~82~3~5~~-100~ | Pump (PCE) [82] - CWP-1 : Suction flow | t/h | 19511.1836 | 19511.1836
83¦93¦~82~3~27~~-100~ | Pump (PCE) [82] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~82~3~28~~-100~ | Pump (PCE) [82] - CWP-1 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~82~3~4~~-100~ | Pump (PCE) [82] - CWP-1 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~82~3~8~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge flow | t/h | 19511.1836 | 19511.1836
83¦93¦~82~3~29~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~82~3~6~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~82~3~7~~-100~ | Pump (PCE) [82] - CWP-1 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~82~6~1~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Mode |  | Design | Design
91¦~82~1~7~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate power | kW | 2262.0662 | 2262.0662
91¦~82~1~19~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate efficiency | % | 96.8532 | 96.8532
91¦~82~1~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~82~2~8~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~82~7~2~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electricity consumption | kW | 2185.7017 | 2185.7017
93¦~82~7~6~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Shaft power | kW | 2116.6816 | 2116.6816
93¦~82~7~4~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Efficiency | % | 96.8422 | 96.8422
93¦~82~7~3~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Electrical loss | kW | 69.0199 | 69.0199
89¦~82~3~5~1000~-100~ | Pump (PCE) [82] - CWP-1 : Motor: Nameplate motor shaft power | kW | 2190.6348 | 2190.6348
82¦71¦~83~10~3~~-100~ | Pump (PCE) [83] - CWP-2 : Mode |  | TD | TD
82¦71¦~83~10~7~~-100~ | Pump (PCE) [83] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~83~10~6~~-100~ | Pump (PCE) [83] - CWP-2 : Pump head | m | 28.9733 | 28.9733
83¦93¦~83~3~15~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise before control valve | bar | 2.8312 | 2.8312
83¦93¦~83~3~18~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.8312 | 2.8312
83¦93¦~83~3~16~~-100~ | Pump (PCE) [83] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~83~3~12~~-100~ | Pump (PCE) [83] - CWP-2 : Apparent isentropic efficiency | % | 74.9992 | 74.9992
83¦93¦~83~3~13~~-100~ | Pump (PCE) [83] - CWP-2 : Shaft work per station | kW | 2116.6816 | 2116.6816
82¦71¦~83~10~1~~-100~ | Pump (PCE) [83] - CWP-2 : Hydraulic work per station | kW | 2053.1814 | 2053.1814
82¦71¦~83~10~2~~-100~ | Pump (PCE) [83] - CWP-2 : Electricity consumption per station | kW | 2185.7017 | 2185.7017
83¦93¦~83~3~5~~-100~ | Pump (PCE) [83] - CWP-2 : Suction flow | t/h | 19511.1836 | 19511.1836
83¦93¦~83~3~27~~-100~ | Pump (PCE) [83] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~83~3~28~~-100~ | Pump (PCE) [83] - CWP-2 : Suction temperature | C | 27.3223 | 27.3223
83¦93¦~83~3~4~~-100~ | Pump (PCE) [83] - CWP-2 : Suction enthalpy | kJ/kg | 114.5466 | 114.5466
83¦93¦~83~3~8~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge flow | t/h | 19511.1836 | 19511.1836
83¦93¦~83~3~29~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge pressure | bar | 3.8447 | 3.8447
83¦93¦~83~3~6~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge temperature | C | 27.3502 | 27.3502
83¦93¦~83~3~7~~-100~ | Pump (PCE) [83] - CWP-2 : Discharge enthalpy | kJ/kg | 114.9254 | 114.9254
82¦71¦~83~6~1~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Mode |  | Design | Design
91¦~83~1~7~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate power | kW | 2262.0662 | 2262.0662
91¦~83~1~19~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate efficiency | % | 96.8532 | 96.8532
91¦~83~1~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~83~2~8~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~83~7~2~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electricity consumption | kW | 2185.7017 | 2185.7017
93¦~83~7~6~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Shaft power | kW | 2116.6816 | 2116.6816
93¦~83~7~4~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Efficiency | % | 96.8422 | 96.8422
93¦~83~7~3~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Electrical loss | kW | 69.0199 | 69.0199
89¦~83~3~5~1000~-100~ | Pump (PCE) [83] - CWP-2 : Motor: Nameplate motor shaft power | kW | 2190.6348 | 2190.6348
93¦~8~3~64~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Primary air path heat transfer | kW | 23841.3887 | 23841.3887
93¦~8~3~44~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Secondary air path heat transfer | kW | 84779.9609 | 84779.9609
82¦71¦~8~5~1~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Total heat transfer | kW | 108621.3438 | 108621.3438
93¦~8~3~69~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Heat transfer duty ratio (Qpa / Qsa) | % | 28.1215 | 28.1215
93¦~8~3~24~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Average cold end temperature (ACET) | C | 86.871 | 86.871
93¦~8~3~191~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O dew point temperature | C | 49.336 | 49.336
93¦~8~3~138~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit sulfur dew point temperature | C | -273.15 | -273.15
93¦~8~3~139~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas sulfur dew point temperature within air heater | C | -273.15 | -273.15
93¦~8~3~11~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit O2 mol% | % | 5.1748 | 5.1748
93¦~8~3~12~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit CO2 mol% | % | 11.8816 | 11.8816
93¦~8~3~13~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit H2O mol% | % | 12.0931 | 12.0931
82¦71¦~8~5~2~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit N2 mol% | % | 69.9911 | 69.9911
93¦~8~3~132~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit Ar mol% | % | 0.84192 | 0.84192
93¦~8~3~131~~-120~ | Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Flue gas exit SO2 mol% | % | 0.017411 | 0.017411
82¦71¦~1~5~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~1~5~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~1~1~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of existing units |  | 1 | 1
93¦~1~3~20~~-85~ | ST-Driven Pump [1] - BFPT-A : Number of operating units |  | 1 | 1
93¦~1~3~19~~-85~ | ST-Driven Pump [1] - BFPT-A : Total shaft power | kW | 4218.3604 | 4218.3604
93¦~1~3~1~~-85~ | ST-Driven Pump [1] - BFPT-A : Shaft power per unit | kW | 4218.3604 | 4218.3604
93¦~1~3~2~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping power per unit | kW | 4086.3577 | 4086.3577
93¦~1~3~3~~-85~ | ST-Driven Pump [1] - BFPT-A : Pumping flow per unit | t/h | 558.9188 | 558.9188
93¦~1~3~4~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump pressure rise (before control valve) | bar | 174.5563 | 174.5563
93¦~1~3~5~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall pressure rise | bar | 174.5563 | 174.5563
93¦~1~3~6~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~1~3~7~~-85~ | ST-Driven Pump [1] - BFPT-A : Pump overall apparent isentropic efficiency | % | 74.4499 | 74.4499
93¦~1~3~8~~-85~ | ST-Driven Pump [1] - BFPT-A : Current RPM |  | 3600.0005 | 3600.0005
93¦~1~3~9~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical loss per unit | kW | 132.0026 | 132.0026
93¦~1~3~10~~-85~ | ST-Driven Pump [1] - BFPT-A : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~1~10~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Type of inlet control |  | Sliding | Sliding
93¦~1~3~29~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Steam supply pressure | bar | 9.85 | 9.85
93¦~1~3~11~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet pressure | bar | 8.98 | 8.98
93¦~1~3~12~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet temperature | C | 360.6185 | 360.6185
93¦~1~3~14~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet flow per unit | t/h | 20.6528 | 20.6528
93¦~1~3~13~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Inlet enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~1~3~16~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion massflow per unit | t/h | 20.6528 | 20.6528
93¦~1~3~4~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial pressure | bar | 8.98 | 8.98
93¦~1~3~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion initial enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~1~3~6~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~1~3~25~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2443.8579 | 2443.8579
93¦~1~3~21~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~1~3~22~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~1~3~24~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet flow per unit | t/h | 20.6528 | 20.6528
93¦~1~3~23~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Outlet enthalpy | kJ/kg | 2443.8579 | 2443.8579
72¦79¦93¦~1~7~15~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust volume flow per unit | m^3/s | 81.178 | 81.178
72¦79¦93¦~1~7~18~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~1~7~17~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~1~3~7~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual flow function | m^2 | 0.0051317 | 0.0051317
93¦~1~3~10~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Actual pressure ratio (blading) |  | 92.1026 | 92.1026
93¦~1~3~3~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Dry step efficiency | % | 85 | 85
93¦~1~3~1~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group overall efficiency | % | 87.4281 | 87.4281
93¦~1~3~30~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Group blading efficiency | % | 87.4281 | 87.4281
93¦~1~3~50~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Expansion power per unit | kW | 4228.9331 | 4228.9331
93¦~1~3~9~1~-85~ | ST-Driven Pump [1] - BFPT-A : ST: Mechanical loss per unit | kW | 10.5723 | 10.5723
82¦71¦~86~5~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mode |  | TD - Variable RPM | TD - Variable RPM
82¦71¦~86~5~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Actual operating mode |  | TD - Variable RPM | TD - Variable RPM
91¦~86~1~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of existing units |  | 1 | 1
93¦~86~3~20~~-85~ | ST-Driven Pump [86] - BFPT-B : Number of operating units |  | 1 | 1
93¦~86~3~19~~-85~ | ST-Driven Pump [86] - BFPT-B : Total shaft power | kW | 4218.3604 | 4218.3604
93¦~86~3~1~~-85~ | ST-Driven Pump [86] - BFPT-B : Shaft power per unit | kW | 4218.3604 | 4218.3604
93¦~86~3~2~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping power per unit | kW | 4086.3577 | 4086.3577
93¦~86~3~3~~-85~ | ST-Driven Pump [86] - BFPT-B : Pumping flow per unit | t/h | 558.9188 | 558.9188
93¦~86~3~4~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump pressure rise (before control valve) | bar | 174.5563 | 174.5563
93¦~86~3~5~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall pressure rise | bar | 174.5563 | 174.5563
93¦~86~3~6~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump isentropic efficiency | % | 74.45 | 74.45
93¦~86~3~7~~-85~ | ST-Driven Pump [86] - BFPT-B : Pump overall apparent isentropic efficiency | % | 74.4499 | 74.4499
93¦~86~3~8~~-85~ | ST-Driven Pump [86] - BFPT-B : Current RPM |  | 3000.0002 | 3000.0002
93¦~86~3~9~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical loss per unit | kW | 132.0026 | 132.0026
93¦~86~3~10~~-85~ | ST-Driven Pump [86] - BFPT-B : Mechanical efficiency | % | 96.8708 | 96.8708
82¦71¦~86~10~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Type of inlet control |  | Sliding | Sliding
93¦~86~3~29~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Steam supply pressure | bar | 9.85 | 9.85
93¦~86~3~11~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet pressure | bar | 9.36 | 9.36
93¦~86~3~12~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet temperature | C | 360.6185 | 360.6185
93¦~86~3~14~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet flow per unit | t/h | 20.5189 | 20.5189
93¦~86~3~13~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Inlet enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~86~3~16~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion massflow per unit | t/h | 20.5189 | 20.5189
93¦~86~3~4~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial pressure | bar | 9.36 | 9.36
93¦~86~3~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion initial enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~86~3~6~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~86~3~25~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2439.0479 | 2439.0479
93¦~86~3~21~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet pressure | bar | 0.0975 | 0.0975
93¦~86~3~22~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet temperature | C | 45.3132 | 45.3132
93¦~86~3~24~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet flow per unit | t/h | 20.5189 | 20.5189
93¦~86~3~23~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Outlet enthalpy | kJ/kg | 2439.0479 | 2439.0479
72¦79¦93¦~86~7~15~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust volume flow per unit | m^3/s | 80.4796 | 80.4796
72¦79¦93¦~86~7~18~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~86~7~17~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry exhaust loss | kJ/kg | 0 | 0
93¦~86~3~7~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual flow function | m^2 | 0.0048913 | 0.0048913
93¦~86~3~10~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Actual pressure ratio (blading) |  | 96 | 96
93¦~86~3~3~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Dry step efficiency | % | 85 | 85
93¦~86~3~1~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group overall efficiency | % | 87.377 | 87.377
93¦~86~3~30~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Group blading efficiency | % | 87.377 | 87.377
93¦~86~3~50~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Expansion power per unit | kW | 4228.9326 | 4228.9326
93¦~86~3~9~1~-85~ | ST-Driven Pump [86] - BFPT-B : ST: Mechanical loss per unit | kW | 10.5723 | 10.5723
91¦~34~1~13~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~34~1~71~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~34~3~7~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer | kW | 418.6735 | 418.6735
91¦~34~1~101~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Feedwater temperature rise (overall) | C | 0.42585 | 0.42585
82¦71¦~34~5~2~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Terminal difference | C | 11.4013 | 11.4013
91¦~34~1~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total heat transfer area | m^2 | 65.2424 | 65.2424
91¦~34~1~82~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~34~3~52~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell length | m | 0 | 0
89¦~34~3~53~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Shell inner diameter | m | 1.1308 | 1.1308
89¦~34~3~56~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall length | m | 0 | 0
89¦~34~3~27~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Overall outer diameter | m | 0 | 0
89¦~34~3~45~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total dry weight | kg | 0 | 0
89¦~34~3~57~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~34~5~5~~-127~ | Shell-Tube Water Heater (PCE) [34] - GC : Total estimated installed cost | USD | 0 | 0
91¦~4~1~1~~-7~ | Splitter [4] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~4~1~3~~-7~ | Splitter [4] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~4~3~1~~-7~ | Splitter [4] : Actual flow fraction of 1st clockwise outlet |  | 0.96942 | 0.96942
93¦~4~3~3~~-7~ | Splitter [4] : Actual flow fraction of 3rd clockwise outlet |  | 0.030584 | 0.030584
91¦~9~1~1~~-7~ | Splitter [9] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~9~1~3~~-7~ | Splitter [9] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~9~3~1~~-7~ | Splitter [9] : Actual flow fraction of 1st clockwise outlet |  | 0.83091 | 0.83091
93¦~9~3~3~~-7~ | Splitter [9] : Actual flow fraction of 3rd clockwise outlet |  | 0.16909 | 0.16909
91¦~18~1~1~~-7~ | Splitter [18] : Desired flow fraction of 1st clockwise node |  | 0.0001 | 0.0001
91¦~18~1~2~~-7~ | Splitter [18] : Desired flow fraction of 2nd clockwise node |  | 0.0001 | 0.0001
91¦~18~1~3~~-7~ | Splitter [18] : Desired flow fraction of 3rd clockwise node |  | 0.9998 | 0.9998
93¦~18~3~1~~-7~ | Splitter [18] : Actual flow fraction of 1st clockwise outlet |  | 2.6443e-10 | 2.6443e-10
93¦~18~3~2~~-7~ | Splitter [18] : Actual flow fraction of 2nd clockwise outlet |  | 2.6443e-10 | 2.6443e-10
93¦~18~3~3~~-7~ | Splitter [18] : Actual flow fraction of 3rd clockwise outlet |  | 1 | 1
91¦~19~1~1~~-7~ | Splitter [19] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~19~1~3~~-7~ | Splitter [19] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~19~3~1~~-7~ | Splitter [19] : Actual flow fraction of 1st clockwise outlet |  | 0.93213 | 0.93213
93¦~19~3~3~~-7~ | Splitter [19] : Actual flow fraction of 3rd clockwise outlet |  | 0.067866 | 0.067866
91¦~20~1~1~~-7~ | Splitter [20] : Desired flow fraction of 1st clockwise node |  | 0.8 | 0.8
91¦~20~1~2~~-7~ | Splitter [20] : Desired flow fraction of 2nd clockwise node |  | 0.195 | 0.195
91¦~20~1~3~~-7~ | Splitter [20] : Desired flow fraction of 3rd clockwise node |  | 0.005 | 0.005
93¦~20~3~1~~-7~ | Splitter [20] : Actual flow fraction of 1st clockwise outlet |  | 0.90853 | 0.90853
93¦~20~3~2~~-7~ | Splitter [20] : Actual flow fraction of 2nd clockwise outlet |  | 0.085127 | 0.085127
93¦~20~3~3~~-7~ | Splitter [20] : Actual flow fraction of 3rd clockwise outlet |  | 0.0063468 | 0.0063468
91¦~22~1~1~~-7~ | Splitter [22] : Desired flow fraction of 1st clockwise node |  | 0.001 | 0.001
91¦~22~1~2~~-7~ | Splitter [22] : Desired flow fraction of 2nd clockwise node |  | 0.00057 | 0.00057
91¦~22~1~3~~-7~ | Splitter [22] : Desired flow fraction of 3rd clockwise node |  | 0.99843 | 0.99843
93¦~22~3~1~~-7~ | Splitter [22] : Actual flow fraction of 1st clockwise outlet |  | 0.001 | 0.001
93¦~22~3~2~~-7~ | Splitter [22] : Actual flow fraction of 2nd clockwise outlet |  | 0.00057 | 0.00057
93¦~22~3~3~~-7~ | Splitter [22] : Actual flow fraction of 3rd clockwise outlet |  | 0.99843 | 0.99843
91¦~27~1~1~~-7~ | Splitter [27] : Desired flow fraction of 1st clockwise node |  | 0.9999 | 0.9999
91¦~27~1~3~~-7~ | Splitter [27] : Desired flow fraction of 3rd clockwise node |  | 0.00010002 | 0.00010002
93¦~27~3~1~~-7~ | Splitter [27] : Actual flow fraction of 1st clockwise outlet |  | 0.98968 | 0.98968
93¦~27~3~3~~-7~ | Splitter [27] : Actual flow fraction of 3rd clockwise outlet |  | 0.010319 | 0.010319
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.9668 | 0.9668
91¦~29~1~3~~-7~ | Splitter [29] : Desired flow fraction of 3rd clockwise node |  | 0.0332 | 0.0332
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.97567 | 0.97567
93¦~29~3~3~~-7~ | Splitter [29] : Actual flow fraction of 3rd clockwise outlet |  | 0.024329 | 0.024329
91¦~32~1~1~~-7~ | Splitter [32] : Desired flow fraction of 1st clockwise node |  | 0.0417 | 0.0417
91¦~32~1~2~~-7~ | Splitter [32] : Desired flow fraction of 2nd clockwise node |  | 0.8005 | 0.8005
91¦~32~1~3~~-7~ | Splitter [32] : Desired flow fraction of 3rd clockwise node |  | 0.1578 | 0.1578
93¦~32~3~1~~-7~ | Splitter [32] : Actual flow fraction of 1st clockwise outlet |  | 0.045224 | 0.045224
93¦~32~3~2~~-7~ | Splitter [32] : Actual flow fraction of 2nd clockwise outlet |  | 0.89624 | 0.89624
93¦~32~3~3~~-7~ | Splitter [32] : Actual flow fraction of 3rd clockwise outlet |  | 0.058535 | 0.058535
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~49~1~3~~-7~ | Splitter [49] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.94325 | 0.94325
93¦~49~3~3~~-7~ | Splitter [49] : Actual flow fraction of 3rd clockwise outlet |  | 0.056752 | 0.056752
91¦~50~1~1~~-7~ | Splitter [50] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~50~1~3~~-7~ | Splitter [50] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~50~3~1~~-7~ | Splitter [50] : Actual flow fraction of 1st clockwise outlet |  | 0.96299 | 0.96299
93¦~50~3~3~~-7~ | Splitter [50] : Actual flow fraction of 3rd clockwise outlet |  | 0.037008 | 0.037008
91¦~51~1~1~~-7~ | Splitter [51] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~51~1~3~~-7~ | Splitter [51] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~51~3~1~~-7~ | Splitter [51] : Actual flow fraction of 1st clockwise outlet |  | 0.95768 | 0.95768
93¦~51~3~3~~-7~ | Splitter [51] : Actual flow fraction of 3rd clockwise outlet |  | 0.042318 | 0.042318
91¦~70~1~1~~-7~ | Splitter [70] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~70~1~3~~-7~ | Splitter [70] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~70~3~1~~-7~ | Splitter [70] : Actual flow fraction of 1st clockwise outlet |  | 0.38141 | 0.38141
93¦~70~3~3~~-7~ | Splitter [70] : Actual flow fraction of 3rd clockwise outlet |  | 0.61859 | 0.61859
91¦~71~1~1~~-7~ | Splitter [71] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~71~1~2~~-7~ | Splitter [71] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~71~1~3~~-7~ | Splitter [71] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~71~3~1~~-7~ | Splitter [71] : Actual flow fraction of 1st clockwise outlet |  | 0.0022644 | 0.0022644
93¦~71~3~2~~-7~ | Splitter [71] : Actual flow fraction of 2nd clockwise outlet |  | 0.0059414 | 0.0059414
93¦~71~3~3~~-7~ | Splitter [71] : Actual flow fraction of 3rd clockwise outlet |  | 0.99179 | 0.99179
91¦~84~1~1~~-7~ | Splitter [84] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~84~1~3~~-7~ | Splitter [84] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~84~3~1~~-7~ | Splitter [84] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~84~3~3~~-7~ | Splitter [84] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~88~1~1~~-7~ | Splitter [88] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~88~1~3~~-7~ | Splitter [88] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~88~3~1~~-7~ | Splitter [88] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~88~3~3~~-7~ | Splitter [88] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~89~1~1~~-7~ | Splitter [89] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~89~1~3~~-7~ | Splitter [89] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~89~3~1~~-7~ | Splitter [89] : Actual flow fraction of 1st clockwise outlet |  | 0.50163 | 0.50163
93¦~89~3~3~~-7~ | Splitter [89] : Actual flow fraction of 3rd clockwise outlet |  | 0.49837 | 0.49837
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 144.9853 | 144.9853
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 49.8496 | 49.8496
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 143.5011 | 143.5011
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 7890.0283 | 7890.0283
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 5.1748 | 5.1748
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 11.8816 | 11.8816
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 12.0931 | 12.0931
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 69.9911 | 69.9911
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.84192 | 0.84192
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.017411 | 0.017411
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 201.5119 | 201.5119
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 561.7842 | 561.7842
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 196.5543 | 196.5543
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.031206 | 0.031206
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 8.9675 | 8.9675
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 25.0001 | 25.0001
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 5.1748 | 5.1748
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 12.0931 | 12.0931
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~23~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Mode |  | TD | TD
~23~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet mass flow | t/h | 1110.0084 | 1110.0084
~23~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet pressure | bar | 169.0981 | 169.0981
~23~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet enthalpy | kJ/kg | 3000.8169 | 3000.8169
~23~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam inlet temperature | C | 418.001 | 418.001
~23~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit mass flow | t/h | 1110.0084 | 1110.0084
~23~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit pressure | bar | 167.4239 | 167.4239
~23~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit temperature | C | 490 | 490
~23~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam exit enthalpy | kJ/kg | 3256.6096 | 3256.6096
~23~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas mass flow | t/h | 1667.9181 | 1667.9181
~23~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Flyash mass flow | t/h | 8.1714 | 8.1714
~23~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas inlet temperature | C | 1151 | 1151
~23~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas exit temperature | C | 1029.4705 | 1029.4705
~23~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat transfer to steam | kW | 78871.2812 | 78871.2812
~23~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Heat loss | kW | 591.5347 | 591.5347
~23~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Radiant heat influx | kW | 3855.1636 | 3855.1636
~23~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~23~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH : Steam side pressure drop | bar | 1.6742 | 1.6742
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 1112.5415 | 1112.5415
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 165.7662 | 165.7662
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3333.9304 | 3333.9304
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 514.998 | 514.998
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 1112.5415 | 1112.5415
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 164.125 | 164.125
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 536.8 | 536.8
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3398.4937 | 3398.4937
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 1667.9181 | 1667.9181
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 8.1714 | 8.1714
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 774.2047 | 774.2047
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 740.1719 | 740.1719
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 19952.9355 | 19952.9355
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 149.647 | 149.647
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 1.6412 | 1.6412
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 1105.8999 | 1105.8999
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 170.7891 | 170.7891
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2544.8325 | 2544.8325
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 352.6726 | 352.6726
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 1105.8999 | 1105.8999
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 169.0981 | 169.0981
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 420 | 420
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3009.0886 | 3009.0886
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 1667.9181 | 1667.9181
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 8.1714 | 8.1714
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 740.172 | 740.172
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 489.3695 | 489.3695
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 142619.1094 | 142619.1094
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 1069.6433 | 1069.6433
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 1.691 | 1.691
~77~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Mode |  | TD | TD
~77~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet mass flow | t/h | 942.8237 | 942.8237
~77~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet pressure | bar | 35.78 | 35.78
~77~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet enthalpy | kJ/kg | 3041.0444 | 3041.0444
~77~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam inlet temperature | C | 324.9996 | 324.9996
~77~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit mass flow | t/h | 942.8237 | 942.8237
~77~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit pressure | bar | 35.4257 | 35.4257
~77~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit temperature | C | 511 | 511
~77~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam exit enthalpy | kJ/kg | 3475.947 | 3475.947
~77~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas mass flow | t/h | 1667.9181 | 1667.9181
~77~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Flyash mass flow | t/h | 8.1714 | 8.1714
~77~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas inlet temperature | C | 987.4719 | 987.4719
~77~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas exit temperature | C | 797.6589 | 797.6589
~77~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat transfer to steam | kW | 113900.75 | 113900.75
~77~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Heat loss | kW | 854.2557 | 854.2557
~77~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Radiant heat influx | kW | 0 | 0
~77~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~77~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 : Steam side pressure drop | bar | 0.35426 | 0.35426
~78~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Mode |  | TD | TD
~78~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet mass flow | t/h | 942.8237 | 942.8237
~78~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet pressure | bar | 35.4257 | 35.4257
~78~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet enthalpy | kJ/kg | 3475.947 | 3475.947
~78~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam inlet temperature | C | 511.0026 | 511.0026
~78~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit mass flow | t/h | 942.8237 | 942.8237
~78~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit pressure | bar | 35.075 | 35.075
~78~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit temperature | C | 534.1 | 534.1
~78~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit enthalpy | kJ/kg | 3528.7349 | 3528.7349
~78~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas mass flow | t/h | 1667.9181 | 1667.9181
~78~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Flyash mass flow | t/h | 8.1714 | 8.1714
~78~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas inlet temperature | C | 797.659 | 797.659
~78~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas exit temperature | C | 774.2047 | 774.2047
~78~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat transfer to steam | kW | 13825.1299 | 13825.1299
~78~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Heat loss | kW | 103.6885 | 103.6885
~78~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Radiant heat influx | kW | 0 | 0
~78~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Gas side pressure drop | millibar | 2.4907 | 2.4907
~78~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam side pressure drop | bar | 0.35075 | 0.35075
~79~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Mode |  | TD | TD
~79~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet mass flow | t/h | 1110.0084 | 1110.0084
~79~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet pressure | bar | 167.4239 | 167.4239
~79~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet enthalpy | kJ/kg | 3256.6096 | 3256.6096
~79~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam inlet temperature | C | 489.9974 | 489.9974
~79~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit mass flow | t/h | 1110.0084 | 1110.0084
~79~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit pressure | bar | 165.7662 | 165.7662
~79~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit temperature | C | 517 | 517
~79~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam exit enthalpy | kJ/kg | 3339.772 | 3339.772
~79~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas mass flow | t/h | 1667.9181 | 1667.9181
~79~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Flyash mass flow | t/h | 8.1714 | 8.1714
~79~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas inlet temperature | C | 1029.4706 | 1029.4706
~79~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas exit temperature | C | 987.4717 | 987.4717
~79~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat transfer to steam | kW | 25642.2871 | 25642.2871
~79~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Heat loss | kW | 192.3171 | 192.3171
~79~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Radiant heat influx | kW | 0 | 0
~79~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~79~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH : Steam side pressure drop | bar | 1.6577 | 1.6577
~14~5~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure control mode |  | Down set point | Down set point
~14~5~2~~-32~ | Boiler Assembly [1]: Valve [14] : Valve current status |  | Wide open | Wide open
~14~3~1~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop @ VWO | bar | 0 | 0
~14~3~10~~-32~ | Boiler Assembly [1]: Valve [14] : Pressure drop | bar | 2.149 | 2.149
~14~3~3~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet pressure | bar | 35.075 | 35.075
~14~3~4~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet temperature | C | 534.1036 | 534.1036
~14~3~5~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet enthalpy | kJ/kg | 3528.7349 | 3528.7349
~14~3~6~~-32~ | Boiler Assembly [1]: Valve [14] : Inlet mass flow | t/h | 942.8237 | 942.8237
~14~3~7~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet pressure | bar | 32.926 | 32.926
~14~3~8~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet temperature | C | 533.1637 | 533.1637
~14~3~9~~-32~ | Boiler Assembly [1]: Valve [14] : Outlet enthalpy | kJ/kg | 3528.7349 | 3528.7349
~80~5~1~~-32~ | Valve [80] : Pressure control mode |  | Closed | Closed
~80~5~2~~-32~ | Valve [80] : Valve current status |  | Closed | Closed
~80~3~1~~-32~ | Valve [80] : Pressure drop @ VWO | bar | 0 | 0
~80~3~10~~-32~ | Valve [80] : Pressure drop | bar | 0 | 0
~80~3~3~~-32~ | Valve [80] : Inlet pressure | bar | 35.78 | 35.78
~80~3~4~~-32~ | Valve [80] : Inlet temperature | C | 476.3312 | 476.3312
~80~3~5~~-32~ | Valve [80] : Inlet enthalpy | kJ/kg | 3396.7937 | 3396.7937
~80~3~6~~-32~ | Valve [80] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~80~3~7~~-32~ | Valve [80] : Outlet pressure | bar | 35.78 | 35.78
~80~3~8~~-32~ | Valve [80] : Outlet temperature | C | 476.3312 | 476.3312
~80~3~9~~-32~ | Valve [80] : Outlet enthalpy | kJ/kg | 3396.7937 | 3396.7937
~81~5~1~~-32~ | Valve [81] : Pressure control mode |  | Closed | Closed
~81~5~2~~-32~ | Valve [81] : Valve current status |  | Closed | Closed
~81~3~1~~-32~ | Valve [81] : Pressure drop @ VWO | bar | 0 | 0
~81~3~10~~-32~ | Valve [81] : Pressure drop | bar | 0 | 0
~81~3~3~~-32~ | Valve [81] : Inlet pressure | bar | 32.6 | 32.6
~81~3~4~~-32~ | Valve [81] : Inlet temperature | C | 474.6068 | 474.6068
~81~3~5~~-32~ | Valve [81] : Inlet enthalpy | kJ/kg | 3396.7937 | 3396.7937
~81~3~6~~-32~ | Valve [81] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~81~3~7~~-32~ | Valve [81] : Outlet pressure | bar | 32.6 | 32.6
~81~3~8~~-32~ | Valve [81] : Outlet temperature | C | 474.6068 | 474.6068
~81~3~9~~-32~ | Valve [81] : Outlet enthalpy | kJ/kg | 3396.7937 | 3396.7937
93¦~58~3~1~~-14~ | Water Sink [58] : Pressure | bar | 3.5 | 3.5
93¦~58~3~2~~-14~ | Water Sink [58] : Temperature | C | 37.3673 | 37.3673
93¦~58~3~3~~-14~ | Water Sink [58] : Enthalpy | kJ/kg | 156.7739 | 156.7739
93¦~58~3~4~~-14~ | Water Sink [58] : Mass flow | t/h | 39022.3672 | 39022.3672
93¦~57~3~1~~-9~ | Water Source [57] : Pressure | bar | 1.0135 | 1.0135
93¦~57~3~2~~-9~ | Water Source [57] : Temperature | C | 27.3223 | 27.3223
93¦~57~3~3~~-9~ | Water Source [57] : Enthalpy | kJ/kg | 114.5466 | 114.5466
93¦~57~3~4~~-9~ | Water Source [57] : Mass flow | t/h | 39022.3672 | 39022.3672
~59~10~1~~-104~ | Water-cooled Condenser (PCE) [59] : Mode |  | TD | TD
~59~3~27~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser pressure | bar | 0.0975 | 0.0975
~59~3~26~~-104~ | Water-cooled Condenser (PCE) [59] : Saturation temperature | C | 45.3132 | 45.3132
~59~3~21~~-104~ | Water-cooled Condenser (PCE) [59] : Condenser heat rejection (per unit) | kW | 453625.4062 | 453625.4062
~59~3~23~~-104~ | Water-cooled Condenser (PCE) [59] : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
82¦71¦~1~6~1~~-20000~ | Generator [1]: Mode |  | Design | Design
91¦~1~1~7~~-20000~ | Generator [1]: Nameplate power | kW | 367571 | 367571
91¦~1~1~19~~-20000~ | Generator [1]: Nameplate efficiency | % | 98.9676 | 98.9676
91¦~1~1~5~~-20000~ | Generator [1]: Nameplate / Design point load |  | 1.05 | 1.05
76¦~1~2~8~~-20000~ | Generator [1]: Number of operating units |  | 1 | 1
93¦~1~7~2~~-20000~ | Generator [1]: Generator power output | kW | 350067.625 | 350067.625
93¦~1~7~6~~-20000~ | Generator [1]: Shaft power | kW | 353770.6562 | 353770.6562
93¦~1~7~4~~-20000~ | Generator [1]: Generator efficiency | % | 98.9533 | 98.9533
93¦~1~7~3~~-20000~ | Generator [1]: Total loss | kW | 3703.0332 | 3703.0332
93¦~1~7~28~~-20000~ | Generator [1]: Electrical & Windage loss | kW | 3247.6411 | 3247.6411
93¦~1~7~29~~-20000~ | Generator [1]: Mechanical loss | kW | 455.3922 | 455.3922
86¦87¦68¦86¦86¦~13~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 350067.625 | 350067.625
86¦87¦68¦86¦86¦~13~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.9533 | 98.9533
86¦87¦68¦86¦86¦~13~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 551.3565 | 551.3565
86¦87¦68¦86¦86¦~13~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 183.7855 | 183.7855
86¦87¦68¦86¦86¦~13~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 408.4122 | 408.4122
86¦87¦68¦86¦86¦~13~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~13~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.9676 | 98.9676
86¦87¦68¦86¦86¦~13~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 170.625 | 170.625
86¦87¦68¦86¦86¦~13~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 535.5406 | 535.5406
86¦87¦68¦86¦86¦~13~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 1112.5415 | 1112.5415
86¦87¦68¦86¦86¦~13~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~13~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 6 | 6
86¦87¦68¦86¦86¦~13~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~13~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~13~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 367571 | 367571
91¦~13~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.9676 | 98.9676
91¦~13~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~13~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~13~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 350067.625 | 350067.625
93¦~13~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 353770.6562 | 353770.6562
93¦~13~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.9533 | 98.9533
93¦~13~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 3703.0332 | 3703.0332
93¦~13~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 3247.6411 | 3247.6411
93¦~13~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 455.3922 | 455.3922
86¦87¦68¦86¦86¦~13~3~30~~-4100~ | ST Assembly [1]: Steam turbine length (including gear box) | m | 24.4379 | 24.4379
86¦87¦68¦86¦86¦~13~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 5.36 | 5.36
86¦87¦68¦86¦86¦~13~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight (including weight of gear box) | kg | 492639.8438 | 492639.8438
86¦87¦68¦86¦86¦~13~3~33~~-4100~ | ST Assembly [1]: Gear box length | m | 0 | 0
86¦87¦68¦86¦86¦~13~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 13.5723 | 13.5723
86¦87¦68¦86¦86¦~13~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 4.07 | 4.07
86¦87¦68¦86¦86¦~13~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 387463.1562 | 387463.1562
86¦87¦68¦86¦86¦~13~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 38.0102 | 38.0102
86¦87¦68¦86¦86¦~13~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 5.36 | 5.36
86¦87¦68¦86¦86¦~13~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 880103 | 880103
86¦87¦68¦86¦86¦~13~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 40.5583 | 40.5583
86¦87¦68¦86¦86¦~13~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 6.432 | 6.432
86¦87¦68¦86¦86¦~13~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 52082436 | 52082436
86¦87¦68¦86¦86¦~13~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 60995604 | 60995604
82¦71¦~13~10~3~~-11~ | ST Assembly [1]: ST Group [13] : Mode |  | Design | Design
82¦71¦~13~10~4~~-11~ | ST Assembly [1]: ST Group [13] : Type of inlet control |  | Sliding | Sliding
93¦~13~3~29~~-11~ | ST Assembly [1]: ST Group [13] : Steam supply pressure | bar | 162.5 | 162.5
93¦~13~3~11~~-11~ | ST Assembly [1]: ST Group [13] : Inlet pressure | bar | 162.5 | 162.5
93¦~13~3~12~~-11~ | ST Assembly [1]: ST Group [13] : Inlet temperature | C | 535.5406 | 535.5406
93¦~13~3~14~~-11~ | ST Assembly [1]: ST Group [13] : Inlet flow | t/h | 1112.5415 | 1112.5415
93¦~13~3~13~~-11~ | ST Assembly [1]: ST Group [13] : Inlet enthalpy | kJ/kg | 3396.7937 | 3396.7937
93¦~13~3~16~~-11~ | ST Assembly [1]: ST Group [13] : Expansion massflow | t/h | 1112.0624 | 1112.0624
93¦~13~3~4~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial pressure | bar | 162.5 | 162.5
93¦~13~3~15~~-11~ | ST Assembly [1]: ST Group [13] : Expansion initial enthalpy | kJ/kg | 3396.7937 | 3396.7937
93¦~13~3~6~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end pressure (before Exhaust Loss) | bar | 59.74 | 59.74
93¦~13~3~25~~-11~ | ST Assembly [1]: ST Group [13] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3139.1685 | 3139.1685
93¦~13~3~21~~-11~ | ST Assembly [1]: ST Group [13] : Outlet pressure | bar | 59.74 | 59.74
93¦~13~3~22~~-11~ | ST Assembly [1]: ST Group [13] : Outlet temperature | C | 384.7573 | 384.7573
93¦~13~3~24~~-11~ | ST Assembly [1]: ST Group [13] : Outlet flow | t/h | 1112.0624 | 1112.0624
93¦~13~3~23~~-11~ | ST Assembly [1]: ST Group [13] : Outlet enthalpy | kJ/kg | 3139.1685 | 3139.1685
72¦79¦93¦~13~7~15~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust volume flow | m^3/s | 14.2484 | 14.2484
72¦79¦93¦~13~7~18~~-11~ | ST Assembly [1]: ST Group [13] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~13~7~17~~-11~ | ST Assembly [1]: ST Group [13] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~13~3~7~~-11~ | ST Assembly [1]: ST Group [13] : Actual flow function | m^2 | 0.016398 | 0.016398
93¦~13~3~10~~-11~ | ST Assembly [1]: ST Group [13] : Actual pressure ratio (blading) |  | 2.7201 | 2.7201
93¦~13~3~3~~-11~ | ST Assembly [1]: ST Group [13] : Dry step efficiency | % | 85.1821 | 85.1821
93¦~13~3~1~~-11~ | ST Assembly [1]: ST Group [13] : Group overall efficiency | % | 86.4346 | 86.4346
93¦~13~3~30~~-11~ | ST Assembly [1]: ST Group [13] : Group blading efficiency | % | 86.4346 | 86.4346
93¦~13~3~50~~-11~ | ST Assembly [1]: ST Group [13] : Expansion power | kW | 79583.2734 | 79583.2734
93¦~13~3~8~~-11~ | ST Assembly [1]: ST Group [13] : Shaft power | kW | 79384.3125 | 79384.3125
93¦~13~3~9~~-11~ | ST Assembly [1]: ST Group [13] : Mechanical loss | kW | 198.958 | 198.958
82¦71¦~15~10~3~~-11~ | ST Assembly [1]: ST Group [15] : Mode |  | Design | Design
82¦71¦~15~10~4~~-11~ | ST Assembly [1]: ST Group [15] : Type of inlet control |  | Sliding | Sliding
93¦~15~3~29~~-11~ | ST Assembly [1]: ST Group [15] : Steam supply pressure | bar | 59.74 | 59.74
93¦~15~3~11~~-11~ | ST Assembly [1]: ST Group [15] : Inlet pressure | bar | 59.74 | 59.74
93¦~15~3~12~~-11~ | ST Assembly [1]: ST Group [15] : Inlet temperature | C | 384.7573 | 384.7573
93¦~15~3~14~~-11~ | ST Assembly [1]: ST Group [15] : Inlet flow | t/h | 1036.5914 | 1036.5914
93¦~15~3~13~~-11~ | ST Assembly [1]: ST Group [15] : Inlet enthalpy | kJ/kg | 3139.1685 | 3139.1685
93¦~15~3~16~~-11~ | ST Assembly [1]: ST Group [15] : Expansion massflow | t/h | 1036.5914 | 1036.5914
93¦~15~3~4~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial pressure | bar | 59.74 | 59.74
93¦~15~3~15~~-11~ | ST Assembly [1]: ST Group [15] : Expansion initial enthalpy | kJ/kg | 3139.1685 | 3139.1685
93¦~15~3~6~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end pressure (before Exhaust Loss) | bar | 35.78 | 35.78
93¦~15~3~25~~-11~ | ST Assembly [1]: ST Group [15] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3047.1467 | 3047.1467
93¦~15~3~21~~-11~ | ST Assembly [1]: ST Group [15] : Outlet pressure | bar | 35.78 | 35.78
93¦~15~3~22~~-11~ | ST Assembly [1]: ST Group [15] : Outlet temperature | C | 327.4125 | 327.4125
93¦~15~3~24~~-11~ | ST Assembly [1]: ST Group [15] : Outlet flow | t/h | 1036.5914 | 1036.5914
93¦~15~3~23~~-11~ | ST Assembly [1]: ST Group [15] : Outlet enthalpy | kJ/kg | 3047.1467 | 3047.1467
72¦79¦93¦~15~7~15~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust volume flow | m^3/s | 20.5558 | 20.5558
72¦79¦93¦~15~7~18~~-11~ | ST Assembly [1]: ST Group [15] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~15~7~17~~-11~ | ST Assembly [1]: ST Group [15] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~15~3~7~~-11~ | ST Assembly [1]: ST Group [15] : Actual flow function | m^2 | 0.037887 | 0.037887
93¦~15~3~10~~-11~ | ST Assembly [1]: ST Group [15] : Actual pressure ratio (blading) |  | 1.6696 | 1.6696
93¦~15~3~3~~-11~ | ST Assembly [1]: ST Group [15] : Dry step efficiency | % | 67.9832 | 67.9832
93¦~15~3~1~~-11~ | ST Assembly [1]: ST Group [15] : Group overall efficiency | % | 68.9315 | 68.9315
93¦~15~3~30~~-11~ | ST Assembly [1]: ST Group [15] : Group blading efficiency | % | 68.9315 | 68.9315
93¦~15~3~50~~-11~ | ST Assembly [1]: ST Group [15] : Expansion power | kW | 26497.3066 | 26497.3066
93¦~15~3~8~~-11~ | ST Assembly [1]: ST Group [15] : Shaft power | kW | 26431.0625 | 26431.0625
93¦~15~3~9~~-11~ | ST Assembly [1]: ST Group [15] : Mechanical loss | kW | 66.2432 | 66.2432
82¦71¦~26~10~3~~-11~ | ST Assembly [1]: ST Group [26] : Mode |  | Design | Design
82¦71¦~26~10~4~~-11~ | ST Assembly [1]: ST Group [26] : Type of inlet control |  | Sliding | Sliding
93¦~26~3~29~~-11~ | ST Assembly [1]: ST Group [26] : Steam supply pressure | bar | 32.6 | 32.6
93¦~26~3~11~~-11~ | ST Assembly [1]: ST Group [26] : Inlet pressure | bar | 32.6 | 32.6
93¦~26~3~12~~-11~ | ST Assembly [1]: ST Group [26] : Inlet temperature | C | 532.2689 | 532.2689
93¦~26~3~14~~-11~ | ST Assembly [1]: ST Group [26] : Inlet flow | t/h | 933.0945 | 933.0945
93¦~26~3~13~~-11~ | ST Assembly [1]: ST Group [26] : Inlet enthalpy | kJ/kg | 3527.0349 | 3527.0349
93¦~26~3~16~~-11~ | ST Assembly [1]: ST Group [26] : Expansion massflow | t/h | 933.0945 | 933.0945
93¦~26~3~4~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial pressure | bar | 32.6 | 32.6
93¦~26~3~15~~-11~ | ST Assembly [1]: ST Group [26] : Expansion initial enthalpy | kJ/kg | 3527.0349 | 3527.0349
93¦~26~3~6~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end pressure (before Exhaust Loss) | bar | 17.44 | 17.44
93¦~26~3~25~~-11~ | ST Assembly [1]: ST Group [26] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3337.1973 | 3337.1973
93¦~26~3~21~~-11~ | ST Assembly [1]: ST Group [26] : Outlet pressure | bar | 17.44 | 17.44
93¦~26~3~22~~-11~ | ST Assembly [1]: ST Group [26] : Outlet temperature | C | 438.8859 | 438.8859
93¦~26~3~24~~-11~ | ST Assembly [1]: ST Group [26] : Outlet flow | t/h | 933.0945 | 933.0945
93¦~26~3~23~~-11~ | ST Assembly [1]: ST Group [26] : Outlet enthalpy | kJ/kg | 3337.1973 | 3337.1973
72¦79¦93¦~26~7~15~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust volume flow | m^3/s | 47.9339 | 47.9339
72¦79¦93¦~26~7~18~~-11~ | ST Assembly [1]: ST Group [26] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~26~7~17~~-11~ | ST Assembly [1]: ST Group [26] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~26~3~7~~-11~ | ST Assembly [1]: ST Group [26] : Actual flow function | m^2 | 0.07181 | 0.07181
93¦~26~3~10~~-11~ | ST Assembly [1]: ST Group [26] : Actual pressure ratio (blading) |  | 1.8693 | 1.8693
93¦~26~3~3~~-11~ | ST Assembly [1]: ST Group [26] : Dry step efficiency | % | 88.6914 | 88.6914
93¦~26~3~1~~-11~ | ST Assembly [1]: ST Group [26] : Group overall efficiency | % | 89.2107 | 89.2107
93¦~26~3~30~~-11~ | ST Assembly [1]: ST Group [26] : Group blading efficiency | % | 89.2107 | 89.2107
93¦~26~3~50~~-11~ | ST Assembly [1]: ST Group [26] : Expansion power | kW | 49205.2773 | 49205.2773
93¦~26~3~8~~-11~ | ST Assembly [1]: ST Group [26] : Shaft power | kW | 49082.2656 | 49082.2656
93¦~26~3~9~~-11~ | ST Assembly [1]: ST Group [26] : Mechanical loss | kW | 123.0131 | 123.0131
82¦71¦~28~10~3~~-11~ | ST Assembly [1]: ST Group [28] : Mode |  | Design | Design
82¦71¦~28~10~4~~-11~ | ST Assembly [1]: ST Group [28] : Type of inlet control |  | Sliding | Sliding
93¦~28~3~29~~-11~ | ST Assembly [1]: ST Group [28] : Steam supply pressure | bar | 17.44 | 17.44
93¦~28~3~11~~-11~ | ST Assembly [1]: ST Group [28] : Inlet pressure | bar | 17.44 | 17.44
93¦~28~3~12~~-11~ | ST Assembly [1]: ST Group [28] : Inlet temperature | C | 438.8859 | 438.8859
93¦~28~3~14~~-11~ | ST Assembly [1]: ST Group [28] : Inlet flow | t/h | 910.3932 | 910.3932
93¦~28~3~13~~-11~ | ST Assembly [1]: ST Group [28] : Inlet enthalpy | kJ/kg | 3337.1973 | 3337.1973
93¦~28~3~16~~-11~ | ST Assembly [1]: ST Group [28] : Expansion massflow | t/h | 910.3932 | 910.3932
93¦~28~3~4~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial pressure | bar | 17.44 | 17.44
93¦~28~3~15~~-11~ | ST Assembly [1]: ST Group [28] : Expansion initial enthalpy | kJ/kg | 3337.1973 | 3337.1973
93¦~28~3~6~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end pressure (before Exhaust Loss) | bar | 9.85 | 9.85
93¦~28~3~25~~-11~ | ST Assembly [1]: ST Group [28] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3180.9927 | 3180.9927
93¦~28~3~21~~-11~ | ST Assembly [1]: ST Group [28] : Outlet pressure | bar | 9.85 | 9.85
93¦~28~3~22~~-11~ | ST Assembly [1]: ST Group [28] : Outlet temperature | C | 360.6185 | 360.6185
93¦~28~3~24~~-11~ | ST Assembly [1]: ST Group [28] : Outlet flow | t/h | 910.3932 | 910.3932
93¦~28~3~23~~-11~ | ST Assembly [1]: ST Group [28] : Outlet enthalpy | kJ/kg | 3180.9927 | 3180.9927
72¦79¦93¦~28~7~15~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust volume flow | m^3/s | 73.864 | 73.864
72¦79¦93¦~28~7~18~~-11~ | ST Assembly [1]: ST Group [28] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~28~7~17~~-11~ | ST Assembly [1]: ST Group [28] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~28~3~7~~-11~ | ST Assembly [1]: ST Group [28] : Actual flow function | m^2 | 0.12332 | 0.12332
93¦~28~3~10~~-11~ | ST Assembly [1]: ST Group [28] : Actual pressure ratio (blading) |  | 1.7706 | 1.7706
93¦~28~3~3~~-11~ | ST Assembly [1]: ST Group [28] : Dry step efficiency | % | 89.8737 | 89.8737
93¦~28~3~1~~-11~ | ST Assembly [1]: ST Group [28] : Group overall efficiency | % | 90.27 | 90.27
93¦~28~3~30~~-11~ | ST Assembly [1]: ST Group [28] : Group blading efficiency | % | 90.27 | 90.27
93¦~28~3~50~~-11~ | ST Assembly [1]: ST Group [28] : Expansion power | kW | 39502.7148 | 39502.7148
93¦~28~3~8~~-11~ | ST Assembly [1]: ST Group [28] : Shaft power | kW | 39403.9531 | 39403.9531
93¦~28~3~9~~-11~ | ST Assembly [1]: ST Group [28] : Mechanical loss | kW | 98.7567 | 98.7567
82¦71¦~44~10~3~~-11~ | ST Assembly [1]: ST Group [44] : Mode |  | Design | Design
82¦71¦~44~10~4~~-11~ | ST Assembly [1]: ST Group [44] : Type of inlet control |  | Sliding | Sliding
93¦~44~3~29~~-11~ | ST Assembly [1]: ST Group [44] : Steam supply pressure | bar | 9.85 | 9.85
93¦~44~3~11~~-11~ | ST Assembly [1]: ST Group [44] : Inlet pressure | bar | 9.85 | 9.85
93¦~44~3~12~~-11~ | ST Assembly [1]: ST Group [44] : Inlet temperature | C | 360.6185 | 360.6185
93¦~44~3~14~~-11~ | ST Assembly [1]: ST Group [44] : Inlet flow | t/h | 815.9312 | 815.9312
93¦~44~3~13~~-11~ | ST Assembly [1]: ST Group [44] : Inlet enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~44~3~16~~-11~ | ST Assembly [1]: ST Group [44] : Expansion massflow | t/h | 815.9312 | 815.9312
93¦~44~3~4~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial pressure | bar | 9.85 | 9.85
93¦~44~3~15~~-11~ | ST Assembly [1]: ST Group [44] : Expansion initial enthalpy | kJ/kg | 3180.9927 | 3180.9927
93¦~44~3~6~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end pressure (before Exhaust Loss) | bar | 3.88 | 3.88
93¦~44~3~25~~-11~ | ST Assembly [1]: ST Group [44] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2960.0698 | 2960.0698
93¦~44~3~21~~-11~ | ST Assembly [1]: ST Group [44] : Outlet pressure | bar | 3.88 | 3.88
93¦~44~3~22~~-11~ | ST Assembly [1]: ST Group [44] : Outlet temperature | C | 247.614 | 247.614
93¦~44~3~24~~-11~ | ST Assembly [1]: ST Group [44] : Outlet flow | t/h | 815.9312 | 815.9312
93¦~44~3~23~~-11~ | ST Assembly [1]: ST Group [44] : Outlet enthalpy | kJ/kg | 2960.0698 | 2960.0698
72¦79¦93¦~44~7~15~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust volume flow | m^3/s | 138.4578 | 138.4578
72¦79¦93¦~44~7~18~~-11~ | ST Assembly [1]: ST Group [44] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~44~7~17~~-11~ | ST Assembly [1]: ST Group [44] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~44~3~7~~-11~ | ST Assembly [1]: ST Group [44] : Actual flow function | m^2 | 0.18482 | 0.18482
93¦~44~3~10~~-11~ | ST Assembly [1]: ST Group [44] : Actual pressure ratio (blading) |  | 2.5387 | 2.5387
93¦~44~3~3~~-11~ | ST Assembly [1]: ST Group [44] : Dry step efficiency | % | 90.9151 | 90.9151
93¦~44~3~1~~-11~ | ST Assembly [1]: ST Group [44] : Group overall efficiency | % | 91.5081 | 91.5081
93¦~44~3~30~~-11~ | ST Assembly [1]: ST Group [44] : Group blading efficiency | % | 91.5081 | 91.5081
93¦~44~3~50~~-11~ | ST Assembly [1]: ST Group [44] : Expansion power | kW | 50072.4297 | 50072.4297
93¦~44~3~8~~-11~ | ST Assembly [1]: ST Group [44] : Shaft power | kW | 49947.25 | 49947.25
93¦~44~3~9~~-11~ | ST Assembly [1]: ST Group [44] : Mechanical loss | kW | 125.181 | 125.181
82¦71¦~45~10~3~~-11~ | ST Assembly [1]: ST Group [45] : Mode |  | Design | Design
82¦71¦~45~10~4~~-11~ | ST Assembly [1]: ST Group [45] : Type of inlet control |  | Sliding | Sliding
93¦~45~3~29~~-11~ | ST Assembly [1]: ST Group [45] : Steam supply pressure | bar | 3.88 | 3.88
93¦~45~3~11~~-11~ | ST Assembly [1]: ST Group [45] : Inlet pressure | bar | 3.88 | 3.88
93¦~45~3~12~~-11~ | ST Assembly [1]: ST Group [45] : Inlet temperature | C | 247.614 | 247.614
93¦~45~3~14~~-11~ | ST Assembly [1]: ST Group [45] : Inlet flow | t/h | 769.6258 | 769.6258
93¦~45~3~13~~-11~ | ST Assembly [1]: ST Group [45] : Inlet enthalpy | kJ/kg | 2960.0698 | 2960.0698
93¦~45~3~16~~-11~ | ST Assembly [1]: ST Group [45] : Expansion massflow | t/h | 769.6258 | 769.6258
93¦~45~3~4~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial pressure | bar | 3.88 | 3.88
93¦~45~3~15~~-11~ | ST Assembly [1]: ST Group [45] : Expansion initial enthalpy | kJ/kg | 2960.0698 | 2960.0698
93¦~45~3~6~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end pressure (before Exhaust Loss) | bar | 1.47 | 1.47
93¦~45~3~25~~-11~ | ST Assembly [1]: ST Group [45] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2769.8633 | 2769.8633
93¦~45~3~21~~-11~ | ST Assembly [1]: ST Group [45] : Outlet pressure | bar | 1.47 | 1.47
93¦~45~3~22~~-11~ | ST Assembly [1]: ST Group [45] : Outlet temperature | C | 148.393 | 148.393
93¦~45~3~24~~-11~ | ST Assembly [1]: ST Group [45] : Outlet flow | t/h | 769.6258 | 769.6258
93¦~45~3~23~~-11~ | ST Assembly [1]: ST Group [45] : Outlet enthalpy | kJ/kg | 2769.8633 | 2769.8633
72¦79¦93¦~45~7~15~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust volume flow | m^3/s | 279.3802 | 279.3802
72¦79¦93¦~45~7~18~~-11~ | ST Assembly [1]: ST Group [45] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~45~7~17~~-11~ | ST Assembly [1]: ST Group [45] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~45~3~7~~-11~ | ST Assembly [1]: ST Group [45] : Actual flow function | m^2 | 0.4017 | 0.4017
93¦~45~3~10~~-11~ | ST Assembly [1]: ST Group [45] : Actual pressure ratio (blading) |  | 2.6395 | 2.6395
93¦~45~3~3~~-11~ | ST Assembly [1]: ST Group [45] : Dry step efficiency | % | 92.0601 | 92.0601
93¦~45~3~1~~-11~ | ST Assembly [1]: ST Group [45] : Group overall efficiency | % | 92.4759 | 92.4759
93¦~45~3~30~~-11~ | ST Assembly [1]: ST Group [45] : Group blading efficiency | % | 92.4759 | 92.4759
93¦~45~3~50~~-11~ | ST Assembly [1]: ST Group [45] : Expansion power | kW | 40663.9219 | 40663.9219
93¦~45~3~8~~-11~ | ST Assembly [1]: ST Group [45] : Shaft power | kW | 40562.2617 | 40562.2617
93¦~45~3~9~~-11~ | ST Assembly [1]: ST Group [45] : Mechanical loss | kW | 101.6597 | 101.6597
82¦71¦~46~10~3~~-11~ | ST Assembly [1]: ST Group [46] : Mode |  | Design | Design
82¦71¦~46~10~4~~-11~ | ST Assembly [1]: ST Group [46] : Type of inlet control |  | Sliding | Sliding
93¦~46~3~29~~-11~ | ST Assembly [1]: ST Group [46] : Steam supply pressure | bar | 1.47 | 1.47
93¦~46~3~11~~-11~ | ST Assembly [1]: ST Group [46] : Inlet pressure | bar | 1.47 | 1.47
93¦~46~3~12~~-11~ | ST Assembly [1]: ST Group [46] : Inlet temperature | C | 148.393 | 148.393
93¦~46~3~14~~-11~ | ST Assembly [1]: ST Group [46] : Inlet flow | t/h | 741.1432 | 741.1432
93¦~46~3~13~~-11~ | ST Assembly [1]: ST Group [46] : Inlet enthalpy | kJ/kg | 2769.8633 | 2769.8633
93¦~46~3~16~~-11~ | ST Assembly [1]: ST Group [46] : Expansion massflow | t/h | 741.1432 | 741.1432
93¦~46~3~4~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial pressure | bar | 1.47 | 1.47
93¦~46~3~15~~-11~ | ST Assembly [1]: ST Group [46] : Expansion initial enthalpy | kJ/kg | 2769.8633 | 2769.8633
93¦~46~3~6~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end pressure (before Exhaust Loss) | bar | 0.78 | 0.78
93¦~46~3~25~~-11~ | ST Assembly [1]: ST Group [46] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2665.5569 | 2665.5569
93¦~46~3~21~~-11~ | ST Assembly [1]: ST Group [46] : Outlet pressure | bar | 0.78 | 0.78
93¦~46~3~22~~-11~ | ST Assembly [1]: ST Group [46] : Outlet temperature | C | 93.5291 | 93.5291
93¦~46~3~24~~-11~ | ST Assembly [1]: ST Group [46] : Outlet flow | t/h | 741.1432 | 741.1432
93¦~46~3~23~~-11~ | ST Assembly [1]: ST Group [46] : Outlet enthalpy | kJ/kg | 2665.5569 | 2665.5569
72¦79¦93¦~46~7~15~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust volume flow | m^3/s | 440.9083 | 440.9083
72¦79¦93¦~46~7~18~~-11~ | ST Assembly [1]: ST Group [46] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~46~7~17~~-11~ | ST Assembly [1]: ST Group [46] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~46~3~7~~-11~ | ST Assembly [1]: ST Group [46] : Actual flow function | m^2 | 0.91919 | 0.91919
93¦~46~3~10~~-11~ | ST Assembly [1]: ST Group [46] : Actual pressure ratio (blading) |  | 1.8846 | 1.8846
93¦~46~3~3~~-11~ | ST Assembly [1]: ST Group [46] : Dry step efficiency | % | 92.3209 | 92.3209
93¦~46~3~1~~-11~ | ST Assembly [1]: ST Group [46] : Group overall efficiency | % | 92.321 | 92.321
93¦~46~3~30~~-11~ | ST Assembly [1]: ST Group [46] : Group blading efficiency | % | 92.321 | 92.321
93¦~46~3~50~~-11~ | ST Assembly [1]: ST Group [46] : Expansion power | kW | 21474.2246 | 21474.2246
93¦~46~3~8~~-11~ | ST Assembly [1]: ST Group [46] : Shaft power | kW | 21420.5391 | 21420.5391
93¦~46~3~9~~-11~ | ST Assembly [1]: ST Group [46] : Mechanical loss | kW | 53.6855 | 53.6855
82¦71¦~47~10~3~~-11~ | ST Assembly [1]: ST Group [47] : Mode |  | Design | Design
82¦71¦~47~10~4~~-11~ | ST Assembly [1]: ST Group [47] : Type of inlet control |  | Sliding | Sliding
93¦~47~3~29~~-11~ | ST Assembly [1]: ST Group [47] : Steam supply pressure | bar | 0.78 | 0.78
93¦~47~3~11~~-11~ | ST Assembly [1]: ST Group [47] : Inlet pressure | bar | 0.78 | 0.78
93¦~47~3~12~~-11~ | ST Assembly [1]: ST Group [47] : Inlet temperature | C | 93.5291 | 93.5291
93¦~47~3~14~~-11~ | ST Assembly [1]: ST Group [47] : Inlet flow | t/h | 709.7795 | 709.7795
93¦~47~3~13~~-11~ | ST Assembly [1]: ST Group [47] : Inlet enthalpy | kJ/kg | 2665.5569 | 2665.5569
93¦~47~3~16~~-11~ | ST Assembly [1]: ST Group [47] : Expansion massflow | t/h | 709.7795 | 709.7795
93¦~47~3~4~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial pressure | bar | 0.78 | 0.78
93¦~47~3~15~~-11~ | ST Assembly [1]: ST Group [47] : Expansion initial enthalpy | kJ/kg | 2665.5569 | 2665.5569
93¦~47~3~6~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end pressure (before Exhaust Loss) | bar | 0.283 | 0.283
93¦~47~3~25~~-11~ | ST Assembly [1]: ST Group [47] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2519.4097 | 2519.4097
93¦~47~3~21~~-11~ | ST Assembly [1]: ST Group [47] : Outlet pressure | bar | 0.283 | 0.283
93¦~47~3~22~~-11~ | ST Assembly [1]: ST Group [47] : Outlet temperature | C | 67.7608 | 67.7608
93¦~47~3~24~~-11~ | ST Assembly [1]: ST Group [47] : Outlet flow | t/h | 709.7795 | 709.7795
93¦~47~3~23~~-11~ | ST Assembly [1]: ST Group [47] : Outlet enthalpy | kJ/kg | 2519.4097 | 2519.4097
72¦79¦93¦~47~7~15~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust volume flow | m^3/s | 1040.8906 | 1040.8906
72¦79¦93¦~47~7~18~~-11~ | ST Assembly [1]: ST Group [47] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~47~7~17~~-11~ | ST Assembly [1]: ST Group [47] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~47~3~7~~-11~ | ST Assembly [1]: ST Group [47] : Actual flow function | m^2 | 1.547 | 1.547
93¦~47~3~10~~-11~ | ST Assembly [1]: ST Group [47] : Actual pressure ratio (blading) |  | 2.7562 | 2.7562
93¦~47~3~3~~-11~ | ST Assembly [1]: ST Group [47] : Dry step efficiency | % | 92.25 | 92.25
93¦~47~3~1~~-11~ | ST Assembly [1]: ST Group [47] : Group overall efficiency | % | 91.5996 | 91.5996
93¦~47~3~30~~-11~ | ST Assembly [1]: ST Group [47] : Group blading efficiency | % | 91.5996 | 91.5996
93¦~47~3~50~~-11~ | ST Assembly [1]: ST Group [47] : Expansion power | kW | 28814.9453 | 28814.9453
93¦~47~3~8~~-11~ | ST Assembly [1]: ST Group [47] : Shaft power | kW | 28742.9082 | 28742.9082
93¦~47~3~9~~-11~ | ST Assembly [1]: ST Group [47] : Mechanical loss | kW | 72.0373 | 72.0373
82¦71¦~5~10~3~~-11~ | ST Assembly [1]: ST Group [5] : Mode |  | Design | Design
82¦71¦~5~10~4~~-11~ | ST Assembly [1]: ST Group [5] : Type of inlet control |  | Sliding | Sliding
93¦~5~3~29~~-11~ | ST Assembly [1]: ST Group [5] : Steam supply pressure | bar | 0.283 | 0.283
93¦~5~3~11~~-11~ | ST Assembly [1]: ST Group [5] : Inlet pressure | bar | 0.283 | 0.283
93¦~5~3~12~~-11~ | ST Assembly [1]: ST Group [5] : Inlet temperature | C | 67.7608 | 67.7608
93¦~5~3~14~~-11~ | ST Assembly [1]: ST Group [5] : Inlet flow | t/h | 688.0715 | 688.0715
93¦~5~3~13~~-11~ | ST Assembly [1]: ST Group [5] : Inlet enthalpy | kJ/kg | 2519.4097 | 2519.4097
93¦~5~3~16~~-11~ | ST Assembly [1]: ST Group [5] : Expansion massflow | t/h | 688.0715 | 688.0715
93¦~5~3~4~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial pressure | bar | 0.283 | 0.283
93¦~5~3~15~~-11~ | ST Assembly [1]: ST Group [5] : Expansion initial enthalpy | kJ/kg | 2519.4097 | 2519.4097
93¦~5~3~6~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end pressure (before Exhaust Loss) | bar | 0.0975 | 0.0975
93¦~5~3~25~~-11~ | ST Assembly [1]: ST Group [5] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2387.3787 | 2387.3787
93¦~5~3~21~~-11~ | ST Assembly [1]: ST Group [5] : Outlet pressure | bar | 0.0975 | 0.0975
93¦~5~3~22~~-11~ | ST Assembly [1]: ST Group [5] : Outlet temperature | C | 45.3132 | 45.3132
93¦~5~3~24~~-11~ | ST Assembly [1]: ST Group [5] : Outlet flow | t/h | 688.3437 | 688.3437
93¦~5~3~23~~-11~ | ST Assembly [1]: ST Group [5] : Outlet enthalpy | kJ/kg | 2420.9624 | 2420.9624
72¦79¦76¦~5~6~2~~-11~ | ST Assembly [1]: ST Group [5] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~5~7~15~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust volume flow per end | m^3/s | 2636.7698 | 2636.7698
72¦79¦91¦~5~5~3~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus area | m^2 | 10.6957 | 10.6957
72¦79¦93¦~5~7~16~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust annulus velocity | m/s | 246.5267 | 246.5267
72¦79¦91¦~5~5~1~~-11~ | ST Assembly [1]: ST Group [5] : Last stage pitch diameter | mm | 2981.0054 | 2981.0054
72¦79¦91¦~5~5~2~~-11~ | ST Assembly [1]: ST Group [5] : Last stage blade length | mm | 1142.0778 | 1142.0778
72¦79¦93¦~5~7~18~~-11~ | ST Assembly [1]: ST Group [5] : Exhaust loss | kJ/kg | 33.4446 | 33.4446
72¦79¦93¦~5~7~17~~-11~ | ST Assembly [1]: ST Group [5] : Dry exhaust loss | kJ/kg | 33.4446 | 33.4446
93¦~5~3~7~~-11~ | ST Assembly [1]: ST Group [5] : Actual flow function | m^2 | 3.8222 | 3.8222
93¦~5~3~10~~-11~ | ST Assembly [1]: ST Group [5] : Actual pressure ratio (blading) |  | 2.9026 | 2.9026
93¦~5~3~3~~-11~ | ST Assembly [1]: ST Group [5] : Dry step efficiency | % | 92.15 | 92.15
93¦~5~3~1~~-11~ | ST Assembly [1]: ST Group [5] : Group overall efficiency | % | 65.5473 | 65.5473
93¦~5~3~30~~-11~ | ST Assembly [1]: ST Group [5] : Group blading efficiency | % | 87.7837 | 87.7837
93¦~5~3~50~~-11~ | ST Assembly [1]: ST Group [5] : Expansion power | kW | 18843.1992 | 18843.1992
93¦~5~3~8~~-11~ | ST Assembly [1]: ST Group [5] : Shaft power | kW | 18796.0918 | 18796.0918
93¦~5~3~9~~-11~ | ST Assembly [1]: ST Group [5] : Mechanical loss | kW | 47.108 | 47.108
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (source) | bar | 162.5 | 162.5
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Pressure (sink) | bar | 32.6 | 32.6
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (source) | C | 535.5406 | 535.5406
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Temperature (sink) | C | 474.6068 | 474.6068
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to IPT inlet: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (source) | bar | 125 | 125
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Pressure (sink) | bar | 32.6 | 32.6
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (source) | C | 519.7215 | 519.7215
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Temperature (sink) | C | 474.6068 | 474.6068
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to IPT inlet: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~1~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~1~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~3~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (source) | bar | 35.78 | 35.78
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~5~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Pressure (sink) | bar | 9.85 | 9.85
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~1~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (source) | C | 327.4126 | 327.4126
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~10~2~7~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Temperature (sink) | C | 297.6837 | 297.6837
86¦87¦68¦86¦86¦98¦86¦79¦78¦~13~3~7~2~-4100~ | ST Assembly [1]: HPT LP leak 1 to LPT crossover: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 91.4529 | 91.4529
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.9074 | 83.9074
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 886.8862 | 886.8862
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 966.6408 | 966.6408
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 184.6997 | 184.6997
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 811082.875 | 811082.875
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 164.125 | 164.125
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 536.8 | 536.8
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 1112.5415 | 1112.5415
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3398.4937 | 3398.4937
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 172.497 | 172.497
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 271.7824 | 271.7824
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 1108.6648 | 1108.6648
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 1191.1445 | 1191.1445
93¦~7~3~165~~-4200~ | Boiler Assembly [1]: Hot reheat pressure | bar | 32.926 | 32.926
93¦~7~3~166~~-4200~ | Boiler Assembly [1]: Hot reheat temperature | C | 533.1637 | 533.1637
93¦~7~3~167~~-4200~ | Boiler Assembly [1]: Hot reheat massflow | t/h | 942.8237 | 942.8237
93¦~7~3~168~~-4200~ | Boiler Assembly [1]: Hot reheat enthalpy | kJ/kg | 3528.7349 | 3528.7349
93¦~7~3~161~~-4200~ | Boiler Assembly [1]: Cold reheat pressure | bar | 35.78 | 35.78
93¦~7~3~162~~-4200~ | Boiler Assembly [1]: Cold reheat temperature | C | 327.4125 | 327.4125
93¦~7~3~163~~-4200~ | Boiler Assembly [1]: Cold reheat massflow | t/h | 940.2924 | 940.2924
93¦~7~3~164~~-4200~ | Boiler Assembly [1]: Cold reheat enthalpy | kJ/kg | 3047.1467 | 3047.1467
~1~1~0~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Pressure | bar | 1.0332 | 1.0332
~1~1~1~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Temperature | C | 25.85 | 25.85
~1~1~2~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mass flow | t/h | 1277.0692 | 1277.0692
~1~1~22~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash flow | t/h | 0 | 0
~1~1~16~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~1~18~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Relative humidity | % | 59.24 | 59.24
~1~1~20~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Entropy | kJ/kg-C | 0.18546 | 0.18546
~1~1~3~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Enthalpy | kJ/kg | 0.86557 | 0.86557
~1~1~19~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Molecular weight | M.W. | 28.7578 | 28.7578
~1~1~4~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO2 mass flow | t/h | 0.58093 | 0.58093
~1~1~5~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Volume flow | m^3/s | 296.824 | 296.824
~1~1~101~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Density | kg/m^3 | 1.1951 | 1.1951
~1~1~6~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of N2 | % | 76.5891 | 76.5891
~1~1~7~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of O2 | % | 20.5495 | 20.5495
~1~1~8~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~1~9~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O | % | 1.9093 | 1.9093
~1~1~10~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~1~11~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of Ar | % | 0.92239 | 0.92239
~1~1~12~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Mole percent of SO2 | % | 0 | 0
~1~1~14~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~1~23~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: HCl mass flow | kg/hr | 0 | 0
~1~1~24~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: NOx mass flow | kg/hr | 0 | 0
~1~1~25~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: CO mass flow | kg/hr | 0 | 0
~1~1~26~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: UHC mass flow | kg/hr | 0 | 0
~1~1~29~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Hg mass flow | kg/hr | 0 | 0
~1~1~32~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~1~31~~-5001~ | 1 - Outlet of Gas/Air Source [3] - Sec.Air -> Inlet of Boiler Assembly [1]: Fan [66] - SA Fan: Normal volume flow | Nm^3/hr | 995396.75 | 995396.75
~1~2~0~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1254 | 1.1254
~1~2~1~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 320.6714 | 320.6714
~1~2~2~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 269.4123 | 269.4123
~1~2~22~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~2~16~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~2~18~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~2~20~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.86695 | 0.86695
~1~2~3~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 305.6506 | 305.6506
~1~2~19~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~2~4~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.12266 | 0.12266
~1~2~5~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 114.1108 | 114.1108
~1~2~101~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.65583 | 0.65583
~1~2~6~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~2~7~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~2~8~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~2~9~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~2~10~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~2~12~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~2~14~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~2~23~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~2~31~~-5001~ | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 209880.9062 | 209880.9062
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Pressure | bar | 1.1379 | 1.1379
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Temperature | C | 28.2082 | 28.2082
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mass flow | t/h | 372.8713 | 372.8713
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Relative humidity | % | 52.7378 | 52.7378
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Entropy | kJ/kg-C | 0.16412 | 0.16412
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Enthalpy | kJ/kg | 3.2646 | 3.2646
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Molecular weight | M.W. | 28.7728 | 28.7728
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO2 mass flow | t/h | 0.16976 | 0.16976
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Volume flow | m^3/s | 79.2707 | 79.2707
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Density | kg/m^3 | 1.3066 | 1.3066
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of N2 | % | 76.6959 | 76.6959
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of O2 | % | 20.5782 | 20.5782
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O | % | 1.7725 | 1.7725
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of Ar | % | 0.92367 | 0.92367
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct: Normal volume flow | Nm^3/hr | 290478.8125 | 290478.8125
~1~13~0~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 1.0118 | 1.0118
~1~13~1~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 1151 | 1151
~1~13~2~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 1667.917 | 1667.917
~1~13~22~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash flow | t/h | 8.1714 | 8.1714
~1~13~16~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Fly ash enthalpy | kJ/kg | 1270.1007 | 1270.1007
~1~13~18~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Relative humidity | % | 0 | 0
~1~13~20~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 2.1108 | 2.1108
~1~13~3~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 1367.6945 | 1367.6945
~1~13~19~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~13~4~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~13~5~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Volume flow | m^3/s | 1866.9561 | 1866.9561
~1~13~101~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 0.24816 | 0.24816
~1~13~6~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~13~7~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~13~8~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~13~9~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~13~10~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~13~12~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~13~14~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~13~23~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~13~31~~-5001~ | 13 - Flue gas outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99933 | 0.99933
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 740.1719 | 740.1719
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 1667.917 | 1667.917
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 8.1714 | 8.1714
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 781.5541 | 781.5541
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6697 | 1.6697
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 830.0085 | 830.0085
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 1344.9578 | 1344.9578
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34448 | 0.34448
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.99683 | 0.99683
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 489.3695 | 489.3695
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 1667.917 | 1667.917
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 8.1714 | 8.1714
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 470.5514 | 470.5514
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.321 | 1.321
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 521.4022 | 521.4022
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 29.0436 | 29.0436
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 1014.6044 | 1014.6044
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.45664 | 0.45664
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 69.3633 | 69.3633
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 3.7173 | 3.7173
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 13.0614 | 13.0614
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.83426 | 0.83426
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 4.2757 | 4.2757
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~16~0~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 0.99434 | 0.99434
~1~16~1~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 352.373 | 352.373
~1~16~2~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 1667.917 | 1667.917
~1~16~22~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 8.1714 | 8.1714
~1~16~16~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 310.8075 | 310.8075
~1~16~18~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 0 | 0
~1~16~20~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 1.0897 | 1.0897
~1~16~3~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 360.819 | 360.819
~1~16~19~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 29.0436 | 29.0436
~1~16~4~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~16~5~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 834.4041 | 834.4041
~1~16~101~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 0.55526 | 0.55526
~1~16~6~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 69.3633 | 69.3633
~1~16~7~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 3.7173 | 3.7173
~1~16~8~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~16~9~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 13.0614 | 13.0614
~1~16~10~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.83426 | 0.83426
~1~16~12~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~16~14~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~16~23~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 4.2757 | 4.2757
~1~16~31~~-5001~ | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~83~0~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 1.0093 | 1.0093
~1~83~1~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 1029.4705 | 1029.4705
~1~83~2~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 1667.917 | 1667.917
~1~83~22~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash flow | t/h | 8.1714 | 8.1714
~1~83~16~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Fly ash enthalpy | kJ/kg | 1129.3052 | 1129.3052
~1~83~18~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Relative humidity | % | 0 | 0
~1~83~20~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 1.9923 | 1.9923
~1~83~3~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 1205.1968 | 1205.1968
~1~83~19~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~83~4~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~83~5~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Volume flow | m^3/s | 1711.8569 | 1711.8569
~1~83~101~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 0.27065 | 0.27065
~1~83~6~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~83~7~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~83~8~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~83~9~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~83~10~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of H2O liquid | % | 0 | 0
~1~83~11~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~83~12~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~83~14~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~83~23~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: HCl mass flow | kg/hr | 0 | 0
~1~83~24~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: NOx mass flow | kg/hr | 0 | 0
~1~83~25~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: CO mass flow | kg/hr | 0 | 0
~1~83~26~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: UHC mass flow | kg/hr | 0 | 0
~1~83~29~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Hg mass flow | kg/hr | 0 | 0
~1~83~32~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dry Oxygen | % | 4.2757 | 4.2757
~1~83~31~~-5001~ | 83 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~89~0~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.1329 | 1.1329
~1~89~1~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 27.2082 | 27.2082
~1~89~2~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 63.0472 | 63.0472
~1~89~22~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 55.664 | 55.664
~1~89~20~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~89~3~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~89~19~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~89~4~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.028705 | 0.028705
~1~89~5~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 13.4178 | 13.4178
~1~89~101~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 1.3052 | 1.3052
~1~89~6~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~89~7~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~89~8~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~89~9~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~89~10~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~89~12~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet 3 of Splitter [9] -> Tempering air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 49115.7852 | 49115.7852
~1~90~0~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.1329 | 1.1329
~1~90~1~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 27.2082 | 27.2082
~1~90~2~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 309.8241 | 309.8241
~1~90~22~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~90~16~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~90~18~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 55.664 | 55.664
~1~90~20~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.162 | 0.162
~1~90~3~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 2.247 | 2.247
~1~90~19~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7728 | 28.7728
~1~90~4~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.14106 | 0.14106
~1~90~5~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 65.9375 | 65.9375
~1~90~101~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.3052 | 1.3052
~1~90~6~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.6959 | 76.6959
~1~90~7~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5782 | 20.5782
~1~90~8~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~90~9~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.7725 | 1.7725
~1~90~10~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~90~11~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92367 | 0.92367
~1~90~12~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~90~14~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~90~23~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~90~24~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~90~25~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~90~26~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~90~29~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~90~32~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~90~31~~-5001~ | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 241363.0469 | 241363.0469
~1~91~0~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.98686 | 0.98686
~1~91~1~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 140.7547 | 140.7547
~1~91~2~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 1824.4261 | 1824.4261
~1~91~22~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 8.1714 | 8.1714
~1~91~16~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 95.1798 | 95.1798
~1~91~18~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 3.2328 | 3.2328
~1~91~20~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.63122 | 0.63122
~1~91~3~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 123.7419 | 123.7419
~1~91~19~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 29.0192 | 29.0192
~1~91~4~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 328.7514 | 328.7514
~1~91~5~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 609.0163 | 609.0163
~1~91~101~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.83214 | 0.83214
~1~91~6~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 69.9911 | 69.9911
~1~91~7~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 5.1748 | 5.1748
~1~91~8~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 11.8816 | 11.8816
~1~91~9~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 12.0931 | 12.0931
~1~91~10~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~91~11~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.84192 | 0.84192
~1~91~12~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.017411 | 0.017411
~1~91~14~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.87057 | 0.87057
~1~91~23~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~91~24~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~91~25~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~91~26~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~91~29~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~91~32~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 5.8867 | 5.8867
~1~91~31~~-5001~ | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 1409217.125 | 1409217.125
~1~92~0~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0243 | 1.0243
~1~92~1~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 273.8889 | 273.8889
~1~92~2~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 1160.972 | 1160.972
~1~92~22~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash flow | t/h | 0 | 0
~1~92~16~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~92~18~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Relative humidity | % | 0 | 0
~1~92~20~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 0.80947 | 0.80947
~1~92~3~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 256.4639 | 256.4639
~1~92~19~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 28.7578 | 28.7578
~1~92~4~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO2 mass flow | t/h | 0.52812 | 0.52812
~1~92~5~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Volume flow | m^3/s | 497.9917 | 497.9917
~1~92~101~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 0.64759 | 0.64759
~1~92~6~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of N2 | % | 76.5891 | 76.5891
~1~92~7~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of O2 | % | 20.5495 | 20.5495
~1~92~8~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~92~9~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O | % | 1.9093 | 1.9093
~1~92~10~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of H2O liquid | % | 0 | 0
~1~92~11~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of Ar | % | 0.92239 | 0.92239
~1~92~12~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mole percent of SO2 | % | 0 | 0
~1~92~14~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~92~23~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HCl mass flow | kg/hr | 0 | 0
~1~92~24~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: NOx mass flow | kg/hr | 0 | 0
~1~92~25~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: CO mass flow | kg/hr | 0 | 0
~1~92~26~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: UHC mass flow | kg/hr | 0 | 0
~1~92~29~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Hg mass flow | kg/hr | 0 | 0
~1~92~32~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~92~31~~-5001~ | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Normal volume flow | Nm^3/hr | 904906.0625 | 904906.0625
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Pressure | bar | 0.97876 | 0.97876
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Temperature | C | 140.7547 | 140.7547
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mass flow | t/h | 1824.4261 | 1824.4261
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash flow | t/h | 0.031206 | 0.031206
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Fly ash enthalpy | kJ/kg | 95.1798 | 95.1798
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Relative humidity | % | 3.2063 | 3.2063
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Entropy | kJ/kg-C | 0.63358 | 0.63358
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Enthalpy | kJ/kg | 123.7419 | 123.7419
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Molecular weight | M.W. | 29.0192 | 29.0192
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO2 mass flow | t/h | 328.7514 | 328.7514
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Volume flow | m^3/s | 614.057 | 614.057
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Density | kg/m^3 | 0.82531 | 0.82531
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of N2 | % | 69.9911 | 69.9911
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of O2 | % | 5.1748 | 5.1748
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of CO2 | % | 11.8816 | 11.8816
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O | % | 12.0931 | 12.0931
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of Ar | % | 0.84192 | 0.84192
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Mole percent of SO2 | % | 0.017411 | 0.017411
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Dry Oxygen | % | 5.8867 | 5.8867
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct: Normal volume flow | Nm^3/hr | 1409217.125 | 1409217.125
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.97378 | 0.97378
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 139.6436 | 139.6436
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 1824.4261 | 1824.4261
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.031206 | 0.031206
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 94.1792 | 94.1792
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 3.2918 | 3.2918
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.63214 | 0.63214
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 122.5397 | 122.5397
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 29.0192 | 29.0192
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 328.7514 | 328.7514
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 615.5439 | 615.5439
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.82331 | 0.82331
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 69.9911 | 69.9911
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 5.1748 | 5.1748
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 11.8816 | 11.8816
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 12.0931 | 12.0931
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.84192 | 0.84192
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.017411 | 0.017411
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 5.8867 | 5.8867
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Outlet Flue Gas Duct -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 1409217.125 | 1409217.125
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 144.9853 | 144.9853
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 1824.4261 | 1824.4261
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.031206 | 0.031206
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 99.0038 | 99.0038
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 2.9477 | 2.9477
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.63491 | 0.63491
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 128.322 | 128.322
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 29.0192 | 29.0192
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 328.7514 | 328.7514
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 599.7147 | 599.7147
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.84504 | 0.84504
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 69.9911 | 69.9911
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 5.1748 | 5.1748
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 11.8816 | 11.8816
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 12.0931 | 12.0931
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.84192 | 0.84192
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.017411 | 0.017411
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 5.8867 | 5.8867
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 1409217.125 | 1409217.125
~1~96~0~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Pressure | bar | 1.0317 | 1.0317
~1~96~1~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | C | 26.2127 | 26.2127
~1~96~2~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mass flow | t/h | 1277.0692 | 1277.0692
~1~96~22~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash flow | t/h | 0 | 0
~1~96~16~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Fly ash enthalpy | kJ/kg | 0 | 0
~1~96~18~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Relative humidity | % | 57.9016 | 57.9016
~1~96~20~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Entropy | kJ/kg-C | 0.1871 | 0.1871
~1~96~3~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~96~19~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Molecular weight | M.W. | 28.7578 | 28.7578
~1~96~4~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO2 mass flow | t/h | 0.58093 | 0.58093
~1~96~5~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Volume flow | m^3/s | 297.6015 | 297.6015
~1~96~101~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Density | kg/m^3 | 1.192 | 1.192
~1~96~6~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of N2 | % | 76.5891 | 76.5891
~1~96~7~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of O2 | % | 20.5495 | 20.5495
~1~96~8~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~96~9~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O | % | 1.9093 | 1.9093
~1~96~10~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of H2O liquid | % | 0 | 0
~1~96~11~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of Ar | % | 0.92239 | 0.92239
~1~96~12~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Mole percent of SO2 | % | 0 | 0
~1~96~14~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~96~23~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: HCl mass flow | kg/hr | 0 | 0
~1~96~24~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: NOx mass flow | kg/hr | 0 | 0
~1~96~25~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: CO mass flow | kg/hr | 0 | 0
~1~96~26~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: UHC mass flow | kg/hr | 0 | 0
~1~96~29~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Hg mass flow | kg/hr | 0 | 0
~1~96~32~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Dry Oxygen | % | 20.9495 | 20.9495
~1~96~31~~-5001~ | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Normal volume flow | Nm^3/hr | 995396.75 | 995396.75
~1~97~0~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Pressure | bar | 1.0367 | 1.0367
~1~97~1~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Temperature | C | 26.2127 | 26.2127
~1~97~2~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mass flow | t/h | 1277.0692 | 1277.0692
~1~97~22~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash flow | t/h | 0 | 0
~1~97~16~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Fly ash enthalpy | kJ/kg | 0 | 0
~1~97~18~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Relative humidity | % | 58.1814 | 58.1814
~1~97~20~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Entropy | kJ/kg-C | 0.18571 | 0.18571
~1~97~3~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Enthalpy | kJ/kg | 1.2349 | 1.2349
~1~97~19~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Molecular weight | M.W. | 28.7578 | 28.7578
~1~97~4~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO2 mass flow | t/h | 0.58093 | 0.58093
~1~97~5~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Volume flow | m^3/s | 296.1704 | 296.1704
~1~97~101~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Density | kg/m^3 | 1.1978 | 1.1978
~1~97~6~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of N2 | % | 76.5891 | 76.5891
~1~97~7~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of O2 | % | 20.5495 | 20.5495
~1~97~8~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of CO2 | % | 0.029724 | 0.029724
~1~97~9~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O | % | 1.9093 | 1.9093
~1~97~10~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of H2O liquid | % | 0 | 0
~1~97~11~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of Ar | % | 0.92239 | 0.92239
~1~97~12~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Mole percent of SO2 | % | 0 | 0
~1~97~14~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~97~23~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: HCl mass flow | kg/hr | 0 | 0
~1~97~24~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: NOx mass flow | kg/hr | 0 | 0
~1~97~25~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: CO mass flow | kg/hr | 0 | 0
~1~97~26~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: UHC mass flow | kg/hr | 0 | 0
~1~97~29~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Hg mass flow | kg/hr | 0 | 0
~1~97~32~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Dry Oxygen | % | 20.9495 | 20.9495
~1~97~31~~-5001~ | 97 - Outlet of Boiler Assembly [1]: Fan [66] - SA Fan -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct: Normal volume flow | Nm^3/hr | 995396.75 | 995396.75
~1~98~0~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Pressure | bar | 1.1329 | 1.1329
~1~98~1~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Temperature | C | 27.2082 | 27.2082
~1~98~2~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mass flow | t/h | 372.8713 | 372.8713
~1~98~22~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash flow | t/h | 0 | 0
~1~98~16~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~98~18~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Relative humidity | % | 55.664 | 55.664
~1~98~20~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Entropy | kJ/kg-C | 0.162 | 0.162
~1~98~3~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Enthalpy | kJ/kg | 2.247 | 2.247
~1~98~19~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Molecular weight | M.W. | 28.7728 | 28.7728
~1~98~4~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO2 mass flow | t/h | 0.16976 | 0.16976
~1~98~5~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Volume flow | m^3/s | 79.3553 | 79.3553
~1~98~101~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Density | kg/m^3 | 1.3052 | 1.3052
~1~98~6~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of N2 | % | 76.6959 | 76.6959
~1~98~7~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of O2 | % | 20.5782 | 20.5782
~1~98~8~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~98~9~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O | % | 1.7725 | 1.7725
~1~98~10~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of H2O liquid | % | 0 | 0
~1~98~11~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of Ar | % | 0.92367 | 0.92367
~1~98~12~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Mole percent of SO2 | % | 0 | 0
~1~98~14~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~98~23~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: HCl mass flow | kg/hr | 0 | 0
~1~98~24~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: NOx mass flow | kg/hr | 0 | 0
~1~98~25~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: CO mass flow | kg/hr | 0 | 0
~1~98~26~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: UHC mass flow | kg/hr | 0 | 0
~1~98~29~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Hg mass flow | kg/hr | 0 | 0
~1~98~32~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Dry Oxygen | % | 20.9495 | 20.9495
~1~98~31~~-5001~ | 98 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - Inlet PA Duct -> Inlet of Splitter [9]: Normal volume flow | Nm^3/hr | 290478.8125 | 290478.8125
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Pressure | bar | 1.1129 | 1.1129
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Temperature | C | 25.85 | 25.85
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mass flow | t/h | 372.8713 | 372.8713
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Relative humidity | % | 59.24 | 59.24
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Entropy | kJ/kg-C | 0.16252 | 0.16252
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Enthalpy | kJ/kg | 0.86495 | 0.86495
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Molecular weight | M.W. | 28.7728 | 28.7728
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO2 mass flow | t/h | 0.16976 | 0.16976
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Volume flow | m^3/s | 80.4119 | 80.4119
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Density | kg/m^3 | 1.2881 | 1.2881
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of N2 | % | 76.6959 | 76.6959
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of O2 | % | 20.5782 | 20.5782
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of CO2 | % | 0.029766 | 0.029766
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O | % | 1.7725 | 1.7725
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of Ar | % | 0.92367 | 0.92367
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - Prim.Air -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan: Normal volume flow | Nm^3/hr | 290478.8125 | 290478.8125
~1~113~0~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 1.0043 | 1.0043
~1~113~1~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 797.6589 | 797.6589
~1~113~2~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 1667.917 | 1667.917
~1~113~22~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash flow | t/h | 8.1714 | 8.1714
~1~113~16~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Fly ash enthalpy | kJ/kg | 853.1778 | 853.1778
~1~113~18~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Relative humidity | % | 0 | 0
~1~113~20~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 1.7385 | 1.7385
~1~113~3~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 903.1089 | 903.1089
~1~113~19~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Molecular weight | M.W. | 29.0436 | 29.0436
~1~113~4~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~113~5~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Volume flow | m^3/s | 1414.2039 | 1414.2039
~1~113~101~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 0.32761 | 0.32761
~1~113~6~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of N2 | % | 69.3633 | 69.3633
~1~113~7~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of O2 | % | 3.7173 | 3.7173
~1~113~8~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~113~9~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O | % | 13.0614 | 13.0614
~1~113~10~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of Ar | % | 0.83426 | 0.83426
~1~113~12~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~113~14~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~113~23~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dry Oxygen | % | 4.2757 | 4.2757
~1~113~31~~-5001~ | 113 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~114~0~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 1.0018 | 1.0018
~1~114~1~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 774.2047 | 774.2047
~1~114~2~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 1667.917 | 1667.917
~1~114~22~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 8.1714 | 8.1714
~1~114~16~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 824.0283 | 824.0283
~1~114~18~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~114~20~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.7109 | 1.7109
~1~114~3~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 873.1886 | 873.1886
~1~114~19~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 29.0436 | 29.0436
~1~114~4~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~114~5~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 1386.6698 | 1386.6698
~1~114~101~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.33412 | 0.33412
~1~114~6~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 69.3633 | 69.3633
~1~114~7~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 3.7173 | 3.7173
~1~114~8~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~114~9~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 13.0614 | 13.0614
~1~114~10~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.83426 | 0.83426
~1~114~12~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~114~14~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~114~23~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 4.2757 | 4.2757
~1~114~31~~-5001~ | 114 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~1~116~0~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 1.0068 | 1.0068
~1~116~1~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 987.4717 | 987.4717
~1~116~2~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 1667.917 | 1667.917
~1~116~22~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash flow | t/h | 8.1714 | 8.1714
~1~116~16~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Fly ash enthalpy | kJ/kg | 1081.5461 | 1081.5461
~1~116~18~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Relative humidity | % | 0 | 0
~1~116~20~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 1.9496 | 1.9496
~1~116~3~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 1149.671 | 1149.671
~1~116~19~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Molecular weight | M.W. | 29.0436 | 29.0436
~1~116~4~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO2 mass flow | t/h | 328.6802 | 328.6802
~1~116~5~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Volume flow | m^3/s | 1660.7653 | 1660.7653
~1~116~101~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 0.27897 | 0.27897
~1~116~6~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of N2 | % | 69.3633 | 69.3633
~1~116~7~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of O2 | % | 3.7173 | 3.7173
~1~116~8~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of CO2 | % | 13.0047 | 13.0047
~1~116~9~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O | % | 13.0614 | 13.0614
~1~116~10~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of Ar | % | 0.83426 | 0.83426
~1~116~12~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mole percent of SO2 | % | 0.019061 | 0.019061
~1~116~14~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Sulfur trioxide SO3 | ppmv | 0.95306 | 0.95306
~1~116~23~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dry Oxygen | % | 4.2757 | 4.2757
~1~116~31~~-5001~ | 116 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Normal volume flow | Nm^3/hr | 1287244.375 | 1287244.375
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 0.175 | 0.175
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 285.2752 | 285.2752
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 0.53681 | 0.53681
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 8.9722 | 8.9722
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | 1.1874 | 1.1874
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 0.067935 | 0.067935
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 1.9906 | 1.9906
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.041888 | 0.041888
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [22] -> Heating steam inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 1.9696e-05 | 1.9696e-05
~2~4~0~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~4~1~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Temperature | C | 285.173 | 285.173
~2~4~2~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 0.94177 | 0.94177
~2~4~20~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 9.242 | 9.242
~2~4~4~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~4~3~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~4~5~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Steam quality |  | 1.1939 | 1.1939
~2~4~10~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.037849 | 0.037849
~2~4~11~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 1.9894 | 1.9894
~2~4~12~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.04187 | 0.04187
~2~4~13~~-5001~ | 4 - Outlet 1 of Splitter [22] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.9693e-05 | 1.9693e-05
~2~5~0~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 177.7064 | 177.7064
~2~5~1~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 242.4065 | 242.4065
~2~5~2~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 1108.6648 | 1108.6648
~2~5~20~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 2.6936 | 2.6936
~2~5~4~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 1050.8513 | 1050.8513
~2~5~3~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | -1496.6372 | -1496.6372
~2~5~5~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | -0.8431 | -0.8431
~2~5~10~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 824.4111 | 824.4111
~2~5~11~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 4.6449 | 4.6449
~2~5~12~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.64324 | 0.64324
~2~5~13~~-5001~ | 5 - Feedwater outlet of Feedwater Heater [17] - HPH-2 -> Feedwater inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 0.00011306 | 0.00011306
~2~6~0~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Pressure | bar | 10.4276 | 10.4276
~2~6~1~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Temperature | C | 136.2265 | 136.2265
~2~6~2~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Mass flow | t/h | 861.8255 | 861.8255
~2~6~20~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 1.6993 | 1.6993
~2~6~4~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 573.4191 | 573.4191
~2~6~3~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1974.0695 | -1974.0695
~2~6~5~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Steam quality |  | -0.098282 | -0.098282
~2~6~10~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Density | kg/m^3 | 929.883 | 929.883
~2~6~11~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.2742 | 4.2742
~2~6~12~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.68597 | 0.68597
~2~6~13~~-5001~ | 6 - Feedwater outlet of Feedwater Heater [56] - LPH-5 -> Feedwater inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00020237 | 0.00020237
~2~7~0~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Pressure | bar | 9.85 | 9.85
~2~7~1~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Temperature | C | 360.6185 | 360.6185
~2~7~2~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Mass flow | t/h | 41.1718 | 41.1718
~2~7~20~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Entropy | kJ/kg-C | 7.346 | 7.346
~2~7~4~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~7~3~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~7~5~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Steam quality |  | 1.2005 | 1.2005
~2~7~10~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Density | kg/m^3 | 3.4237 | 3.4237
~2~7~11~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~7~12~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~7~13~~-5001~ | 7 - Outlet 1 of Splitter [32] -> Inlet of Splitter [89]: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~9~0~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 35.78 | 35.78
~2~9~1~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 327.4125 | 327.4125
~2~9~2~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 940.2924 | 940.2924
~2~9~20~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~9~4~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~9~3~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~9~5~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | 1.14 | 1.14
~2~9~10~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 14.0078 | 14.0078
~2~9~11~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~9~12~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~9~13~~-5001~ | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~10~0~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Pressure | bar | 35.075 | 35.075
~2~10~1~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Temperature | C | 534.1036 | 534.1036
~2~10~2~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Mass flow | t/h | 942.8237 | 942.8237
~2~10~20~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Entropy | kJ/kg-C | 7.2559 | 7.2559
~2~10~4~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy | kJ/kg | 3528.7349 | 3528.7349
~2~10~3~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Enthalpy H* | kJ/kg | 981.2463 | 981.2463
~2~10~5~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Steam quality |  | 1.4143 | 1.4143
~2~10~10~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Density | kg/m^3 | 9.6337 | 9.6337
~2~10~11~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Specific heat | kJ/kg-C | 2.2571 | 2.2571
~2~10~12~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Thermal conductivity | W/m-C | 0.073641 | 0.073641
~2~10~13~~-5001~ | 10 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 -> Inlet of Boiler Assembly [1]: Valve [14]: Dynamic viscosity | kg/m-s | 3.0058e-05 | 3.0058e-05
~2~11~0~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Pressure | bar | 0.45641 | 0.45641
~2~11~1~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Temperature | C | 45.3184 | 45.3184
~2~11~2~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Mass flow | t/h | 858.8537 | 858.8537
~2~11~20~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Entropy | kJ/kg-C | 0.64279 | 0.64279
~2~11~4~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy | kJ/kg | 189.7462 | 189.7462
~2~11~3~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Enthalpy H* | kJ/kg | -2357.7424 | -2357.7424
~2~11~5~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Steam quality |  | -0.061141 | -0.061141
~2~11~10~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Density | kg/m^3 | 990.103 | 990.103
~2~11~11~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~11~12~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Thermal conductivity | W/m-C | 0.63566 | 0.63566
~2~11~13~~-5001~ | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Dynamic viscosity | kg/m-s | 0.0005921 | 0.0005921
~2~12~0~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Pressure | bar | 58.1048 | 58.1048
~2~12~1~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Temperature | C | 245.1857 | 245.1857
~2~12~2~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 75.4708 | 75.4708
~2~12~20~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.7444 | 2.7444
~2~12~4~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 1062.5718 | 1062.5718
~2~12~3~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1484.9167 | -1484.9167
~2~12~5~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Steam quality |  | -0.088667 | -0.088667
~2~12~10~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 808.35 | 808.35
~2~12~11~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.7909 | 4.7909
~2~12~12~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.62644 | 0.62644
~2~12~13~~-5001~ | 12 - Drain outlet of Feedwater Heater [16] - HPH-1 -> Water/steam addition to shell of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.0001086 | 0.0001086
~2~17~0~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Pressure | bar | 174.222 | 174.222
~2~17~1~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Temperature | C | 271.9911 | 271.9911
~2~17~2~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Mass flow | t/h | 1108.6648 | 1108.6648
~2~17~20~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Entropy | kJ/kg-C | 2.9608 | 2.9608
~2~17~4~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy | kJ/kg | 1192.1444 | 1192.1444
~2~17~3~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Enthalpy H* | kJ/kg | -1355.344 | -1355.344
~2~17~5~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Steam quality |  | -0.62531 | -0.62531
~2~17~10~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Density | kg/m^3 | 780.3115 | 780.3115
~2~17~11~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Specific heat | kJ/kg-C | 4.9299 | 4.9299
~2~17~12~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Thermal conductivity | W/m-C | 0.60761 | 0.60761
~2~17~13~~-5001~ | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Dynamic viscosity | kg/m-s | 0.00010007 | 0.00010007
~2~18~0~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Pressure | bar | 162.5 | 162.5
~2~18~1~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Temperature | C | 535.5406 | 535.5406
~2~18~2~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Mass flow | t/h | 1112.5415 | 1112.5415
~2~18~20~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Entropy | kJ/kg-C | 6.4241 | 6.4241
~2~18~4~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~18~3~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~18~5~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Steam quality |  | 1.9024 | 1.9024
~2~18~10~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Density | kg/m^3 | 48.9669 | 48.9669
~2~18~11~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Specific heat | kJ/kg-C | 2.7792 | 2.7792
~2~18~12~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Thermal conductivity | W/m-C | 0.086019 | 0.086019
~2~18~13~~-5001~ | 18 - Outlet of Pipe (PCE) [74] -> Inlet of Splitter [18]: Dynamic viscosity | kg/m-s | 3.0901e-05 | 3.0901e-05
~2~19~0~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Pressure | bar | 11.6372 | 11.6372
~2~19~1~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Temperature | C | 45.3735 | 45.3735
~2~19~2~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Mass flow | t/h | 861.8255 | 861.8255
~2~19~20~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Entropy | kJ/kg-C | 0.64303 | 0.64303
~2~19~4~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy | kJ/kg | 190.9593 | 190.9593
~2~19~3~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Enthalpy H* | kJ/kg | -2356.5293 | -2356.5293
~2~19~5~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Steam quality |  | -0.30215 | -0.30215
~2~19~10~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Density | kg/m^3 | 990.5665 | 990.5665
~2~19~11~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Specific heat | kJ/kg-C | 4.1769 | 4.1769
~2~19~12~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Thermal conductivity | W/m-C | 0.6363 | 0.6363
~2~19~13~~-5001~ | 19 - Discharge of General Pump [40] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [34] - GC: Dynamic viscosity | kg/m-s | 0.00059166 | 0.00059166
~2~20~0~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Pressure | bar | 59.74 | 59.74
~2~20~1~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Temperature | C | 384.7573 | 384.7573
~2~20~2~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Mass flow | t/h | 1112.0624 | 1112.0624
~2~20~20~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Entropy | kJ/kg-C | 6.4863 | 6.4863
~2~20~4~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy | kJ/kg | 3139.1685 | 3139.1685
~2~20~3~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Enthalpy H* | kJ/kg | 591.6798 | 591.6798
~2~20~5~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Steam quality |  | 1.2253 | 1.2253
~2~20~10~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Density | kg/m^3 | 21.6801 | 21.6801
~2~20~11~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Specific heat | kJ/kg-C | 2.6154 | 2.6154
~2~20~12~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Thermal conductivity | W/m-C | 0.059458 | 0.059458
~2~20~13~~-5001~ | 20 - Outlet of ST Assembly [1]: ST Group [13] -> Inlet of Splitter [19]: Dynamic viscosity | kg/m-s | 2.3713e-05 | 2.3713e-05
~2~21~0~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Pressure | bar | 59.74 | 59.74
~2~21~1~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Temperature | C | 384.7573 | 384.7573
~2~21~2~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Mass flow | t/h | 1036.5914 | 1036.5914
~2~21~20~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Entropy | kJ/kg-C | 6.4863 | 6.4863
~2~21~4~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy | kJ/kg | 3139.1685 | 3139.1685
~2~21~3~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Enthalpy H* | kJ/kg | 591.6798 | 591.6798
~2~21~5~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Steam quality |  | 1.2253 | 1.2253
~2~21~10~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Density | kg/m^3 | 21.6801 | 21.6801
~2~21~11~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Specific heat | kJ/kg-C | 2.6154 | 2.6154
~2~21~12~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Thermal conductivity | W/m-C | 0.059458 | 0.059458
~2~21~13~~-5001~ | 21 - Outlet 1 of Splitter [19] -> Inlet of ST Assembly [1]: ST Group [15]: Dynamic viscosity | kg/m-s | 2.3713e-05 | 2.3713e-05
~2~22~0~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Pressure | bar | 59.74 | 59.74
~2~22~1~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Temperature | C | 384.7573 | 384.7573
~2~22~2~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Mass flow | t/h | 75.4708 | 75.4708
~2~22~20~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Entropy | kJ/kg-C | 6.4863 | 6.4863
~2~22~4~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy | kJ/kg | 3139.1685 | 3139.1685
~2~22~3~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Enthalpy H* | kJ/kg | 591.6798 | 591.6798
~2~22~5~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Steam quality |  | 1.2253 | 1.2253
~2~22~10~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Density | kg/m^3 | 21.6801 | 21.6801
~2~22~11~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Specific heat | kJ/kg-C | 2.6154 | 2.6154
~2~22~12~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Thermal conductivity | W/m-C | 0.059458 | 0.059458
~2~22~13~~-5001~ | 22 - Outlet 3 of Splitter [19] -> Inlet of Pipe (PCE) [35]: Dynamic viscosity | kg/m-s | 2.3713e-05 | 2.3713e-05
~2~23~0~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | bar | 35.78 | 35.78
~2~23~1~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Temperature | C | 327.4125 | 327.4125
~2~23~2~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Mass flow | t/h | 1036.5914 | 1036.5914
~2~23~20~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~23~4~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~23~3~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~23~5~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Steam quality |  | 1.14 | 1.14
~2~23~10~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Density | kg/m^3 | 14.0078 | 14.0078
~2~23~11~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~23~12~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~23~13~~-5001~ | 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~24~0~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Pressure | bar | 35.78 | 35.78
~2~24~1~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Temperature | C | 327.4125 | 327.4125
~2~24~2~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Mass flow | t/h | 941.7711 | 941.7711
~2~24~20~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~24~4~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~24~3~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~24~5~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Steam quality |  | 1.14 | 1.14
~2~24~10~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Density | kg/m^3 | 14.0078 | 14.0078
~2~24~11~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~24~12~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~24~13~~-5001~ | 24 - Outlet 1 of Splitter [20] -> Inlet of Splitter [22]: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~25~0~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Pressure | bar | 35.78 | 35.78
~2~25~1~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Temperature | C | 327.4125 | 327.4125
~2~25~2~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Mass flow | t/h | 940.2924 | 940.2924
~2~25~20~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~25~4~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~25~3~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~25~5~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Steam quality |  | 1.14 | 1.14
~2~25~10~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Density | kg/m^3 | 14.0078 | 14.0078
~2~25~11~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~25~12~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~25~13~~-5001~ | 25 - Outlet 3 of Splitter [22] -> Inlet 3 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Pressure | bar | 35.78 | 35.78
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Temperature | C | 327.4125 | 327.4125
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Mass flow | t/h | 88.2415 | 88.2415
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Steam quality |  | 1.14 | 1.14
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Density | kg/m^3 | 14.0078 | 14.0078
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [20] -> Inlet of Pipe (PCE) [36]: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~27~0~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Pressure | bar | 162.5 | 162.5
~2~27~1~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Temperature | C | 535.5406 | 535.5406
~2~27~2~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Mass flow | t/h | 1112.5415 | 1112.5415
~2~27~20~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Entropy | kJ/kg-C | 6.4241 | 6.4241
~2~27~4~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~27~3~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~27~5~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Steam quality |  | 1.9024 | 1.9024
~2~27~10~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Density | kg/m^3 | 48.9669 | 48.9669
~2~27~11~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Specific heat | kJ/kg-C | 2.7792 | 2.7792
~2~27~12~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Thermal conductivity | W/m-C | 0.086019 | 0.086019
~2~27~13~~-5001~ | 27 - Outlet 3 of Splitter [18] -> Inlet of ST Assembly [1]: ST Group [13]: Dynamic viscosity | kg/m-s | 3.0901e-05 | 3.0901e-05
~2~28~0~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 35.0784 | 35.0784
~2~28~1~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 326.2738 | 326.2738
~2~28~2~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 88.2415 | 88.2415
~2~28~20~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 6.563 | 6.563
~2~28~4~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 3046.1467 | 3046.1467
~2~28~3~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | 498.6582 | 498.6582
~2~28~5~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | 1.1389 | 1.1389
~2~28~10~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 13.7436 | 13.7436
~2~28~11~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 2.5348 | 2.5348
~2~28~12~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.050813 | 0.050813
~2~28~13~~-5001~ | 28 - Outlet of Pipe (PCE) [36] -> Heating steam inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 2.1159e-05 | 2.1159e-05
~2~29~0~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Pressure | bar | 181.2605 | 181.2605
~2~29~1~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Temperature | C | 201.6832 | 201.6832
~2~29~2~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Mass flow | t/h | 1108.6648 | 1108.6648
~2~29~20~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Entropy | kJ/kg-C | 2.3213 | 2.3213
~2~29~4~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy | kJ/kg | 866.8958 | 866.8958
~2~29~3~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Enthalpy H* | kJ/kg | -1680.5928 | -1680.5928
~2~29~5~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Steam quality |  | -1.1354 | -1.1354
~2~29~10~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Density | kg/m^3 | 874.8438 | 874.8438
~2~29~11~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Specific heat | kJ/kg-C | 4.4166 | 4.4166
~2~29~12~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Thermal conductivity | W/m-C | 0.67689 | 0.67689
~2~29~13~~-5001~ | 29 - Feedwater outlet of Feedwater Heater [24] - HPH-3 -> Feedwater inlet of Feedwater Heater [17] - HPH-2: Dynamic viscosity | kg/m-s | 0.0001365 | 0.0001365
~2~30~0~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Pressure | bar | 35.0784 | 35.0784
~2~30~1~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Temperature | C | 207.2855 | 207.2855
~2~30~2~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 163.7123 | 163.7123
~2~30~20~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.3965 | 2.3965
~2~30~4~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 885.9738 | 885.9738
~2~30~3~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1661.5148 | -1661.5148
~2~30~5~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Steam quality |  | -0.093829 | -0.093829
~2~30~10~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 857.4168 | 857.4168
~2~30~11~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.5242 | 4.5242
~2~30~12~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.66038 | 0.66038
~2~30~13~~-5001~ | 30 - Drain outlet of Feedwater Heater [17] - HPH-2 -> Water/steam addition to shell of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00012913 | 0.00012913
~2~31~0~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Pressure | bar | 9.85 | 9.85
~2~31~1~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Temperature | C | 360.6185 | 360.6185
~2~31~2~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Mass flow | t/h | 815.9312 | 815.9312
~2~31~20~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Entropy | kJ/kg-C | 7.346 | 7.346
~2~31~4~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~31~3~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~31~5~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Steam quality |  | 1.2005 | 1.2005
~2~31~10~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Density | kg/m^3 | 3.4237 | 3.4237
~2~31~11~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~31~12~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~31~13~~-5001~ | 31 - Outlet 2 of Splitter [32] -> Inlet of ST Assembly [1]: ST Group [44]: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~32~0~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | bar | 32.6 | 32.6
~2~32~1~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Temperature | C | 532.2689 | 532.2689
~2~32~2~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Mass flow | t/h | 933.0945 | 933.0945
~2~32~20~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Entropy | kJ/kg-C | 7.2868 | 7.2868
~2~32~4~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy | kJ/kg | 3527.0349 | 3527.0349
~2~32~3~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Enthalpy H* | kJ/kg | 979.5462 | 979.5462
~2~32~5~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Steam quality |  | 1.4083 | 1.4083
~2~32~10~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Density | kg/m^3 | 8.9612 | 8.9612
~2~32~11~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Specific heat | kJ/kg-C | 2.2488 | 2.2488
~2~32~12~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Thermal conductivity | W/m-C | 0.07323 | 0.07323
~2~32~13~~-5001~ | 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Dynamic viscosity | kg/m-s | 2.9974e-05 | 2.9974e-05
~2~33~0~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Pressure | bar | 32.6 | 32.6
~2~33~1~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Temperature | C | 532.2689 | 532.2689
~2~33~2~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Mass flow | t/h | 933.0945 | 933.0945
~2~33~20~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Entropy | kJ/kg-C | 7.2868 | 7.2868
~2~33~4~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy | kJ/kg | 3527.0349 | 3527.0349
~2~33~3~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Enthalpy H* | kJ/kg | 979.5463 | 979.5463
~2~33~5~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Steam quality |  | 1.4083 | 1.4083
~2~33~10~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Density | kg/m^3 | 8.9612 | 8.9612
~2~33~11~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Specific heat | kJ/kg-C | 2.2488 | 2.2488
~2~33~12~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Thermal conductivity | W/m-C | 0.07323 | 0.07323
~2~33~13~~-5001~ | 33 - Outlet 1 of Splitter [27] -> Inlet 1 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.9974e-05 | 2.9974e-05
~2~34~0~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | bar | 17.44 | 17.44
~2~34~1~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Temperature | C | 438.8859 | 438.8859
~2~34~2~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Mass flow | t/h | 933.0945 | 933.0945
~2~34~20~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.3193 | 7.3193
~2~34~4~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3337.1973 | 3337.1973
~2~34~3~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 789.7088 | 789.7088
~2~34~5~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Steam quality |  | 1.2826 | 1.2826
~2~34~10~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Density | kg/m^3 | 5.4073 | 5.4073
~2~34~11~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1688 | 2.1688
~2~34~12~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.060663 | 0.060663
~2~34~13~~-5001~ | 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.6057e-05 | 2.6057e-05
~2~35~0~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Pressure | bar | 17.44 | 17.44
~2~35~1~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Temperature | C | 438.8859 | 438.8859
~2~35~2~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Mass flow | t/h | 910.3932 | 910.3932
~2~35~20~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Entropy | kJ/kg-C | 7.3193 | 7.3193
~2~35~4~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy | kJ/kg | 3337.1973 | 3337.1973
~2~35~3~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Enthalpy H* | kJ/kg | 789.7088 | 789.7088
~2~35~5~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Steam quality |  | 1.2826 | 1.2826
~2~35~10~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Density | kg/m^3 | 5.4073 | 5.4073
~2~35~11~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Specific heat | kJ/kg-C | 2.1688 | 2.1688
~2~35~12~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Thermal conductivity | W/m-C | 0.060663 | 0.060663
~2~35~13~~-5001~ | 35 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [28]: Dynamic viscosity | kg/m-s | 2.6057e-05 | 2.6057e-05
~2~36~0~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Pressure | bar | 17.44 | 17.44
~2~36~1~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Temperature | C | 438.8859 | 438.8859
~2~36~2~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Mass flow | t/h | 22.7014 | 22.7014
~2~36~20~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Entropy | kJ/kg-C | 7.3193 | 7.3193
~2~36~4~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy | kJ/kg | 3337.1973 | 3337.1973
~2~36~3~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Enthalpy H* | kJ/kg | 789.7088 | 789.7088
~2~36~5~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Steam quality |  | 1.2826 | 1.2826
~2~36~10~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Density | kg/m^3 | 5.4073 | 5.4073
~2~36~11~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Specific heat | kJ/kg-C | 2.1688 | 2.1688
~2~36~12~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Thermal conductivity | W/m-C | 0.060663 | 0.060663
~2~36~13~~-5001~ | 36 - Outlet 3 of Splitter [29] -> Inlet 3 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.6057e-05 | 2.6057e-05
~2~37~0~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Pressure | bar | 17.44 | 17.44
~2~37~1~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Temperature | C | 525.4932 | 525.4932
~2~37~2~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Mass flow | t/h | 9.7292 | 9.7292
~2~37~20~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Entropy | kJ/kg-C | 7.5708 | 7.5708
~2~37~4~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy | kJ/kg | 3527.0349 | 3527.0349
~2~37~3~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Enthalpy H* | kJ/kg | 979.5463 | 979.5463
~2~37~5~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Steam quality |  | 1.3816 | 1.3816
~2~37~10~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Density | kg/m^3 | 4.7877 | 4.7877
~2~37~11~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Specific heat | kJ/kg-C | 2.1992 | 2.1992
~2~37~12~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Thermal conductivity | W/m-C | 0.071299 | 0.071299
~2~37~13~~-5001~ | 37 - Outlet 3 of Splitter [27] -> Inlet 1 of Mixer [30]: Dynamic viscosity | kg/m-s | 2.9654e-05 | 2.9654e-05
~2~38~0~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Pressure | bar | 17.44 | 17.44
~2~38~1~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Temperature | C | 464.9683 | 464.9683
~2~38~2~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Mass flow | t/h | 32.4305 | 32.4305
~2~38~20~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Entropy | kJ/kg-C | 7.3978 | 7.3978
~2~38~4~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy | kJ/kg | 3394.1484 | 3394.1484
~2~38~3~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Enthalpy H* | kJ/kg | 846.66 | 846.66
~2~38~5~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Steam quality |  | 1.3123 | 1.3123
~2~38~10~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Density | kg/m^3 | 5.2032 | 5.2032
~2~38~11~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Specific heat | kJ/kg-C | 2.1749 | 2.1749
~2~38~12~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Thermal conductivity | W/m-C | 0.06379 | 0.06379
~2~38~13~~-5001~ | 38 - Outlet of Mixer [30] -> Inlet of Pipe (PCE) [37]: Dynamic viscosity | kg/m-s | 2.7149e-05 | 2.7149e-05
~2~39~0~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Pressure | bar | 16.2246 | 16.2246
~2~39~1~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Temperature | C | 182.9617 | 182.9617
~2~39~2~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 196.1428 | 196.1428
~2~39~20~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 2.1674 | 2.1674
~2~39~4~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 776.4781 | 776.4781
~2~39~3~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | -1771.0104 | -1771.0104
~2~39~5~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Steam quality |  | -0.04409 | -0.04409
~2~39~10~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 884.229 | 884.229
~2~39~11~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 4.4166 | 4.4166
~2~39~12~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.67414 | 0.67414
~2~39~13~~-5001~ | 39 - Drain outlet of Feedwater Heater [24] - HPH-3 -> Secondary stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 0.00014697 | 0.00014697
~2~40~0~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Pressure | bar | 10.3295 | 10.3295
~2~40~1~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Temperature | C | 176.5336 | 176.5336
~2~40~2~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Mass flow | t/h | 1117.8375 | 1117.8375
~2~40~20~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Entropy | kJ/kg-C | 2.1057 | 2.1057
~2~40~4~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy | kJ/kg | 747.8646 | 747.8646
~2~40~3~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Enthalpy H* | kJ/kg | -1799.6239 | -1799.6239
~2~40~5~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Steam quality |  | -0.010483 | -0.010483
~2~40~10~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Density | kg/m^3 | 890.7844 | 890.7844
~2~40~11~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Specific heat | kJ/kg-C | 4.3936 | 4.3936
~2~40~12~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Thermal conductivity | W/m-C | 0.67674 | 0.67674
~2~40~13~~-5001~ | 40 - Feedwater outlet of Deaerator [31] - DAER -> Inlet of Splitter [88]: Dynamic viscosity | kg/m-s | 0.00015258 | 0.00015258
~2~41~0~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | bar | 9.85 | 9.85
~2~41~1~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Temperature | C | 360.6185 | 360.6185
~2~41~2~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Mass flow | t/h | 910.3932 | 910.3932
~2~41~20~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Entropy | kJ/kg-C | 7.346 | 7.346
~2~41~4~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~41~3~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~41~5~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Steam quality |  | 1.2005 | 1.2005
~2~41~10~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Density | kg/m^3 | 3.4237 | 3.4237
~2~41~11~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~41~12~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~41~13~~-5001~ | 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~42~0~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Pressure | bar | 9.85 | 9.85
~2~42~1~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Temperature | C | 360.6185 | 360.6185
~2~42~2~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Mass flow | t/h | 53.2902 | 53.2902
~2~42~20~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Entropy | kJ/kg-C | 7.346 | 7.346
~2~42~4~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~42~3~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~42~5~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Steam quality |  | 1.2005 | 1.2005
~2~42~10~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Density | kg/m^3 | 3.4237 | 3.4237
~2~42~11~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~42~12~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~42~13~~-5001~ | 42 - Outlet 3 of Splitter [32] -> Inlet 2 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~43~0~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Pressure | bar | 9.85 | 9.85
~2~43~1~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Temperature | C | 353.6855 | 353.6855
~2~43~2~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Mass flow | t/h | 59.8692 | 59.8692
~2~43~20~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Entropy | kJ/kg-C | 7.3227 | 7.3227
~2~43~4~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy | kJ/kg | 3166.2844 | 3166.2844
~2~43~3~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Enthalpy H* | kJ/kg | 618.7959 | 618.7959
~2~43~5~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Steam quality |  | 1.1933 | 1.1933
~2~43~10~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Density | kg/m^3 | 3.4641 | 3.4641
~2~43~11~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Specific heat | kJ/kg-C | 2.1156 | 2.1156
~2~43~12~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Thermal conductivity | W/m-C | 0.050233 | 0.050233
~2~43~13~~-5001~ | 43 - Outlet of Mixer [33] -> Inlet of Pipe (PCE) [73]: Dynamic viscosity | kg/m-s | 2.2483e-05 | 2.2483e-05
~2~44~0~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Pressure | bar | 184.8857 | 184.8857
~2~44~1~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Temperature | C | 180.4437 | 180.4437
~2~44~2~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Mass flow | t/h | 1117.8375 | 1117.8375
~2~44~20~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~44~4~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~44~3~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~44~5~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Steam quality |  | -1.3315 | -1.3315
~2~44~10~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Density | kg/m^3 | 897.7841 | 897.7841
~2~44~11~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~44~12~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~44~13~~-5001~ | 44 - Outlet of Mixer [90] -> Inlet of Splitter [71]: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~45~0~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Pressure | bar | 35.78 | 35.78
~2~45~1~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Temperature | C | 327.4125 | 327.4125
~2~45~2~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Mass flow | t/h | 6.579 | 6.579
~2~45~20~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Entropy | kJ/kg-C | 6.5563 | 6.5563
~2~45~4~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy | kJ/kg | 3047.1467 | 3047.1467
~2~45~3~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Enthalpy H* | kJ/kg | 499.6581 | 499.6581
~2~45~5~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Steam quality |  | 1.14 | 1.14
~2~45~10~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Density | kg/m^3 | 14.0078 | 14.0078
~2~45~11~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Specific heat | kJ/kg-C | 2.5426 | 2.5426
~2~45~12~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Thermal conductivity | W/m-C | 0.051028 | 0.051028
~2~45~13~~-5001~ | 45 - Outlet 3 of Splitter [20] -> Inlet 1 of Mixer [33]: Dynamic viscosity | kg/m-s | 2.1206e-05 | 2.1206e-05
~2~46~0~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Pressure | bar | 32.6 | 32.6
~2~46~1~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Temperature | C | 474.6068 | 474.6068
~2~46~2~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~46~20~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Entropy | kJ/kg-C | 7.119 | 7.119
~2~46~4~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~46~3~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~46~5~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Steam quality |  | 1.3349 | 1.3349
~2~46~10~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Density | kg/m^3 | 9.7268 | 9.7268
~2~46~11~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Specific heat | kJ/kg-C | 2.241 | 2.241
~2~46~12~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Thermal conductivity | W/m-C | 0.06616 | 0.06616
~2~46~13~~-5001~ | 46 - Outlet of Valve [81] -> Inlet 3 of Mixer [25]: Dynamic viscosity | kg/m-s | 2.7571e-05 | 2.7571e-05
~2~47~0~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Pressure | bar | 58.5686 | 58.5686
~2~47~1~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Temperature | C | 383.4555 | 383.4555
~2~47~2~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Mass flow | t/h | 75.4708 | 75.4708
~2~47~20~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Entropy | kJ/kg-C | 6.4931 | 6.4931
~2~47~4~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy | kJ/kg | 3138.1685 | 3138.1685
~2~47~3~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Enthalpy H* | kJ/kg | 590.6799 | 590.6799
~2~47~5~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Steam quality |  | 1.2228 | 1.2228
~2~47~10~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Density | kg/m^3 | 21.2689 | 21.2689
~2~47~11~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Specific heat | kJ/kg-C | 2.6067 | 2.6067
~2~47~12~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Thermal conductivity | W/m-C | 0.059172 | 0.059172
~2~47~13~~-5001~ | 47 - Outlet of Pipe (PCE) [35] -> Heating steam inlet of Feedwater Heater [16] - HPH-1: Dynamic viscosity | kg/m-s | 2.3655e-05 | 2.3655e-05
~2~48~0~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Pressure | bar | 35.78 | 35.78
~2~48~1~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Temperature | C | 476.3312 | 476.3312
~2~48~2~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~48~20~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Entropy | kJ/kg-C | 7.0773 | 7.0773
~2~48~4~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~48~3~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~48~5~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Steam quality |  | 1.3402 | 1.3402
~2~48~10~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Density | kg/m^3 | 10.6795 | 10.6795
~2~48~11~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Specific heat | kJ/kg-C | 2.2548 | 2.2548
~2~48~12~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Thermal conductivity | W/m-C | 0.066629 | 0.066629
~2~48~13~~-5001~ | 48 - Outlet 2 of Splitter [18] -> Inlet of Valve [80]: Dynamic viscosity | kg/m-s | 2.7649e-05 | 2.7649e-05
~2~49~0~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 17.098 | 17.098
~2~49~1~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 464.3155 | 464.3155
~2~49~2~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 32.4305 | 32.4305
~2~49~20~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 7.4054 | 7.4054
~2~49~4~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 3393.1484 | 3393.1484
~2~49~3~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | 845.66 | 845.66
~2~49~5~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | 1.3115 | 1.3115
~2~49~10~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 5.1043 | 5.1043
~2~49~11~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 2.1733 | 2.1733
~2~49~12~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.063685 | 0.063685
~2~49~13~~-5001~ | 49 - Outlet of Pipe (PCE) [37] -> Heating steam inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 2.7122e-05 | 2.7122e-05
~2~50~0~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~50~1~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~50~2~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Mass flow | t/h | 41.1718 | 41.1718
~2~50~20~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Entropy | kJ/kg-C | 7.7133 | 7.7133
~2~50~4~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy | kJ/kg | 2441.4607 | 2441.4607
~2~50~3~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Enthalpy H* | kJ/kg | -106.0279 | -106.0279
~2~50~5~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Steam quality |  | 0.94086 | 0.94086
~2~50~10~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Density | kg/m^3 | 0.070746 | 0.070746
~2~50~11~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~50~12~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~50~13~~-5001~ | 50 - Outlet of Mixer [87] -> Inlet 3 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~51~0~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Pressure | bar | 3.88 | 3.88
~2~51~1~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Temperature | C | 247.614 | 247.614
~2~51~2~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Mass flow | t/h | 815.9312 | 815.9312
~2~51~20~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.3857 | 7.3857
~2~51~4~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2960.0698 | 2960.0698
~2~51~3~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | 412.5813 | 412.5813
~2~51~5~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Steam quality |  | 1.1046 | 1.1046
~2~51~10~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Density | kg/m^3 | 1.6369 | 1.6369
~2~51~11~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 2.0597 | 2.0597
~2~51~12~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.038447 | 0.038447
~2~51~13~~-5001~ | 51 - Outlet of ST Assembly [1]: ST Group [44] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.808e-05 | 1.808e-05
~2~52~0~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Pressure | bar | 32.6 | 32.6
~2~52~1~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Temperature | C | 532.2689 | 532.2689
~2~52~2~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Mass flow | t/h | 942.8237 | 942.8237
~2~52~20~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Entropy | kJ/kg-C | 7.2868 | 7.2868
~2~52~4~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy | kJ/kg | 3527.0349 | 3527.0349
~2~52~3~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Enthalpy H* | kJ/kg | 979.5463 | 979.5463
~2~52~5~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Steam quality |  | 1.4083 | 1.4083
~2~52~10~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Density | kg/m^3 | 8.9612 | 8.9612
~2~52~11~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Specific heat | kJ/kg-C | 2.2488 | 2.2488
~2~52~12~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Thermal conductivity | W/m-C | 0.07323 | 0.07323
~2~52~13~~-5001~ | 52 - Outlet of Pipe (PCE) [75] -> Inlet of Splitter [27]: Dynamic viscosity | kg/m-s | 2.9974e-05 | 2.9974e-05
~2~53~0~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 170.7891 | 170.7891
~2~53~1~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 317.0142 | 317.0142
~2~53~2~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 1108.6648 | 1108.6648
~2~53~20~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Entropy | kJ/kg-C | 3.3842 | 3.3842
~2~53~4~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy | kJ/kg | 1432.1023 | 1432.1023
~2~53~3~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | -1115.3862 | -1115.3862
~2~53~5~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Steam quality |  | -0.30707 | -0.30707
~2~53~10~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Density | kg/m^3 | 692.0003 | 692.0003
~2~53~11~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Specific heat | kJ/kg-C | 5.9258 | 5.9258
~2~53~12~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Thermal conductivity | W/m-C | 0.52992 | 0.52992
~2~53~13~~-5001~ | 53 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Dynamic viscosity | kg/m-s | 8.2394e-05 | 8.2394e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 170.7891 | 170.7891
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 352.6726 | 352.6726
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 1105.8999 | 1105.8999
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.1733 | 5.1733
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2544.8325 | 2544.8325
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | -2.656 | -2.656
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 120.458 | 120.458
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 18.0333 | 18.0333
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.14303 | 0.14303
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.4144e-05 | 2.4144e-05
~2~55~0~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 169.0981 | 169.0981
~2~55~1~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 420.0016 | 420.0016
~2~55~2~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 1105.8999 | 1105.8999
~2~55~20~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 5.8889 | 5.8889
~2~55~4~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 3009.0886 | 3009.0886
~2~55~3~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | 461.6002 | 461.6002
~2~55~5~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | 1.5303 | 1.5303
~2~55~10~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 69.7254 | 69.7254
~2~55~11~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 4.068 | 4.068
~2~55~12~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.08375 | 0.08375
~2~55~13~~-5001~ | 55 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 2.6046e-05 | 2.6046e-05
~2~56~0~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 165.7662 | 165.7662
~2~56~1~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 514.998 | 514.998
~2~56~2~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 1112.5415 | 1112.5415
~2~56~20~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.3372 | 6.3372
~2~56~4~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3333.9304 | 3333.9304
~2~56~3~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 786.4418 | 786.4418
~2~56~5~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.8679 | 1.8679
~2~56~10~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 52.213 | 52.213
~2~56~11~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.8842 | 2.8842
~2~56~12~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.084748 | 0.084748
~2~56~13~~-5001~ | 56 - Steam outlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 3.0065e-05 | 3.0065e-05
~2~57~0~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Pressure | bar | 1.47 | 1.47
~2~57~1~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Temperature | C | 148.393 | 148.393
~2~57~2~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Mass flow | t/h | 769.6258 | 769.6258
~2~57~20~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Entropy | kJ/kg-C | 7.4228 | 7.4228
~2~57~4~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy | kJ/kg | 2769.8633 | 2769.8633
~2~57~3~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Enthalpy H* | kJ/kg | 222.3747 | 222.3747
~2~57~5~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Steam quality |  | 1.0349 | 1.0349
~2~57~10~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Density | kg/m^3 | 0.76521 | 0.76521
~2~57~11~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Specific heat | kJ/kg-C | 2.0241 | 2.0241
~2~57~12~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Thermal conductivity | W/m-C | 0.028839 | 0.028839
~2~57~13~~-5001~ | 57 - Outlet of ST Assembly [1]: ST Group [45] -> Inlet of Splitter [50]: Dynamic viscosity | kg/m-s | 1.4109e-05 | 1.4109e-05
~2~58~0~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Pressure | bar | 0.78 | 0.78
~2~58~1~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Temperature | C | 93.5291 | 93.5291
~2~58~2~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Mass flow | t/h | 741.1432 | 741.1432
~2~58~20~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Entropy | kJ/kg-C | 7.4465 | 7.4465
~2~58~4~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy | kJ/kg | 2665.5569 | 2665.5569
~2~58~3~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Enthalpy H* | kJ/kg | 118.0683 | 118.0683
~2~58~5~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Steam quality |  | 1.0006 | 1.0006
~2~58~10~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Density | kg/m^3 | 0.46693 | 0.46693
~2~58~11~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Specific heat | kJ/kg-C | 2.0008 | 2.0008
~2~58~12~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Thermal conductivity | W/m-C | 0.024147 | 0.024147
~2~58~13~~-5001~ | 58 - Outlet of ST Assembly [1]: ST Group [46] -> Inlet of Splitter [51]: Dynamic viscosity | kg/m-s | 1.2059e-05 | 1.2059e-05
~2~59~0~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Pressure | bar | 3.88 | 3.88
~2~59~1~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Temperature | C | 247.614 | 247.614
~2~59~2~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Mass flow | t/h | 46.3054 | 46.3054
~2~59~20~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Entropy | kJ/kg-C | 7.3857 | 7.3857
~2~59~4~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy | kJ/kg | 2960.0698 | 2960.0698
~2~59~3~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Enthalpy H* | kJ/kg | 412.5813 | 412.5813
~2~59~5~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Steam quality |  | 1.1046 | 1.1046
~2~59~10~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Density | kg/m^3 | 1.6369 | 1.6369
~2~59~11~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Specific heat | kJ/kg-C | 2.0597 | 2.0597
~2~59~12~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Thermal conductivity | W/m-C | 0.038447 | 0.038447
~2~59~13~~-5001~ | 59 - Outlet 3 of Splitter [49] -> Inlet of Pipe (PCE) [60]: Dynamic viscosity | kg/m-s | 1.808e-05 | 1.808e-05
~2~60~0~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Pressure | bar | 3.88 | 3.88
~2~60~1~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Temperature | C | 247.614 | 247.614
~2~60~2~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Mass flow | t/h | 769.6258 | 769.6258
~2~60~20~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Entropy | kJ/kg-C | 7.3857 | 7.3857
~2~60~4~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy | kJ/kg | 2960.0698 | 2960.0698
~2~60~3~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Enthalpy H* | kJ/kg | 412.5813 | 412.5813
~2~60~5~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Steam quality |  | 1.1046 | 1.1046
~2~60~10~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Density | kg/m^3 | 1.6369 | 1.6369
~2~60~11~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Specific heat | kJ/kg-C | 2.0597 | 2.0597
~2~60~12~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Thermal conductivity | W/m-C | 0.038447 | 0.038447
~2~60~13~~-5001~ | 60 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [45]: Dynamic viscosity | kg/m-s | 1.808e-05 | 1.808e-05
~2~61~0~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Pressure | bar | 1.47 | 1.47
~2~61~1~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Temperature | C | 148.393 | 148.393
~2~61~2~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Mass flow | t/h | 28.4826 | 28.4826
~2~61~20~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Entropy | kJ/kg-C | 7.4228 | 7.4228
~2~61~4~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy | kJ/kg | 2769.8633 | 2769.8633
~2~61~3~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Enthalpy H* | kJ/kg | 222.3747 | 222.3747
~2~61~5~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Steam quality |  | 1.0349 | 1.0349
~2~61~10~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Density | kg/m^3 | 0.76521 | 0.76521
~2~61~11~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Specific heat | kJ/kg-C | 2.0241 | 2.0241
~2~61~12~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Thermal conductivity | W/m-C | 0.028839 | 0.028839
~2~61~13~~-5001~ | 61 - Outlet 3 of Splitter [50] -> Inlet of Pipe (PCE) [61]: Dynamic viscosity | kg/m-s | 1.4109e-05 | 1.4109e-05
~2~62~0~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Pressure | bar | 1.47 | 1.47
~2~62~1~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Temperature | C | 148.393 | 148.393
~2~62~2~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Mass flow | t/h | 741.1432 | 741.1432
~2~62~20~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Entropy | kJ/kg-C | 7.4228 | 7.4228
~2~62~4~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy | kJ/kg | 2769.8633 | 2769.8633
~2~62~3~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Enthalpy H* | kJ/kg | 222.3747 | 222.3747
~2~62~5~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Steam quality |  | 1.0349 | 1.0349
~2~62~10~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Density | kg/m^3 | 0.76521 | 0.76521
~2~62~11~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Specific heat | kJ/kg-C | 2.0241 | 2.0241
~2~62~12~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Thermal conductivity | W/m-C | 0.028839 | 0.028839
~2~62~13~~-5001~ | 62 - Outlet 1 of Splitter [50] -> Inlet of ST Assembly [1]: ST Group [46]: Dynamic viscosity | kg/m-s | 1.4109e-05 | 1.4109e-05
~2~63~0~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Pressure | bar | 0.283 | 0.283
~2~63~1~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Temperature | C | 67.7608 | 67.7608
~2~63~2~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Mass flow | t/h | 709.7795 | 709.7795
~2~63~20~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Entropy | kJ/kg-C | 7.4858 | 7.4858
~2~63~4~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy | kJ/kg | 2519.4097 | 2519.4097
~2~63~3~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Enthalpy H* | kJ/kg | -28.0788 | -28.0788
~2~63~5~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Steam quality |  | 0.95602 | 0.95602
~2~63~10~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Density | kg/m^3 | 0.18941 | 0.18941
~2~63~11~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~63~12~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~63~13~~-5001~ | 63 - Outlet of ST Assembly [1]: ST Group [47] -> Inlet of Splitter [4]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~64~0~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Pressure | bar | 0.78 | 0.78
~2~64~1~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Temperature | C | 93.5291 | 93.5291
~2~64~2~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Mass flow | t/h | 31.3637 | 31.3637
~2~64~20~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Entropy | kJ/kg-C | 7.4465 | 7.4465
~2~64~4~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy | kJ/kg | 2665.5569 | 2665.5569
~2~64~3~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Enthalpy H* | kJ/kg | 118.0683 | 118.0683
~2~64~5~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Steam quality |  | 1.0006 | 1.0006
~2~64~10~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Density | kg/m^3 | 0.46693 | 0.46693
~2~64~11~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Specific heat | kJ/kg-C | 2.0008 | 2.0008
~2~64~12~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Thermal conductivity | W/m-C | 0.024147 | 0.024147
~2~64~13~~-5001~ | 64 - Outlet 3 of Splitter [51] -> Inlet of Pipe (PCE) [63]: Dynamic viscosity | kg/m-s | 1.2059e-05 | 1.2059e-05
~2~65~0~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Pressure | bar | 0.283 | 0.283
~2~65~1~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Temperature | C | 67.7608 | 67.7608
~2~65~2~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Mass flow | t/h | 21.7079 | 21.7079
~2~65~20~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Entropy | kJ/kg-C | 7.4858 | 7.4858
~2~65~4~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy | kJ/kg | 2519.4097 | 2519.4097
~2~65~3~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Enthalpy H* | kJ/kg | -28.0788 | -28.0788
~2~65~5~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Steam quality |  | 0.95602 | 0.95602
~2~65~10~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Density | kg/m^3 | 0.18941 | 0.18941
~2~65~11~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~65~12~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~65~13~~-5001~ | 65 - Outlet 3 of Splitter [4] -> Inlet of Pipe (PCE) [64]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~66~0~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Pressure | bar | 0.78 | 0.78
~2~66~1~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Temperature | C | 93.5291 | 93.5291
~2~66~2~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Mass flow | t/h | 709.7795 | 709.7795
~2~66~20~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Entropy | kJ/kg-C | 7.4465 | 7.4465
~2~66~4~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy | kJ/kg | 2665.5569 | 2665.5569
~2~66~3~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Enthalpy H* | kJ/kg | 118.0683 | 118.0683
~2~66~5~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Steam quality |  | 1.0006 | 1.0006
~2~66~10~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Density | kg/m^3 | 0.46693 | 0.46693
~2~66~11~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Specific heat | kJ/kg-C | 2.0008 | 2.0008
~2~66~12~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Thermal conductivity | W/m-C | 0.024147 | 0.024147
~2~66~13~~-5001~ | 66 - Outlet 1 of Splitter [51] -> Inlet of ST Assembly [1]: ST Group [47]: Dynamic viscosity | kg/m-s | 1.2059e-05 | 1.2059e-05
~2~67~0~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Pressure | bar | 0.0975 | 0.0975
~2~67~1~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Temperature | C | 45.3132 | 45.3132
~2~67~2~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 688.3437 | 688.3437
~2~67~20~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.6489 | 7.6489
~2~67~4~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2420.9624 | 2420.9624
~2~67~3~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | -126.526 | -126.526
~2~67~5~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Steam quality |  | 0.93229 | 0.93229
~2~67~10~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 0.071395 | 0.071395
~2~67~11~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~67~12~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~67~13~~-5001~ | 67 - Outlet of ST Assembly [1]: ST Group [5] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~68~0~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~68~1~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Temperature | C | 27.3223 | 27.3223
~2~68~2~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Mass flow | t/h | 19511.1836 | 19511.1836
~2~68~20~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~68~4~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~68~3~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~68~5~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Steam quality |  | -0.13493 | -0.13493
~2~68~10~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Density | kg/m^3 | 996.4656 | 996.4656
~2~68~11~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~68~12~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~68~13~~-5001~ | 68 - Outlet 3 of Splitter [84] -> Suction of Pump (PCE) [83] - CWP-2: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~69~0~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Pressure | bar | 3.5 | 3.5
~2~69~1~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Temperature | C | 37.3673 | 37.3673
~2~69~2~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Mass flow | t/h | 39022.3672 | 39022.3672
~2~69~20~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Entropy | kJ/kg-C | 0.53702 | 0.53702
~2~69~4~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy | kJ/kg | 156.774 | 156.774
~2~69~3~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Enthalpy H* | kJ/kg | -2390.7146 | -2390.7146
~2~69~5~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Steam quality |  | -0.19907 | -0.19907
~2~69~10~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Density | kg/m^3 | 993.3504 | 993.3504
~2~69~11~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Specific heat | kJ/kg-C | 4.1775 | 4.1775
~2~69~12~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Thermal conductivity | W/m-C | 0.62587 | 0.62587
~2~69~13~~-5001~ | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Dynamic viscosity | kg/m-s | 0.00068574 | 0.00068574
~2~70~0~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Pressure | bar | 0.283 | 0.283
~2~70~1~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Temperature | C | 67.7608 | 67.7608
~2~70~2~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Mass flow | t/h | 688.0715 | 688.0715
~2~70~20~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Entropy | kJ/kg-C | 7.4858 | 7.4858
~2~70~4~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy | kJ/kg | 2519.4097 | 2519.4097
~2~70~3~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Enthalpy H* | kJ/kg | -28.0788 | -28.0788
~2~70~5~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Steam quality |  | 0.95602 | 0.95602
~2~70~10~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Density | kg/m^3 | 0.18941 | 0.18941
~2~70~11~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Specific heat | kJ/kg-C | 4.1884 | 4.1884
~2~70~12~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Thermal conductivity | W/m-C | 0.021786 | 0.021786
~2~70~13~~-5001~ | 70 - Outlet 1 of Splitter [4] -> Inlet of ST Assembly [1]: ST Group [5]: Dynamic viscosity | kg/m-s | 1.1192e-05 | 1.1192e-05
~2~71~0~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Temperature | C | 48.6122 | 48.6122
~2~71~2~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Mass flow | t/h | 127.8596 | 127.8596
~2~71~20~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Entropy | kJ/kg-C | 0.6858 | 0.6858
~2~71~4~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy | kJ/kg | 203.4954 | 203.4954
~2~71~3~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Enthalpy H* | kJ/kg | -2343.9932 | -2343.9932
~2~71~5~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Steam quality |  | -0.015204 | -0.015204
~2~71~10~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Density | kg/m^3 | 988.6693 | 988.6693
~2~71~11~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~71~12~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Thermal conductivity | W/m-C | 0.63946 | 0.63946
~2~71~13~~-5001~ | 71 - Drain outlet of Feedwater Heater [53] - LPH-8 -> Inlet 2 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00055932 | 0.00055932
~2~72~0~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 11.2872 | 11.2872
~2~72~1~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 45.7993 | 45.7993
~2~72~2~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 861.8255 | 861.8255
~2~72~20~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.64863 | 0.64863
~2~72~4~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 192.7082 | 192.7082
~2~72~3~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2354.7803 | -2354.7803
~2~72~5~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.29748 | -0.29748
~2~72~10~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 990.3715 | 990.3715
~2~72~11~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1771 | 4.1771
~2~72~12~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.63679 | 0.63679
~2~72~13~~-5001~ | 72 - Feedwater outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Feedwater inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00058725 | 0.00058725
~2~73~0~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Pressure | bar | 0.45641 | 0.45641
~2~73~1~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Temperature | C | 45.2485 | 45.2485
~2~73~2~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Mass flow | t/h | 861.8255 | 861.8255
~2~73~20~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Entropy | kJ/kg-C | 0.64187 | 0.64187
~2~73~4~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy | kJ/kg | 189.4538 | 189.4538
~2~73~3~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Enthalpy H* | kJ/kg | -2358.0347 | -2358.0347
~2~73~5~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Steam quality |  | -0.061268 | -0.061268
~2~73~10~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Density | kg/m^3 | 990.1324 | 990.1324
~2~73~11~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~73~12~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Thermal conductivity | W/m-C | 0.63558 | 0.63558
~2~73~13~~-5001~ | 73 - Outlet of Makeup / Blowdown [6] -> Suction of General Pump [40] - CP: Dynamic viscosity | kg/m-s | 0.00059283 | 0.00059283
~2~74~0~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.175 | 0.175
~2~74~1~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 48.6481 | 48.6481
~2~74~2~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 128.3965 | 128.3965
~2~74~20~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.68627 | 0.68627
~2~74~4~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 203.6454 | 203.6454
~2~74~3~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2343.843 | -2343.843
~2~74~5~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.01514 | -0.01514
~2~74~10~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 988.6534 | 988.6534
~2~74~11~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1805 | 4.1805
~2~74~12~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.6395 | 0.6395
~2~74~13~~-5001~ | 74 - Outlet of Mixer [39] -> Secondary steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.00055898 | 0.00055898
~2~75~0~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Pressure | bar | 0.175 | 0.175
~2~75~1~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Temperature | C | 57.2007 | 57.2007
~2~75~2~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Mass flow | t/h | 0.53681 | 0.53681
~2~75~20~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~75~4~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~75~3~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~75~5~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~75~10~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Density | kg/m^3 | 984.2903 | 984.2903
~2~75~11~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~75~12~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~75~13~~-5001~ | 75 - Drain outlet of Shell-Tube Water Heater (PCE) [34] - GC -> Inlet 3 of Mixer [39]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~76~0~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 0.0975 | 0.0975
~2~76~1~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 45.3132 | 45.3132
~2~76~2~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 730.4572 | 730.4572
~2~76~20~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 7.6551 | 7.6551
~2~76~4~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 2422.9253 | 2422.9253
~2~76~3~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -124.5633 | -124.5633
~2~76~5~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | 0.93311 | 0.93311
~2~76~10~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 0.071333 | 0.071333
~2~76~11~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~76~12~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~76~13~~-5001~ | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~78~0~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 11.0659 | 11.0659
~2~78~1~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 61.7129 | 61.7129
~2~78~2~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 861.8255 | 861.8255
~2~78~20~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 0.85208 | 0.85208
~2~78~4~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 259.218 | 259.218
~2~78~3~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2288.2705 | -2288.2705
~2~78~5~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.26177 | -0.26177
~2~78~10~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 982.7964 | 982.7964
~2~78~11~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.1829 | 4.1829
~2~78~12~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.65349 | 0.65349
~2~78~13~~-5001~ | 78 - Feedwater outlet of Feedwater Heater [53] - LPH-8 -> Feedwater inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.00045482 | 0.00045482
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.70449 | 0.70449
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Temperature | C | 64.5154 | 64.5154
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 106.1517 | 106.1517
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 0.88752 | 0.88752
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 270.0782 | 270.0782
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -2277.4102 | -2277.4102
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Steam quality |  | -0.047019 | -0.047019
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 980.8521 | 980.8521
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1866 | 4.1866
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.6555 | 0.6555
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater [54] - LPH-7 -> Water/steam addition to shell of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 0.00043641 | 0.00043641
~2~80~0~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 10.8489 | 10.8489
~2~80~1~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 84.4978 | 84.4978
~2~80~2~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 861.8255 | 861.8255
~2~80~20~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.1278 | 1.1278
~2~80~4~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 354.6534 | 354.6534
~2~80~3~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2192.8352 | -2192.8352
~2~80~5~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.21174 | -0.21174
~2~80~10~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 969.4272 | 969.4272
~2~80~11~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.1976 | 4.1976
~2~80~12~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.67095 | 0.67095
~2~80~13~~-5001~ | 80 - Feedwater outlet of Feedwater Heater [54] - LPH-7 -> Feedwater inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.0003361 | 0.0003361
~2~81~0~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Pressure | bar | 1.4412 | 1.4412
~2~81~1~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Temperature | C | 87.2968 | 87.2968
~2~81~2~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 74.788 | 74.788
~2~81~20~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 1.1612 | 1.1612
~2~81~4~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 365.6669 | 365.6669
~2~81~3~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | -2181.8218 | -2181.8218
~2~81~5~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Steam quality |  | -0.043219 | -0.043219
~2~81~10~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 967.1759 | 967.1759
~2~81~11~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 4.2021 | 4.2021
~2~81~12~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.6721 | 0.6721
~2~81~13~~-5001~ | 81 - Drain outlet of Feedwater Heater [55] - LPH-6 -> Water/steam addition to shell of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 0.00032492 | 0.00032492
~2~82~0~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 10.6362 | 10.6362
~2~82~1~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 104.4559 | 104.4559
~2~82~2~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 861.8255 | 861.8255
~2~82~20~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 1.3563 | 1.3563
~2~82~4~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 438.6047 | 438.6047
~2~82~3~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | -2108.8838 | -2108.8838
~2~82~5~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | -0.1676 | -0.1676
~2~82~10~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 955.5943 | 955.5943
~2~82~11~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 4.2188 | 4.2188
~2~82~12~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.68056 | 0.68056
~2~82~13~~-5001~ | 82 - Feedwater outlet of Feedwater Heater [55] - LPH-6 -> Feedwater inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 0.0002697 | 0.0002697
~2~84~0~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Pressure | bar | 3.8039 | 3.8039
~2~84~1~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Temperature | C | 107.26 | 107.26
~2~84~2~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 46.3054 | 46.3054
~2~84~20~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 1.3881 | 1.3881
~2~84~4~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 449.9346 | 449.9346
~2~84~3~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | -2097.554 | -2097.554
~2~84~5~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Steam quality |  | -0.068747 | -0.068747
~2~84~10~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 953.1785 | 953.1785
~2~84~11~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 4.2241 | 4.2241
~2~84~12~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.68113 | 0.68113
~2~84~13~~-5001~ | 84 - Drain outlet of Feedwater Heater [56] - LPH-5 -> Water/steam addition to shell of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 0.00026202 | 0.00026202
~2~85~0~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Pressure | bar | 3.8039 | 3.8039
~2~85~1~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Temperature | C | 246.9985 | 246.9985
~2~85~2~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Mass flow | t/h | 46.3054 | 46.3054
~2~85~20~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Entropy | kJ/kg-C | 7.3928 | 7.3928
~2~85~4~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy | kJ/kg | 2959.0698 | 2959.0698
~2~85~3~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Enthalpy H* | kJ/kg | 411.5813 | 411.5813
~2~85~5~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Steam quality |  | 1.1044 | 1.1044
~2~85~10~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Density | kg/m^3 | 1.6064 | 1.6064
~2~85~11~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Specific heat | kJ/kg-C | 2.058 | 2.058
~2~85~12~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Thermal conductivity | W/m-C | 0.038375 | 0.038375
~2~85~13~~-5001~ | 85 - Outlet of Pipe (PCE) [60] -> Heating steam inlet of Feedwater Heater [56] - LPH-5: Dynamic viscosity | kg/m-s | 1.8056e-05 | 1.8056e-05
~2~86~0~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Pressure | bar | 1.4412 | 1.4412
~2~86~1~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Temperature | C | 147.79 | 147.79
~2~86~2~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Mass flow | t/h | 28.4826 | 28.4826
~2~86~20~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Entropy | kJ/kg-C | 7.4294 | 7.4294
~2~86~4~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy | kJ/kg | 2768.8633 | 2768.8633
~2~86~3~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Enthalpy H* | kJ/kg | 221.3748 | 221.3748
~2~86~5~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Steam quality |  | 1.0348 | 1.0348
~2~86~10~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Density | kg/m^3 | 0.75115 | 0.75115
~2~86~11~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Specific heat | kJ/kg-C | 2.0223 | 2.0223
~2~86~12~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Thermal conductivity | W/m-C | 0.028778 | 0.028778
~2~86~13~~-5001~ | 86 - Outlet of Pipe (PCE) [61] -> Heating steam inlet of Feedwater Heater [55] - LPH-6: Dynamic viscosity | kg/m-s | 1.4086e-05 | 1.4086e-05
~2~87~0~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Pressure | bar | 0.76471 | 0.76471
~2~87~1~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Temperature | C | 92.9301 | 92.9301
~2~87~2~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Mass flow | t/h | 31.3637 | 31.3637
~2~87~20~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Entropy | kJ/kg-C | 7.4528 | 7.4528
~2~87~4~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy | kJ/kg | 2664.5569 | 2664.5569
~2~87~3~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Enthalpy H* | kJ/kg | 117.0683 | 117.0683
~2~87~5~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Steam quality |  | 1.0006 | 1.0006
~2~87~10~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Density | kg/m^3 | 0.45845 | 0.45845
~2~87~11~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Specific heat | kJ/kg-C | 1.9991 | 1.9991
~2~87~12~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Thermal conductivity | W/m-C | 0.02409 | 0.02409
~2~87~13~~-5001~ | 87 - Outlet of Pipe (PCE) [63] -> Heating steam inlet of Feedwater Heater [54] - LPH-7: Dynamic viscosity | kg/m-s | 1.2039e-05 | 1.2039e-05
~2~88~0~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Pressure | bar | 0.27745 | 0.27745
~2~88~1~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Temperature | C | 67.3104 | 67.3104
~2~88~2~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Mass flow | t/h | 21.7079 | 21.7079
~2~88~20~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Entropy | kJ/kg-C | 7.4915 | 7.4915
~2~88~4~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy | kJ/kg | 2518.4097 | 2518.4097
~2~88~3~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Enthalpy H* | kJ/kg | -29.0787 | -29.0787
~2~88~5~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Steam quality |  | 0.95594 | 0.95594
~2~88~10~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Density | kg/m^3 | 0.18594 | 0.18594
~2~88~11~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Specific heat | kJ/kg-C | 4.1881 | 4.1881
~2~88~12~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Thermal conductivity | W/m-C | 0.021747 | 0.021747
~2~88~13~~-5001~ | 88 - Outlet of Pipe (PCE) [64] -> Heating steam inlet of Feedwater Heater [53] - LPH-8: Dynamic viscosity | kg/m-s | 1.1177e-05 | 1.1177e-05
~2~99~0~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Pressure | bar | 35.78 | 35.78
~2~99~1~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Temperature | C | 324.9996 | 324.9996
~2~99~2~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Mass flow | t/h | 942.8237 | 942.8237
~2~99~20~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Entropy | kJ/kg-C | 6.5461 | 6.5461
~2~99~4~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy | kJ/kg | 3041.0444 | 3041.0444
~2~99~3~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Enthalpy H* | kJ/kg | 493.5559 | 493.5559
~2~99~5~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Steam quality |  | 1.1366 | 1.1366
~2~99~10~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Density | kg/m^3 | 14.0856 | 14.0856
~2~99~11~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Specific heat | kJ/kg-C | 2.5567 | 2.5567
~2~99~12~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Thermal conductivity | W/m-C | 0.050837 | 0.050837
~2~99~13~~-5001~ | 99 - Steam outlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2: Dynamic viscosity | kg/m-s | 2.1098e-05 | 2.1098e-05
~2~100~0~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Pressure | bar | 35.4257 | 35.4257
~2~100~1~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Temperature | C | 511.0027 | 511.0027
~2~100~2~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Mass flow | t/h | 942.8237 | 942.8237
~2~100~20~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Entropy | kJ/kg-C | 7.185 | 7.185
~2~100~4~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy | kJ/kg | 3475.947 | 3475.947
~2~100~3~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Enthalpy H* | kJ/kg | 928.4584 | 928.4584
~2~100~5~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Steam quality |  | 1.3849 | 1.3849
~2~100~10~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Density | kg/m^3 | 10.0489 | 10.0489
~2~100~11~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Specific heat | kJ/kg-C | 2.2537 | 2.2537
~2~100~12~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Thermal conductivity | W/m-C | 0.070799 | 0.070799
~2~100~13~~-5001~ | 100 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [77] - RH-2 -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1: Dynamic viscosity | kg/m-s | 2.91e-05 | 2.91e-05
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Pressure | bar | 169.0981 | 169.0981
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Temperature | C | 418.001 | 418.001
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Mass flow | t/h | 1110.0084 | 1110.0084
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Entropy | kJ/kg-C | 5.8769 | 5.8769
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy | kJ/kg | 3000.8169 | 3000.8169
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Enthalpy H* | kJ/kg | 453.3282 | 453.3282
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Steam quality |  | 1.5207 | 1.5207
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Density | kg/m^3 | 70.2765 | 70.2765
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Specific heat | kJ/kg-C | 4.1254 | 4.1254
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Thermal conductivity | W/m-C | 0.083964 | 0.083964
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH: Dynamic viscosity | kg/m-s | 2.5962e-05 | 2.5962e-05
~2~102~0~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Pressure | bar | 167.4239 | 167.4239
~2~102~1~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Temperature | C | 489.9974 | 489.9974
~2~102~2~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Mass flow | t/h | 1110.0084 | 1110.0084
~2~102~20~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Entropy | kJ/kg-C | 6.2336 | 6.2336
~2~102~4~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy | kJ/kg | 3256.6096 | 3256.6096
~2~102~3~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Enthalpy H* | kJ/kg | 709.121 | 709.121
~2~102~5~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Steam quality |  | 1.7984 | 1.7984
~2~102~10~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Density | kg/m^3 | 55.8631 | 55.8631
~2~102~11~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Specific heat | kJ/kg-C | 3.0461 | 3.0461
~2~102~12~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Thermal conductivity | W/m-C | 0.083323 | 0.083323
~2~102~13~~-5001~ | 102 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [23] - Pa-SH -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH: Dynamic viscosity | kg/m-s | 2.9019e-05 | 2.9019e-05
~2~103~0~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Pressure | bar | 9.6569 | 9.6569
~2~103~1~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Temperature | C | 353.0348 | 353.0348
~2~103~2~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Mass flow | t/h | 59.8692 | 59.8692
~2~103~20~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Entropy | kJ/kg-C | 7.33 | 7.33
~2~103~4~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy | kJ/kg | 3165.2844 | 3165.2844
~2~103~3~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Enthalpy H* | kJ/kg | 617.796 | 617.796
~2~103~5~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Steam quality |  | 1.1928 | 1.1928
~2~103~10~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Density | kg/m^3 | 3.3988 | 3.3988
~2~103~11~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Specific heat | kJ/kg-C | 2.1139 | 2.1139
~2~103~12~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Thermal conductivity | W/m-C | 0.050143 | 0.050143
~2~103~13~~-5001~ | 103 - Outlet of Pipe (PCE) [73] -> Heating stream inlet of Deaerator [31] - DAER: Dynamic viscosity | kg/m-s | 2.2456e-05 | 2.2456e-05
~2~104~0~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Pressure | bar | 184.8857 | 184.8857
~2~104~1~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Temperature | C | 180.4437 | 180.4437
~2~104~2~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Mass flow | t/h | 4.1084 | 4.1084
~2~104~20~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~104~4~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~104~3~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~104~5~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Steam quality |  | -1.3315 | -1.3315
~2~104~10~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Density | kg/m^3 | 897.7841 | 897.7841
~2~104~11~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~104~12~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~104~13~~-5001~ | 104 - Outlet 3 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68] - First Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~105~0~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 184.8857 | 184.8857
~2~105~1~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 180.4437 | 180.4437
~2~105~2~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 2.5331 | 2.5331
~2~105~20~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~105~4~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~105~3~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~105~5~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | -1.3315 | -1.3315
~2~105~10~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 897.7841 | 897.7841
~2~105~11~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~105~12~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~105~13~~-5001~ | 105 - Outlet 1 of Splitter [70] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~106~0~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Pressure | bar | 184.8857 | 184.8857
~2~106~1~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Temperature | C | 180.4437 | 180.4437
~2~106~2~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Mass flow | t/h | 1108.6648 | 1108.6648
~2~106~20~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~106~4~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~106~3~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~106~5~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Steam quality |  | -1.3315 | -1.3315
~2~106~10~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Density | kg/m^3 | 897.7841 | 897.7841
~2~106~11~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~106~12~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~106~13~~-5001~ | 106 - Outlet 3 of Splitter [71] -> Feedwater inlet of Feedwater Heater [24] - HPH-3: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~107~0~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Pressure | bar | 184.8857 | 184.8857
~2~107~1~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Temperature | C | 180.4437 | 180.4437
~2~107~2~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Mass flow | t/h | 6.6415 | 6.6415
~2~107~20~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~107~4~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~107~3~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~107~5~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Steam quality |  | -1.3315 | -1.3315
~2~107~10~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Density | kg/m^3 | 897.7841 | 897.7841
~2~107~11~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~107~12~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~107~13~~-5001~ | 107 - Outlet 2 of Splitter [71] -> Inlet of Splitter [70]: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~108~0~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | bar | 184.8857 | 184.8857
~2~108~1~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | C | 180.4437 | 180.4437
~2~108~2~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | t/h | 2.5312 | 2.5312
~2~108~20~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~108~4~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~108~3~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~108~5~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Steam quality |  | -1.3315 | -1.3315
~2~108~10~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Density | kg/m^3 | 897.7841 | 897.7841
~2~108~11~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~108~12~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~108~13~~-5001~ | 108 - Outlet 1 of Splitter [71] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Pressure | bar | 164.125 | 164.125
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Temperature | C | 536.8009 | 536.8009
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Mass flow | t/h | 1112.5415 | 1112.5415
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Entropy | kJ/kg-C | 6.4221 | 6.4221
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy | kJ/kg | 3398.4937 | 3398.4937
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Enthalpy H* | kJ/kg | 851.0052 | 851.0052
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Steam quality |  | 1.922 | 1.922
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Density | kg/m^3 | 49.4021 | 49.4021
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Specific heat | kJ/kg-C | 2.7833 | 2.7833
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Thermal conductivity | W/m-C | 0.086329 | 0.086329
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Pipe (PCE) [74]: Dynamic viscosity | kg/m-s | 3.0969e-05 | 3.0969e-05
~2~111~0~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Pressure | bar | 32.926 | 32.926
~2~111~1~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Temperature | C | 533.1637 | 533.1637
~2~111~2~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Mass flow | t/h | 942.8237 | 942.8237
~2~111~20~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Entropy | kJ/kg-C | 7.2844 | 7.2844
~2~111~4~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy | kJ/kg | 3528.7349 | 3528.7349
~2~111~3~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Enthalpy H* | kJ/kg | 981.2463 | 981.2463
~2~111~5~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Steam quality |  | 1.4099 | 1.4099
~2~111~10~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Density | kg/m^3 | 9.0419 | 9.0419
~2~111~11~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Specific heat | kJ/kg-C | 2.2501 | 2.2501
~2~111~12~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Thermal conductivity | W/m-C | 0.073366 | 0.073366
~2~111~13~~-5001~ | 111 - Outlet of Boiler Assembly [1]: Valve [14] -> Inlet of Pipe (PCE) [75]: Dynamic viscosity | kg/m-s | 3.0012e-05 | 3.0012e-05
~2~112~0~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 172.497 | 172.497
~2~112~1~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 271.7825 | 271.7825
~2~112~2~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 1108.6648 | 1108.6648
~2~112~20~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.9593 | 2.9593
~2~112~4~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 1191.1445 | 1191.1445
~2~112~3~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1356.344 | -1356.344
~2~112~5~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.60783 | -0.60783
~2~112~10~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 780.4302 | 780.4302
~2~112~11~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.93 | 4.93
~2~112~12~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.60765 | 0.60765
~2~112~13~~-5001~ | 112 - Outlet of Pipe (PCE) [76] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.0001001 | 0.0001001
~2~115~0~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Pressure | bar | 165.7662 | 165.7662
~2~115~1~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Temperature | C | 516.9982 | 516.9982
~2~115~2~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Mass flow | t/h | 1110.0084 | 1110.0084
~2~115~20~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Entropy | kJ/kg-C | 6.3446 | 6.3446
~2~115~4~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy | kJ/kg | 3339.772 | 3339.772
~2~115~3~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Enthalpy H* | kJ/kg | 792.2833 | 792.2833
~2~115~5~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Steam quality |  | 1.8745 | 1.8745
~2~115~10~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Density | kg/m^3 | 51.9941 | 51.9941
~2~115~11~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Specific heat | kJ/kg-C | 2.8745 | 2.8745
~2~115~12~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Thermal conductivity | W/m-C | 0.084901 | 0.084901
~2~115~13~~-5001~ | 115 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [79] - Pl-SH -> Steam inlet of Boiler Assembly [1]: Desuperheater [69] - Second Stage HP Desup: Dynamic viscosity | kg/m-s | 3.015e-05 | 3.015e-05
~2~117~0~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Pressure | bar | 35.78 | 35.78
~2~117~1~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Temperature | C | 476.3312 | 476.3312
~2~117~2~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~117~20~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Entropy | kJ/kg-C | 7.0773 | 7.0773
~2~117~4~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~117~3~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~117~5~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Steam quality |  | 1.3402 | 1.3402
~2~117~10~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Density | kg/m^3 | 10.6795 | 10.6795
~2~117~11~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Specific heat | kJ/kg-C | 2.2548 | 2.2548
~2~117~12~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Thermal conductivity | W/m-C | 0.066629 | 0.066629
~2~117~13~~-5001~ | 117 - Outlet of Valve [80] -> Inlet 1 of Mixer [21]: Dynamic viscosity | kg/m-s | 2.7649e-05 | 2.7649e-05
~2~118~0~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Pressure | bar | 32.6 | 32.6
~2~118~1~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Temperature | C | 474.6068 | 474.6068
~2~118~2~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~118~20~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Entropy | kJ/kg-C | 7.119 | 7.119
~2~118~4~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy | kJ/kg | 3396.7937 | 3396.7937
~2~118~3~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Enthalpy H* | kJ/kg | 849.3051 | 849.3051
~2~118~5~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Steam quality |  | 1.3349 | 1.3349
~2~118~10~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Density | kg/m^3 | 9.7268 | 9.7268
~2~118~11~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Specific heat | kJ/kg-C | 2.241 | 2.241
~2~118~12~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Thermal conductivity | W/m-C | 0.06616 | 0.06616
~2~118~13~~-5001~ | 118 - Outlet 1 of Splitter [18] -> Inlet of Valve [81]: Dynamic viscosity | kg/m-s | 2.7571e-05 | 2.7571e-05
~2~119~0~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~119~1~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Temperature | C | 27.3223 | 27.3223
~2~119~2~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Mass flow | t/h | 19511.1836 | 19511.1836
~2~119~20~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~119~4~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~119~3~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~119~5~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Steam quality |  | -0.13493 | -0.13493
~2~119~10~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Density | kg/m^3 | 996.4656 | 996.4656
~2~119~11~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~119~12~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~119~13~~-5001~ | 119 - Outlet 1 of Splitter [84] -> Suction of Pump (PCE) [82] - CWP-1: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~120~0~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Pressure | bar | 1.0135 | 1.0135
~2~120~1~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Temperature | C | 27.3223 | 27.3223
~2~120~2~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Mass flow | t/h | 39022.3672 | 39022.3672
~2~120~20~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Entropy | kJ/kg-C | 0.39967 | 0.39967
~2~120~4~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy | kJ/kg | 114.5467 | 114.5467
~2~120~3~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Enthalpy H* | kJ/kg | -2432.9419 | -2432.9419
~2~120~5~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Steam quality |  | -0.13493 | -0.13493
~2~120~10~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Density | kg/m^3 | 996.4656 | 996.4656
~2~120~11~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Specific heat | kJ/kg-C | 4.1786 | 4.1786
~2~120~12~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Thermal conductivity | W/m-C | 0.61159 | 0.61159
~2~120~13~~-5001~ | 120 - Outlet of Water Source [57] -> Inlet of Splitter [84]: Dynamic viscosity | kg/m-s | 0.00084396 | 0.00084396
~2~121~0~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~121~1~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~121~2~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Mass flow | t/h | 19511.1836 | 19511.1836
~2~121~20~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~121~4~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~121~3~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~121~5~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~121~10~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~121~11~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~121~12~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~121~13~~-5001~ | 121 - Discharge of Pump (PCE) [83] - CWP-2 -> Inlet 1 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~122~0~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Pressure | bar | 3.8447 | 3.8447
~2~122~1~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Temperature | C | 27.3502 | 27.3502
~2~122~2~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Mass flow | t/h | 19511.1836 | 19511.1836
~2~122~20~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~122~4~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~122~3~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~122~5~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Steam quality |  | -0.22627 | -0.22627
~2~122~10~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Density | kg/m^3 | 996.5845 | 996.5845
~2~122~11~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~122~12~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~122~13~~-5001~ | 122 - Discharge of Pump (PCE) [82] - CWP-1 -> Inlet 3 of Mixer [85]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~123~0~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Pressure | bar | 3.8447 | 3.8447
~2~123~1~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Temperature | C | 27.3502 | 27.3502
~2~123~2~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Mass flow | t/h | 39022.3672 | 39022.3672
~2~123~20~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Entropy | kJ/kg-C | 0.39998 | 0.39998
~2~123~4~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy | kJ/kg | 114.9255 | 114.9255
~2~123~3~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Enthalpy H* | kJ/kg | -2432.563 | -2432.563
~2~123~5~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Steam quality |  | -0.22627 | -0.22627
~2~123~10~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Density | kg/m^3 | 996.5845 | 996.5845
~2~123~11~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Specific heat | kJ/kg-C | 4.1778 | 4.1778
~2~123~12~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Thermal conductivity | W/m-C | 0.61178 | 0.61178
~2~123~13~~-5001~ | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Dynamic viscosity | kg/m-s | 0.0008434 | 0.0008434
~2~124~0~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~124~1~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~124~2~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Mass flow | t/h | 20.5189 | 20.5189
~2~124~20~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Entropy | kJ/kg-C | 7.7057 | 7.7057
~2~124~4~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy | kJ/kg | 2439.0479 | 2439.0479
~2~124~3~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Enthalpy H* | kJ/kg | -108.4408 | -108.4408
~2~124~5~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Steam quality |  | 0.93985 | 0.93985
~2~124~10~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Density | kg/m^3 | 0.070821 | 0.070821
~2~124~11~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~124~12~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~124~13~~-5001~ | 124 - Exhaust steam of ST-Driven Pump [86] - BFPT-B -> Inlet 3 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~125~0~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Pressure | bar | 0.0975 | 0.0975
~2~125~1~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Temperature | C | 45.3132 | 45.3132
~2~125~2~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Mass flow | t/h | 20.6528 | 20.6528
~2~125~20~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Entropy | kJ/kg-C | 7.7208 | 7.7208
~2~125~4~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy | kJ/kg | 2443.8579 | 2443.8579
~2~125~3~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Enthalpy H* | kJ/kg | -103.6306 | -103.6306
~2~125~5~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Steam quality |  | 0.94186 | 0.94186
~2~125~10~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Density | kg/m^3 | 0.07067 | 0.07067
~2~125~11~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~125~12~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Thermal conductivity | W/m-C | 0.019919 | 0.019919
~2~125~13~~-5001~ | 125 - Exhaust steam of ST-Driven Pump [1] - BFPT-A -> Inlet 1 of Mixer [87]: Dynamic viscosity | kg/m-s | 1.0474e-05 | 1.0474e-05
~2~126~0~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 10.3295 | 10.3295
~2~126~1~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 176.5336 | 176.5336
~2~126~2~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 558.9188 | 558.9188
~2~126~20~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 2.1057 | 2.1057
~2~126~4~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 747.8646 | 747.8646
~2~126~3~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | -1799.6239 | -1799.6239
~2~126~5~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | -0.010483 | -0.010483
~2~126~10~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 890.7844 | 890.7844
~2~126~11~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 4.3936 | 4.3936
~2~126~12~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.67674 | 0.67674
~2~126~13~~-5001~ | 126 - Outlet 3 of Splitter [88] -> Water inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 0.00015258 | 0.00015258
~2~127~0~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 10.3295 | 10.3295
~2~127~1~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 176.5336 | 176.5336
~2~127~2~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 558.9188 | 558.9188
~2~127~20~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 2.1057 | 2.1057
~2~127~4~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 747.8646 | 747.8646
~2~127~3~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | -1799.6239 | -1799.6239
~2~127~5~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | -0.010483 | -0.010483
~2~127~10~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 890.7844 | 890.7844
~2~127~11~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 4.3936 | 4.3936
~2~127~12~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.67674 | 0.67674
~2~127~13~~-5001~ | 127 - Outlet 1 of Splitter [88] -> Water inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 0.00015258 | 0.00015258
~2~128~0~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Pressure | bar | 9.85 | 9.85
~2~128~1~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Temperature | C | 360.6185 | 360.6185
~2~128~2~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Mass flow | t/h | 20.6528 | 20.6528
~2~128~20~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Entropy | kJ/kg-C | 7.346 | 7.346
~2~128~4~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~128~3~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~128~5~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Steam quality |  | 1.2005 | 1.2005
~2~128~10~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Density | kg/m^3 | 3.4237 | 3.4237
~2~128~11~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~128~12~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~128~13~~-5001~ | 128 - Outlet 1 of Splitter [89] -> Steam inlet of ST-Driven Pump [1] - BFPT-A: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~129~0~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Pressure | bar | 9.85 | 9.85
~2~129~1~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Temperature | C | 360.6185 | 360.6185
~2~129~2~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Mass flow | t/h | 20.5189 | 20.5189
~2~129~20~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Entropy | kJ/kg-C | 7.346 | 7.346
~2~129~4~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy | kJ/kg | 3180.9927 | 3180.9927
~2~129~3~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Enthalpy H* | kJ/kg | 633.5043 | 633.5043
~2~129~5~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Steam quality |  | 1.2005 | 1.2005
~2~129~10~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Density | kg/m^3 | 3.4237 | 3.4237
~2~129~11~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Specific heat | kJ/kg-C | 2.115 | 2.115
~2~129~12~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Thermal conductivity | W/m-C | 0.051001 | 0.051001
~2~129~13~~-5001~ | 129 - Outlet 3 of Splitter [89] -> Steam inlet of ST-Driven Pump [86] - BFPT-B: Dynamic viscosity | kg/m-s | 2.2776e-05 | 2.2776e-05
~2~130~0~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Pressure | bar | 184.8857 | 184.8857
~2~130~1~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Temperature | C | 180.4437 | 180.4437
~2~130~2~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Mass flow | t/h | 558.9188 | 558.9188
~2~130~20~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~130~4~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~130~3~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~130~5~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Steam quality |  | -1.3315 | -1.3315
~2~130~10~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Density | kg/m^3 | 897.7841 | 897.7841
~2~130~11~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~130~12~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~130~13~~-5001~ | 130 - Water outlet of ST-Driven Pump [1] - BFPT-A -> Inlet 3 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~2~131~0~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Pressure | bar | 184.8857 | 184.8857
~2~131~1~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Temperature | C | 180.4437 | 180.4437
~2~131~2~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Mass flow | t/h | 558.9188 | 558.9188
~2~131~20~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Entropy | kJ/kg-C | 2.1207 | 2.1207
~2~131~4~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy | kJ/kg | 774.1845 | 774.1845
~2~131~3~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Enthalpy H* | kJ/kg | -1773.3041 | -1773.3041
~2~131~5~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Steam quality |  | -1.3315 | -1.3315
~2~131~10~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Density | kg/m^3 | 897.7841 | 897.7841
~2~131~11~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Specific heat | kJ/kg-C | 4.3378 | 4.3378
~2~131~12~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Thermal conductivity | W/m-C | 0.68811 | 0.68811
~2~131~13~~-5001~ | 131 - Water outlet of ST-Driven Pump [86] - BFPT-B -> Inlet 1 of Mixer [90]: Dynamic viscosity | kg/m-s | 0.00015331 | 0.00015331
~3~77~0~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Pressure | bar | 1.0135 | 1.0135
~3~77~1~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | C | 30 | 30
~3~77~2~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Mass flow | t/h | 184.6997 | 184.6997
~3~77~3~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Enthalpy H* | kJ/kg | 17296.6777 | 17296.6777
~3~77~4~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: LHV | kJ/kg | 17286.1191 | 17286.1191
~3~77~5~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: HHV | kJ/kg | 18840.5996 | 18840.5996
~3~77~8~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Molecular weight | M.W. | 6.9862 | 6.9862
~3~77~6~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (LHV) | kW | 886886.125 | 886886.125
~3~77~7~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Energy flow (HHV) | kW | 966640.8125 | 966640.8125
~3~77~120~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Fuel LHV price | USD/GJ | 2.362 | 2.362
~3~77~20~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Ash | % | 5.36 | 5.36
~3~77~21~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Moisture | % | 27.99 | 27.99
~3~77~22~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Carbon | % | 48.63 | 48.63
~3~77~23~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Hydrogen | % | 3.99 | 3.99
~3~77~24~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Oxygen | % | 13.04 | 13.04
~3~77~25~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Nitrogen | % | 0.8 | 0.8
~3~77~26~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Sulfur | % | 0.19 | 0.19
~3~77~27~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Chlorine | % | 0 | 0
~3~77~28~~-5001~ | 77 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Advisory: 103 - The ratio of tempering air over total primary air at the design point is low. Then at off-design, pulverizer may not have enough energy to dry the fuel to the desired outlet conditions when the load is low. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,2
Note on E6: ****************** Advisory Messages ******************* Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct : Advisory: 1 - Inlet temperature is not higher than the threshold (or ambient) temperature and the temperature drop has been set to zero. Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Advisory: 103 - The ratio of tempering air over total primary air at the design point is low. Then at off-design, pulverizer may not have enough energy to dry the fuel to the desired outlet conditions when the load is low. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater [17] - HPH-2 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [53] - LPH-8 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Feedwater Heater [55] - LPH-6 : Remark: 1 - Specified heater outlet temperature has been reduced since the supplied heating steam pressure is too low. Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater : Remark: 4 - Primary air outlet temperature is limited by the minimum pinch. ST-Driven Pump [1] - BFPT-A : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST-Driven Pump [86] - BFPT-B : Remark: 50 - ST: Network set inlet pressure is higher than the specified turbine inlet pressure. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,2

## Eng_Info
Power Out | 350 | MW
Turbine Pressure
Load | Power | Range | Elink | HP - IP | 100% Case (bara) |  | 75% Case (bara) | 50% Case (bara) | Power (MW) | Ps (bara) | Ts ( C ) | Ms' ( tph ) | FEGT ( C ) | Stack ( C )
50% | 230 | 175 - <230 | ELINK (3) | Main steam (1st stage) | 162.5 |  | 152.5315 | 142 | 175 | 142 | 543.23 | 200.5 | 857 | 149.3 | 162.5
75% | 262.5 | 230 - 295 | ELINK (2) | 2nd Stage (inlet) | 59.74 | 0.36763 | 56.0753 | 52.2036 | 265 | 152.5315 | 552.554 |  |  |  | 59.74 | 0.36763
100% | 295 | >295 - 350 | ELINK | 2nd Stage Out (CRH) | 35.78 | 0.22018 | 33.5851 | 31.2662 | 350 | 162.5 | 561.36 | 387.7 | 894 | 148.2 | 35.78 | 0.22018
Full Load | 350 | MW |  | 3rd Stage (HRH) | 32.6 | 0.20062 | 30.6002 | 28.4874 | [6 empty] | 32.6 | 0.20062
|  |  |  | 4th Stage | 17.44 | 0.10732 | 16.3701 | 15.2399 | [6 empty] | 17.44 | 0.10732
|  |  |  | LP |  |  |  |  | Pw | Coal (tph)
|  |  |  | 5th Stage | 9.85 | 0.060615 | 9.2458 | 8.6074 | 175 | 92.74 |  |  |  |  | 9.85 | 0.060615
|  |  |  | 6th Stage | 3.88 | 0.023877 | 3.642 | 3.3905 | 265 | 140.8 |  |  |  |  | 3.88 | 0.023877
|  |  |  | 7th Stage | 1.47 | 0.0090462 | 1.3798 | 1.2846 | 350 | 184.7 |  |  |  |  | 1.47 | 0.0090462
[9 empty] | Pw | Ps
[9 empty] | 175 | 142 |  | 265 | 152.5315
[9 empty] | 350 | 162.5 |  | 330 | 160.143
[9 empty] | Pw | Ts
[9 empty] | 175 | 530.8 |  | 265 | 533.2285
[9 empty] | 350 | 535.5
[9 empty] | 355 | 550
[9 empty] | Pw | Ms | dsh
[9 empty] | 175 | 547.7 | 2.9
[9 empty] | 350 | 1112.5 | 6.6
[9 empty] | Pw | Ms'-6.6
[9 empty] | 175 | 544.8 |  | 265 | 833.3695
[9 empty] | 350 | 1105.9
[9 empty] | Pw | FEGT
350 | 162.62 | [7 empty] | 175 | 1131.2 |  | 265 | 1141.3715
| 4500.0955 | [7 empty] | 350 | 1151
Note on C11: Adhy Marwanto: Steam mass flow (saturated steam)

## input
Expected Output Power |  | 300 | MW | ELINK
Group | Status | Parameters | Unit | short_name | Baris (New) |  | Notes | min | max | param_name | input
Generator | view | Generator Power Factor |  | generator_power_factor | 495 | E495 |  | 0.75 | 0.95 | Generator [1]: Design point power factor | 0.9 | 1
Boiler | view | Desired Coal HHV (kJ/kg) | kcal/kg | desired_coal_hhv | 245 | E245 |  | 3375 | 4775 | Fuel Source [10] - Coal : HHV @ 25C | 4500 | 1
Boiler | view | Total Moisture (% wg) | % | total_moisture | 237 | E237 |  | 25 | 45 | Fuel Source [10] - Coal : Weight percent of Moisture | 30 | 1
Boiler | view | Main Steam Temp. | C | main_steam_temp | 436 | E436 | Korelasi formula dari expected output power | 510 | 538 | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | 534.17
Boiler | view | Saturated Steam Mass Flow | ton/h | sat_steam_mass_flow | 263 | E263 | Korelasi formula dari expected output power | 345 | 1175 | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Steam production rate | 945.59
Boiler | view | Main Steam Press. | bara | main_steam_press | 516 | E516 | Korelasi formula dari expected output power | 60 | 167 | ST Assembly [1]: ST Group [13] : Design point Inlet pressure (upstream of any stop or control valves) | 156.63
Boiler | view | Cold Reheat Press. | bara | cold_reheat_press | 492 | E492 | Korelasi formula dari main steam press | 13.8 | 38.41 | Fix Pressure Stream 23 - Outlet of ST Assembly [1]: ST Group [15] -> Inlet of Splitter [20]: Pressure | 34.4868
Boiler | view | HRH Press. | bara | hrh_press | 491 | E491 | Korelasi formula dari main steam press | 12.42 | 34.569 | Fix Pressure Stream 32 - Outlet of Mixer [25] -> Inlet of ST Assembly [1]: ST Group [26]: Pressure | 31.4223
Boiler | view | Excess Air | % |  | 265 | E265 |  | 15 | 40 | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Excess air | 25 | 1
Ambient Condition | view | Ambient Temperature ( C ) | C |  | 17 | E17 |  | 25 | 33 | Site Menu: Ambient temperature | 30 | 1
Ambient Condition | view | Relative Humidity (%) | % |  | 18 | E18 |  | 60 | 80 | Site Menu: Ambient relative humidity | 75 | 1
Ambient Condition | view | Ambient Pressure (bar) | bar |  | 20 | E20 |  | 1.0123 | 1.0132 | Site Menu: Ambient pressure | 1.0124 | 1
Turbine | background input | Fix Pressure Stream 34 (Outlet Stage-3) | bar | ip_turbine1_out | 493 | E493 | Korelasi formula dari main steam press |  |  | Fix Pressure Stream 34 - Outlet of ST Assembly [1]: ST Group [26] -> Inlet of Splitter [29]: Pressure | 16.81
Turbine | background input | Fix Pressure Stream 41 (Outlet Stage-4) | bar | ip_turbine2_out | 494 | E494 | Korelasi formula dari main steam press |  |  | Fix Pressure Stream 41 - Outlet of ST Assembly [1]: ST Group [28] -> Inlet of Splitter [32]: Pressure | 9.4941
Turbine | background input | Turbine 15 inlet Press | bar | hp_turbine2_in | 525 | E525 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [15] : Design point Inlet pressure (upstream of any stop or control valves) | 57.582
Turbine | background input | Turbine 26 inlet Press | bar | ip_turbine1_in | 534 | E534 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [26] : Design point Inlet pressure (upstream of any stop or control valves) | 31.4223
Turbine | background input | Turbine 28 inlet Press | bar | ip_turbine2_in | 543 | E543 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [28] : Design point Inlet pressure (upstream of any stop or control valves) | 16.81
Turbine | background input | Turbine 44 inlet Press | bar | lp_turbine1_in | 552 | E552 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [44] : Design point Inlet pressure (upstream of any stop or control valves) | 9.4941
Turbine | background input | Turbine 45 inlet Press | bar | lp_turbine2_in | 561 | E561 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [45] : Design point Inlet pressure (upstream of any stop or control valves) | 3.7398
Turbine | background input | Turbine 46 inlet Press | bar | lp_turbine3_in | 570 | E570 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [46] : Design point Inlet pressure (upstream of any stop or control valves) | 1.4169
Furnace | background input | FEGT | C | fegt | 264 | E264 | Korelasi formula dari expected output power |  |  | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Furnace exit temperature | 1145.33
Condenser | background input | Water Cooling Inlet Temp. | C | water_cooling_inlet_temp | 479 | E479 |  | 27 | 32 | Water Source [57] : Temperature | 29 | 1
Condenser | background input | Cooling Temp. Rise | C | cooling _temp_rise | 486 | E486 |  | 8 | 11 | Water-cooled Condenser (PCE) [59] : Cooling water temperature rise | 10 | 1
Note on F4: Adhy Marwanto: di konversi ke kJ/kg ketika di inject ke thermoflow. kali dengan 4.1868
Note on N4: Adhy Marwanto: input from what if sim. This default value is just tracing back value from the default modelling coal HHV.
Note on H7: Adhy Marwanto: steam production rate (from furnace / saturated steam)
Note on K16: Adhy Marwanto: no need boundary in background calculation

## output
CODE | Drawing | Show at View | Param Type | Param Group | Parameters | Unit |  | New | Value | param_name | default | margin_error
1 | N/A |  | output | Generator | Generator Power Factor | (tidak ada satuan) | generator_power_factor | 495 | 0.9 | Generator [1]: Design point power factor | 0.9 | 2.649e-06%
2 |  |  | output | Generator | Expected Gross Power Output | kW | expected_power_output | 605 | 350067.5938 | Plant Summary: Gross power | 350067.5938 | 0%
3 | N/A |  | output | Generator | Auxiliary Power consumption | kW | auxiliary_power_consumption | 608 | 20017.8145 | Plant Summary: Plant auxiliary | 20017.8145 | 0%
4 | D31 |  | output | Boiler | Desired Coal HHV | kJ/kg | desired_coal_hhv | 245 | 4500 | Fuel Source [10] - Coal : HHV @ 25C | 18840.5996 | 76.12%
5 | D53 | 1 | output | Generator | Gross Output | kW | gross_output | 605 | 350067.5938 | Plant Summary: Gross power | 350067.5938 | 0%
6 |  |  | output | Boiler | Boiler Efficiency | % | boiler_efficiency | 1996 | 83.9074 | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | 83.9074 | 0%
7 | N/A | 1 | output | Generator | Net Output | kW | net_output | 606 | 328299.4375 | Plant Summary: Net power | 328299.4375 | 0%
8 | N/A | 1 | output | Boiler | Net Heatrate (HHV) | kcal/kWh | net_heatrate | 619 | 10599.7949 | Plant Summary: Net heat rate(HHV) | 10599.7949 | 0%
9 | N/A | 1 | output | Plant | Gross Heatrate (LHV) | kcal/kWh | gross_heatrate | 611 | 9120.4961 | Plant Summary: Gross heat rate(LHV) | 9120.4961 | 0%
10 | N/A |  | output | Plant | Plant Efficiency (HHV) | kcal/kWh | plant_efficiency | 618 | 33.9629 | Plant Summary: Net electric efficiency(HHV) | 33.9629 | 0%
11 | N/A |  | output | Boiler | SSH Steam Outlet Temperature | C | ssh_steam_outlet_temperature | 1548 | 536.8 | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | 536.8 | 0%
12 | N/A |  | output | Boiler | SSH Steam Outlet Pressure | bara | ssh_steam_outlet_pressure | 1547 | 164.125 | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | 164.125 | 0%
13 | N/A |  | output | Boiler | SSH Steam Outlet Flow | ton/h | ssh_steam_outlet_flow | 1546 | 1112.5415 | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | 1112.5415 | 0%
14 | N/A |  | output | Boiler | FRH Steam Outlet Temperature | C | frh_steam_outlet_temperature | 1602 | 534.1 | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit temperature | 534.1 | 0%
15 | N/A |  | output | Boiler | FRH Steam Outlet Pressure | bara | frh_steam_outlet_pressure | 1601 | 35.075 | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit pressure | 35.075 | 0%
16 | N/A |  | output | Boiler | FRH Steam Outlet Flow | ton/h | frh_steam_outlet_flow | 1600 | 942.8237 | Boiler Assembly [1]: Superheater (PCE) - Parallel Flow [78] - RH-1 : Steam exit mass flow | 942.8237 | 0%
17 | D41 |  | output | Boiler | Main Steam Inlet Temperature | C | main_steam_inlet_temperature | 1730 | 535.5406 | ST Assembly [1]: ST Group [13] : Inlet temperature | 535.5406 | 0%
18 | D42 |  | output | Boiler | Main Steam Inlet Pressure | bara | main_steam_inlet_pressure | 1729 | 162.5 | ST Assembly [1]: ST Group [13] : Inlet pressure | 162.5 | 0%
19 | D40 |  | output | Boiler | Main Steam Inlet Flow | ton/h | main_steam_inlet_flow | 1731 | 1112.5415 | ST Assembly [1]: ST Group [13] : Inlet flow | 1112.5415 | 0%
20 | D44 |  | output | Boiler | HRH Steam Inlet Temperature | C | hrh_steam_inlet_temperature | 1784 | 532.2689 | ST Assembly [1]: ST Group [26] : Inlet temperature | 532.2689 | 0%
21 | D45 |  | output | Boiler | HRH Steam Inlet Pressure | bara | hrh_steam_inlet_pressure | 1783 | 32.6 | ST Assembly [1]: ST Group [26] : Inlet pressure | 32.6 | 0%
22 | D43 |  | output | Boiler | HRH Steam Inlet Flow | ton/h | hrh_steam_inlet_flow | 1785 | 933.0945 | ST Assembly [1]: ST Group [26] : Inlet flow | 933.0945 | 0%
23 | D51 |  | output | Turbine | LP ST Steam Inlet Temperature | C | lp_st_steam_inlet_temperature | 1838 | 360.6185 | ST Assembly [1]: ST Group [44] : Inlet temperature | 360.6185 | 0%
24 | D52 |  | output | Turbine | LP ST Steam Inlet Pressure | bara | lp_st_steam_inlet_pressure | 1837 | 9.85 | ST Assembly [1]: ST Group [44] : Inlet pressure | 9.85 | 0%
25 | D50 |  | output | Turbine | LP ST Steam Inlet Flow | ton/h | lp_st_steam_inlet_flow | 1839 | 815.9312 | ST Assembly [1]: ST Group [44] : Inlet flow | 815.9312 | 0%
26 | D20 |  | output | Condenser | Cond. CW Flow | ton/h | cond_cw_flow | 3284 | 39022.3672 | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Mass flow | 39022.3672 | 0%
27 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff1 | 1747 | 85.1821 | ST Assembly [1]: ST Group [13] : Dry step efficiency | 85.1821 | 0%
28 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff2 | 1774 | 67.9832 | ST Assembly [1]: ST Group [15] : Dry step efficiency | 67.9832 | 0%
29 | N/A |  | output | Turbine | IP Dry Step Eff. | % | ip_dry_step_eff1 | 1801 | 88.6914 | ST Assembly [1]: ST Group [26] : Dry step efficiency | 88.6914 | 0%
30 | N/A |  | output | Turbine | IP Dry Step Eff. | % | ip_dry_step_eff2 | 1828 | 89.8737 | ST Assembly [1]: ST Group [28] : Dry step efficiency | 89.8737 | 0%
31 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff1 | 1855 | 90.9151 | ST Assembly [1]: ST Group [44] : Dry step efficiency | 90.9151 | 0%
32 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff2 | 1882 | 92.0601 | ST Assembly [1]: ST Group [45] : Dry step efficiency | 92.0601 | 0%
33 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff3 | 1909 | 92.3209 | ST Assembly [1]: ST Group [46] : Dry step efficiency | 92.3209 | 0%
34 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff4 | 1936 | 92.25 | ST Assembly [1]: ST Group [47] : Dry step efficiency | 92.25 | 0%
35 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff5 | 1968 | 92.15 | ST Assembly [1]: ST Group [5] : Dry step efficiency | 92.15 | 0%
36 | D13 |  | output |  | FWH1 Terminal Temperature Difference | C | fwh1_terminal_temperature_difference | 924 | 1.5 | Feedwater Heater [16] - HPH-1 : Terminal difference | 1.5 | 0%
37 | D11 |  | output | FWH2 | FWH2 Terminal Temperature Difference | C | fwh2_terminal_temperature_difference | 933 | 0.27802 | Feedwater Heater [17] - HPH-2 : Terminal difference | 0.27802 | 0%
38 | D09 |  | output | FWH3 | FWH3 Terminal Temperature Difference | C | fwh3_terminal_temperature_difference | 942 | 0.38001 | Feedwater Heater [24] - HPH-3 : Terminal difference | 0.38001 | 0%
39 | D07 |  | output | Condensate | FWH5 Terminal Temperature Difference | C | fwh5_terminal_temperature_difference | 978 | 5.6 | Feedwater Heater [56] - LPH-5 : Terminal difference | 5.6 | 0%
40 | D05 |  | output | Condensate | FWH6 Terminal Temperature Difference | C | fwh6_terminal_temperature_difference | 969 | 5.7 | Feedwater Heater [55] - LPH-6 : Terminal difference | 5.7 | 0%
41 | D03 |  | output | Condensate | FWH7 Terminal Temperature Difference | C | fwh7_terminal_temperature_difference | 960 | 5.6 | Feedwater Heater [54] - LPH-7 : Terminal difference | 5.6 | 0%
42 | D01 |  | output | Condensate | FWH8 Terminal Temperature Difference | C | fwh8_terminal_temperature_difference | 951 | 5.6 | Feedwater Heater [53] - LPH-8 : Terminal difference | 5.6 | 0%
43 | D14 |  | output | FWH1 | FWH1 Drain Cooler Approach | C | fwh1_drain_cooler_approach | 925 | 2.8 | Feedwater Heater [16] - HPH-1 : Drain cooler approach | 2.8 | 0%
44 | D12 |  | output | FWH2 | FWH2 Drain Cooler Approach | C | fwh2_drain_cooler_approach | 934 | 5.6 | Feedwater Heater [17] - HPH-2 : Drain cooler approach | 5.6 | 0%
45 | D10 |  | output | FWH3 | FWH3 Drain Cooler Approach | C | fwh3_drain_cooler_approach | 943 | 2.5 | Feedwater Heater [24] - HPH-3 : Drain cooler approach | 2.5 | 0%
46 | D08 |  | output | Condensate | FWH5 Drain Cooler Approach | C | fwh5_drain_cooler_approach | 979 | 2.8 | Feedwater Heater [56] - LPH-5 : Drain cooler approach | 2.8 | 0%
47 | D06 |  | output | Condensate | FWH6 Drain Cooler Approach | C | fwh6_drain_cooler_approach | 970 | 2.8 | Feedwater Heater [55] - LPH-6 : Drain cooler approach | 2.8 | 0%
48 | D04 |  | output | Condensate | FWH7 Drain Cooler Approach | C | fwh7_drain_cooler_approach | 961 | 2.8 | Feedwater Heater [54] - LPH-7 : Drain cooler approach | 2.8 | 0%
49 | D02 |  | output | Condensate | FWH8 Drain Cooler Approach | C | fwh8_drain_cooler_approach | 952 | 2.8 | Feedwater Heater [53] - LPH-8 : Drain cooler approach | 2.8 | 0%
50 | D18 |  | output | Condenser | Cond. Main Steam Inlet Pressure | bara | cond_main_steam_inlet_pressure | 3359 | 0.0975 | 76 - Outlet of Mixer [62] -> Steam inlet of Water-cooled Condenser (PCE) [59]: Pressure | 0.0975 | 0%
51 | N/A |  | output | Condenser | Cond. Calculated Effectiveness | % | cond_calculated_effectiveness | N/A | #REF! | #REF! | #REF! | #REF!
52 | D19 |  | output | Condenser | Cond. Cooling Water Inlet Temperature | C | cond_cooling_water_inlet_temperature | 3701 | 27.3502 | 123 - Outlet of Mixer [85] -> CW inlet of Water-cooled Condenser (PCE) [59]: Temperature | 27.3502 | 0%
53 | D21 |  | output | Condenser | Cond. Cooling Water Exit Temperature | C | cond_cooling_water_exit_temperature | 3283 | 37.3673 | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Temperature | 37.3673 | 0%
54 | D20 |  | output | Condenser | Cond. Cooling Water Inlet Flow | ton/h | cond_cooling_water_inlet_flow | 3284 | 39022.3672 | 69 - CW outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Water Sink [58]: Mass flow | 39022.3672 | 0%
58 | D30 |  | output | Boiler | Coal Flow | ton/h | coal_flow | 1039 | 184.6997 | Boiler Assembly [1]: Furnace w/ Pulverizer [7] : Fuel mass flow | 184.6997 | 0%
59 | D38 |  | output | Boiler | Stack Temperature | C | stack_temperature | 2396 | 144.9853 | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | 144.9853 | 0%
60 | N/A |  | output | Ambient Air | Ambient Pressure | bara | ambient_pressure | 601 | 1.0124 | Plant Summary: Ambient pressure | 1.0124 | 0%
61 | N/A |  | output | Ambient Air | Ambient RH | % | ambient_rh | 603 | 75.41 | Plant Summary: Ambient RH | 75.41 | 0%
62 | N/A |  | output | Condenser | Cond. Condensate temperature | C | cond_condensate_temperature | 2689 | 45.3184 | 11 - Condensate outlet of Water-cooled Condenser (PCE) [59] -> Inlet of Makeup / Blowdown [6]: Temperature | 45.3184 | 0%
63 | D32 |  | output | Air Preheater | APH Flue gas inlet temperature | C | aph_flue_gas_inlet_temperature | 2180 | 352.373 | 16 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | 352.373 | 0%
64 | D34 |  | output | Air Preheater | SA Outlet Temp. | C | sa_outlet_temp | 2315 | 273.8889 | 92 - Main air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Combustion air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | 273.8889 | 0%
65 | D36 |  | output | Air Preheater | PA Outlet Temp. | C | pa_outlet_temp | 2045 | 320.6714 | 2 - Primary air outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Primary air inlet of Boiler Assembly [1]: Furnace w/ Pulverizer [7]: Temperature | 320.6714 | 0%
| D33 |  |  |  | Flue Gas Outlet Temp |  |  | 2288 | 140.7547 | 91 - Flue gas outlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | 140.7547 | 0%
| D35 |  |  |  | SA Inlet Temp ( C ) |  |  | 2423 | 26.2127 | 96 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - Inlet SA Duct -> Main air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | 26.2127 | 0%
| D37 |  |  |  | PA Inlet Temp ( C ) |  |  | 2261 | 27.2082 | 90 - Outlet 1 of Splitter [9] -> Primary air inlet of Boiler Assembly [1]: Rotary Air Heater [8] - Rotary Air Heater: Temperature | 27.2082 | 0%
| D46 |  |  |  | CRH Inlet Mass Flow ( t/h) |  |  | 2668 | 940.2924 | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Mass flow | 940.2924 | 0%
| D47 |  |  |  | CRH Inlet Temp ( C ) |  |  | 2667 | 327.4125 | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Temperature | 327.4125 | 0%
| D48 |  |  |  | CRH Inlet Pressure ( MPa ) |  |  | 2666 | 35.78 | 9 - Outlet of Mixer [21] -> Steam inlet of Boiler Assembly [1]: Desuperheater [67] - RH Desup: Pressure | 35.78 | 0%
| D55 |  |  |  | LP Steam Efficiency (Avg data diatas) (%) |  |  | AVERAGE(J35:J39) | #REF! | #REF! | #REF! | #REF!
| D56 |  |  |  | IP Steam Efficiency (Avg data diatas) (%) |  |  | AVERAGE(J33:J34) | #REF! | #REF! | #REF! | #REF!
| D57 |  |  |  | HP Steam Efficiency (Avg data diatas) (%) |  |  | AVERAGE(J31:J32) | #REF! | #REF! | #REF! | #REF!
| D58 |  |  |  | Ambient Temperature ( C ) |  |  | 17 | 30 | Site Menu: Ambient temperature | 26.95 | 11.32%
| D59 |  |  |  | Relative Humidity (%) |  |  | 18 | 75 | Site Menu: Ambient relative humidity | 75.41 | 0.5437%
| D60 |  |  |  | Ambient Pressure (bar) |  |  | 20 | 1.0124 | Site Menu: Ambient pressure | 1.0124 | 0.001275%
| D15 |  |  |  | Feedwater mass flow (t/h) |  |  | 2712 | 1108.6648 | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Mass flow | 1108.6648 | 0%
| D16 |  |  |  | Feedwater Temperature (C) |  |  | 2711 | 271.9911 | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Temperature | 271.9911 | 0%
| D17 |  |  |  | Feedwater Pressure (MPa) |  |  | 2710 | 174.222 | 17 - Feedwater outlet of Feedwater Heater [16] - HPH-1 -> Inlet of Pipe (PCE) [76]: Pressure | 174.222 | 0%
Note on F6: Adhy Marwanto: Yang ditampilkan MW hasil kalkulasi oleh thermoflow, bukan expected. Tampilan dalam MW.
Note on B10: Adhy Marwanto: Belum ada di gambar. Taruh di gambar boiler bagian tengah.
Note on B30: Adhy Marwanto: Double di bawah
Note on B31: Adhy Marwanto: Yang ditampilkan adalah hasil average.
Note on B61: Adhy Marwanto: Tambah di input dan tampilkan di area bawah Air Preheater.
Note on B76: Adhy Marwanto: ketiga item ini tampilkan di drawing posisi di bawah Air Heater.