## ELINK (3)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_50%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7 | #N/A | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342 | #N/A | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 200.5 | 234.534 | 234.534 | 234.534
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20 | #N/A | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 857.0001 | 863.7255 | 863.7255 | 863.7255
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25 | 25 | 25
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2 | #N/A | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907 | #N/A | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51 | #N/A | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396 | #N/A | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72 | #N/A | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3 | #N/A | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460 | #N/A | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339 | #N/A | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6 | #N/A | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.2158 | 5.2158 | #N/A | 5.2158
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.4352 | 153.4352 | #N/A | 153.4352
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161 | #N/A | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904 | #N/A | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436 | #N/A | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5 | #N/A | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2 | #N/A | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303 | #N/A | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.7969 | 99.7969 | #N/A | 99.7969
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.47583 | 0.47583 | #N/A | 0.47583
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2 | #N/A | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503 | #N/A | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 5.5636 | 5.5636 | #N/A | 5.5636
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 88.7768 | 88.7768 | #N/A | 88.7768
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 73.9174 | 73.9174 | #N/A | 73.9174
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 1.3878 | 1.3878 | #N/A | 1.3878
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 13.7909 | 13.7909 | #N/A | 13.7909
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 2.8631 | 2.8631 | #N/A | 2.8631
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 14.3538 | 14.3538 | #N/A | 14.3538
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 2.8631 | 2.8631 | #N/A | 2.8631
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 14.3538 | 14.3538 | #N/A | 14.3538
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 1.3878 | 1.3878 | #N/A | 1.3878
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 13.7909 | 13.7909 | #N/A | 13.7909
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85 | #N/A | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110 | #N/A | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125 | #N/A | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150 | #N/A | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 198.5162 | 198.5162 | #N/A | 198.5162
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19 | #N/A | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536 | #N/A | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 222.4745 | 222.4745 | #N/A | 222.4745
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1 | #N/A | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041 | #N/A | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778 | #N/A | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124 | #N/A | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33 | #N/A | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79 | #N/A | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392 | #N/A | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim | #N/A | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61 | #N/A | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35 | #N/A | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78 | #N/A | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55 | #N/A | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25 | #N/A | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41 | #N/A | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747 | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42 | #N/A | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75 | #N/A | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15 | #N/A | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9 | #N/A | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09 | #N/A | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91 | #N/A | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5 | #N/A | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8 | #N/A | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9 | #N/A | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0 | #N/A | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904 | #N/A | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306 | #N/A | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03 | #N/A | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92 | #N/A | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08 | #N/A | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989 | #N/A | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011 | #N/A | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954 | #N/A | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046 | #N/A | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873 | #N/A | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027 | #N/A | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942 | #N/A | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058 | #N/A | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393 | #N/A | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607 | #N/A | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 531.4 | 532.534 | 532.534 | 532.534
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0 | #N/A | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1 | #N/A | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5 | #N/A | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1 | #N/A | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3 | #N/A | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2 | #N/A | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75 | #N/A | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 27.3 | 27.3 | 27.3
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2 | #N/A | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985 | #N/A | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1 | #N/A | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1 | #N/A | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1 | #N/A | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1 | #N/A | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736 | #N/A | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241 | #N/A | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889 | #N/A | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15 | #N/A | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 71.35 | 74.0925 | 74.0925 | 74.0925
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81 | #N/A | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 22.93 | 23.8111 | 23.8111 | 23.8111
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86 | #N/A | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 15.31 | 15.8973 | 15.8973 | 15.8973
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91 | #N/A | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.268 | 5.471 | 5.471 | 5.471
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93 | #N/A | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 4.556 | 4.7308 | 4.7308 | 4.7308
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.806 | 1.8753 | 1.8753 | 1.8753
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.11 | 1.1527 | 1.1527 | 1.1527
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.331 | 0.34409 | 0.34409 | 0.34409
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP | #N/A | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 30
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 70.7778
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6328
~~~4~~-5000~ | Plant Summary: Gross power | kW | 55563.4844 | 65451.4688
~~~7~~-5000~ | Plant Summary: Net power | kW | 50058.3711 | 59233.4609
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 5505.1123 | 6218.0093
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 5227.2949 | 5890.752
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 277.8174 | 327.2573
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 34.8285 | 35.8783
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10336.3652 | 10033.9238
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.3778 | 32.4698
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11473.0957 | 11087.2324
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 159534.5781 | 182426.4219
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.3778 | 32.4698
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.3778 | 32.4698
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.4082 | 29.8727
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12672.4102 | 12051.1172
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 176211.1719 | 198285.9219
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 159534.5781 | 182426.4219
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.3778 | 32.4698
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 0.55332 | 0.63843
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.50125 | 0.58634
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 159534.5781 | 182426.4219
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 176211.1719 | 198285.9219
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 1400.8823 | 1601.8969
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 16955324 | 18522126
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 21785416 | 23808226
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 405.4728 | 479.791
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 4652.0288 | 5319.5542
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 4.5337 | 5.2311
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 439.0747 | 494.0794
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 21785.416 | 23808.2266
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 435.2003 | 401.9388
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 217199.0469 | 271867.4062
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 6535.625 | 7142.4688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 44.1091 | 49.5422
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 122.7651 | 140.7243
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.83582 | 0.72664
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 110028.5547 | 138941.6406
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.03633 | 0.034404
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 4.938 | 5.1987
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 16955324 | 18522126
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 16955324 | 18522126
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 3304113.25 | 3619109.5
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 20259438 | 22141236
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 21785416 | 23808226
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 55563.4883 | 65451.4688
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 520.5316 | 583.2448
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 217.5947 | 214.6272
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 578.6446 | 553.9448
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 146.0763 | 155.3615
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 299.2756 | 318.3599
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 146.0763 | 155.3615
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 299.2756 | 318.3599
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 497.6537 | 579.3955
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 52.5018 | 61.4402
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 649.8464 | 789.649
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 649.8465 | 789.6491
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 497.6537 | 579.3955
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 116.6833 | 137.4481
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 555.6349 | 654.5146
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 277.8174 | 327.2573
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 5227.2949 | 5890.752
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 159534.5781 | 182426.4219
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 9.6954 | 11.1867
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 271946.6562 | 296359.2188
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 365712.4375 | 405717.5625
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 15467.9766 | 18164.8945
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 4933.8022 | 5787.624
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 11213.1104 | 13146.5566
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 1368.9108 | 1610.326
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 7549.6353 | 8859.6807
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 3353.9839 | 3948.7363
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 7162.0562 | 8404.5469
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 5518.8594 | 6637.9624
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 520.5316 | 583.2448
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 217.5947 | 214.6272
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 578.6446 | 553.9448
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 146.0763 | 155.3615
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 299.2756 | 318.3599
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 146.0763 | 155.3615
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 299.2756 | 318.3599
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 497.6537 | 579.3955
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 52.5018 | 61.4402
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 649.8464 | 789.649
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 649.8465 | 789.6491
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 497.6537 | 579.3955
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 160.4 | 187.6272
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 40.1 | 46.9068
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 89.6174 | 93.0526
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 303.0413 | 305.7496
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2743.5149 | 2737.7437
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 857.0001 | 857.0001
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 303.0413 | 305.7496
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 66.0719
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 3.541
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.9605
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 15.6285
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0033418
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79472
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 94420.7578 | 112346.1094
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 61569.6211 | 73789.6953
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 15392.4053 | 18447.4238
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 7443.2061 | 8808.9951
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 10015.5273 | 11299.999
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 1396.3406 | 1571.3088
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 1888.4152 | 2246.9224
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 273.5357 | 302.9745
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 638.25 | 706.9405
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 95.7607 | 94.8223
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 172.9346 | 163.5786
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 166.4993 | 149.1612
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.085227 | 0.095903
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.31018 | 0.34903
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 37.8785 | 42.6246
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 909.0823 | 1022.9895
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 159534.5781 | 182430.4375
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 176211.1719 | 198290.2969
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 378.7842 | 426.2456
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 141.7473 | 156.9992
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 2.5038 | 2.8175
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.14905 | 0.16773
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.39087 | 0.43984
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 3.5437 | 3.925
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.0631 | 1.1775
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 2.4806 | 2.7475
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 3.541
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 15.6285
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.2158 | 5.2158
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.4352 | 153.4352
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.2567 | 5.2567
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 147.4578 | 148.8152
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 621.2406 | 627.0827
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 185.8018 | 217.9542
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 5.2158 | 5.4168
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 253.7416 | 253.4088
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2968.178 | 2966.8049
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.6261 | 1.3525
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 15.0098 | 15.0098
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 163.4898 | 163.626
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 691.1366 | 691.7283
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 23.4067 | 27.4697
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 647.1015 | 647.1015
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 210.8345 | 246.7764
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.9985 | 23.9988
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 79.3894 | 82.4325
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0035 | 460.0035
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 205.3774 | 240.3233
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3299.7864 | 3295.4045
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 79.3894 | 82.4325
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0049 | 436.0047
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 210.3333 | 246.19
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3237.772 | 3232.8083
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 4.9558 | 5.8667
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 667.8066 | 668.6221
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5995 | 22.5994
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 80.9772 | 84.0812
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.105 | 434.1047
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 200.5 | 234.534
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3230.1714 | 3225.0325
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 80.9772 | 84.0812
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5055 | 411.5053
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 205.3774 | 240.3233
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3169.3186 | 3163.4492
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 4.8774 | 5.7893
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 667.8066 | 668.6221
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 16.1319 | 17.2958
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 98.3662 | 104.077
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 16.7952 | 18.0066
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 16.7952 | 18.0066
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 16.1319 | 17.2958
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 201.0013 | 235.1203
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 97.683 | 101.4274
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 946.6247 | 948.2319
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 220.1776 | 220.5052
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 201.0013 | 235.1203
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 89.6174 | 93.0526
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 296.1452
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1361.6749 | 1322.0679
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 266.7267 | 287.6494
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 2.4806 | 2.7474
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 527.1766 | 486.7238
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 264.9475 | 225.5052
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 54.6383
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1159.5444 | 969.1915
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 23174.1426 | 24416.0625
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 23174.1426 | 24416.0625
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 173.8061 | 183.1205
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 8.0656 | 8.3747
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.7969 | 99.8081
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 217.5947 | 214.6272
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 126.1789 | 84.9468
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 317212.8438 | 303770.9375
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 266.7265 | 287.6678
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 2.4806 | 2.7474
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 2.4755 | 2.7421
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0050378 | 0.0052716
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3910.4263 | 3848.8792
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 12309.6279 | 13029.3408
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9417 | 7.3851
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 24.9997 | 25.0002
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 98.3914 | 104.1021
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2166 | 1.2402
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 286.3094 | 304.7254
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 286.3094 | 304.7254
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 283.4463 | 301.6781
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 14.3538 | 15.2773
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 2.8631 | 3.0473
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 314.2394 | 334.2779
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 95.689 | 95.7386
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 299.2756 | 318.3599
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 286.3094 | 304.7254
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 95.6675 | 95.7173
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 12.9662 | 13.6345
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 300.6249 | 319.9616
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 556.3565 | 532.4498
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 556.3565 | 532.4498
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 550.793 | 527.1253
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 88.7768 | 84.9557
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.137 | 80.1368
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 5.5636 | 5.3245
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 607.5768 | 581.642
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.1674 | 96.1389
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 578.6446 | 553.9448
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 556.3565 | 532.4498
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.1482 | 96.1196
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 22.2881 | 21.495
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 584.1743 | 559.0722
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 138.7824 | 147.7023
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 138.7824 | 147.7023
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 137.3946 | 146.2252
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 13.7909 | 14.6782
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 1.3878 | 1.477
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 153.3801 | 163.1296
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.0316 | 95.0946
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 146.0763 | 155.3615
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 138.7824 | 147.7023
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.0068 | 95.0701
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 7.2939 | 7.6592
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 145.7216 | 155.0874
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 286.3094 | 304.7254
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 286.3094 | 304.7254
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 283.4463 | 301.6781
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 14.3538 | 15.2773
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 2.8631 | 3.0473
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 314.2394 | 334.2779
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 95.689 | 95.7386
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 299.2756 | 318.3599
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 286.3094 | 304.7254
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 95.6675 | 95.7173
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 12.9662 | 13.6345
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 300.6249 | 319.9616
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 138.7824 | 147.7023
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 138.7824 | 147.7023
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 137.3946 | 146.2252
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 13.7909 | 14.6782
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 1.3878 | 1.477
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 153.3801 | 163.1296
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.0316 | 95.0946
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 146.0763 | 155.3615
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 138.7824 | 147.7023
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.0068 | 95.0701
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 7.2939 | 7.6592
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 145.7216 | 155.0874
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.32451 | 0.33734
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 70.9113 | 71.8159
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 4847.1968 | 5915.3955
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 4152.4326 | 5048.4565
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 694.7637 | 866.9384
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 22.4597 | 23.3647
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.0882 | 1.1301
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 101.987 | 103.0618
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 6733.3198 | 7943.564
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 5927.1265 | 6983.7363
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 806.1935 | 959.8275
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 31.0753 | 31.2458
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 1.7706 | 1.8385
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 116.4022 | 117.5702
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 3142.157 | 3711.1541
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 2943.1038 | 3473.4158
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 199.0532 | 237.7382
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.4141 | 14.5069
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 4.4667 | 4.638
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 147.634 | 149.0262
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 7274.0278 | 8586.8604
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 6517.9141 | 7700.1235
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 395.3543 | 455.9609
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 360.7595 | 430.7758
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 33.027 | 33.2154
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 0.19775 | 0.23304
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 15.0098 | 15.0098
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 198.3262 | 198.3262
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 10132.6807 | 11810.2607
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 7854.5508 | 9156.8242
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 1278.6514 | 1484.9817
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 999.4786 | 1168.4548
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 41.5853 | 41.4491
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 22.4804 | 22.6053
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 218.3745 | 218.6622
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 5937.5054 | 7039.478
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 4773.2168 | 5657.769
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1016.0961 | 1201.9607
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 148.1922 | 179.7481
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 23.62 | 23.9473
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.7725 | -3.8123
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7607 | 15424.9053
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 37.8785 | 42.6237
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 159534.5781 | 182426.4219
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 176211.1719 | 198285.9219
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 1400.8823 | 1601.8969
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15407.5234
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15424.9043
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16828.3848
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 20.46
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 30
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 7.5583
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 30.0002
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 59.0533 | 63.2706
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.026705 | 0.028587
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 30.0002
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 56.7375 | 60.7894
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.025658 | 0.027465
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 30.0002
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 59.0533 | 63.2706
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.026705 | 0.028587
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 30.0002
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 56.7375 | 60.7894
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.025658 | 0.027465
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.2982
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 477.9645 | 557.0624
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 463.6255 | 540.3505
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 497.6536 | 579.3955
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 3993.5029 | 4656.9551
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 3993.5029 | 4656.9551
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 515.0408 | 599.6385
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.0574 | 96.1589
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 497.6536 | 579.3955
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 477.9645 | 557.0624
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.0436 | 96.1454
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 19.6891 | 22.3331
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 494.6637 | 576.5251
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.2982
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 477.9645 | 557.0624
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 463.6255 | 540.3505
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 497.6536 | 579.3955
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 3993.5029 | 4656.9551
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 3993.5029 | 4656.9551
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 515.0408 | 599.6385
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.0574 | 96.1589
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 497.6536 | 579.3955
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 477.9645 | 557.0624
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.0436 | 96.1454
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 19.6891 | 22.3331
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 494.6637 | 576.5251
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.0574 | 96.1589
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 70.7352 | 70.7353
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.8677 | 6.8677
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.8677 | 6.8677
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 75.0006 | 75.0007
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 49.2097 | 57.7253
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 47.7334 | 55.9935
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 52.5018 | 61.4402
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 185.8018 | 217.9542
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.4265 | 45.428
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.1982 | 190.2045
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 185.8018 | 217.9542
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3251 | 7.3251
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5033 | 45.5049
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.1231 | 191.1294
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 54.3362 | 63.5868
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 93.7513 | 93.9747
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 52.5018 | 61.4402
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 49.2097 | 57.7253
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 93.7294 | 93.9536
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 3.2922 | 3.7149
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 50.929 | 59.7421
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1055.7338 | 1097.3058
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 96.0399 | 99.8217
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 96.0399 | 99.8217
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 49.9999 | 50.0001
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 625.0675 | 760.4329
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 606.3155 | 737.6199
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 649.8464 | 789.649
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 105.4173 | 123.3882
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 105.4173 | 123.3882
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 99.4872 | 103.269
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 141.7198 | 141.853
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 602.7352 | 603.5505
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 903.2138 | 1097.5237
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.4074 | 96.514
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 649.8464 | 789.649
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 625.0675 | 760.4329
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.187 | 96.3001
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 24.7789 | 29.2161
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 868.7739 | 1056.9165
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1055.7338 | 1097.3058
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 96.0399 | 99.8217
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 96.0399 | 99.8217
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 49.9999 | 50.0001
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 625.0676 | 760.433
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 606.3156 | 737.62
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 649.8465 | 789.6491
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 105.4173 | 123.3882
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 105.4173 | 123.3882
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 99.4872 | 103.269
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 141.7198 | 141.853
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 602.7352 | 603.5505
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 903.2139 | 1097.5238
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.4074 | 96.514
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 649.8465 | 789.6491
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 625.0676 | 760.433
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.187 | 96.3001
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 24.7789 | 29.2161
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 868.7739 | 1056.9167
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 0.55332 | 0.63843
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 185.2484 | 217.3158
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 185.8018 | 217.9542
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.4265 | 45.428
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.1982 | 190.2045
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0070449 | 0.0069281
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99296 | 0.99307
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 1.3954e-09 | 1.1921e-09
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 11678.3018 | 12509.2402
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 5719.4507 | 6131.04
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 5958.8516 | 6378.2007
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 5690.9956 | 6100.5376
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 5929.2056 | 6346.4688
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 58.1006 | 62.2341
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.052159 | 0.054168
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 1 | 1
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.40651 | 0.33811
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.2843 | 1.3337
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.44961 | 0.46688
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 2.5383 | 3.0106
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.3002 | 0.31171
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 3.9634 | 4.6197
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.089333 | 0.092761
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 3.056 | 3.6175
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.035412 | 0.03677
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 1.2933 | 1.5308
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.021765 | 0.022602
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 2.6303 | 3.1081
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0064902 | 0.0067468
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 1.8249 | 2.2263
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 0.97683 | 1.0143
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 502.5092 | 587.808
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 202.6887 | 237.2826
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.9482 | 0.94632
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7491 | 10.7495
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.04664 | 0.047233
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.95336 | 0.95277
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00077311 | 0.00054935
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99816 | 0.99838
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010692 | 0.0010694
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95643 | 0.95586
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.043574 | 0.044138
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92886 | 0.92914
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.071139 | 0.070856
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99214 | 0.99442
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0078553 | 0.0055813
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.94048 | 0.93995
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.059521 | 0.060052
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96981 | 0.96943
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0034013 | 0.0035386
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.026784 | 0.027035
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94383 | 0.94338
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.056166 | 0.056623
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.96243 | 0.96088
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.037571 | 0.039122
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 1.3954e-09 | 1.1921e-09
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50399 | 0.50332
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49601 | 0.49668
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 130.4938 | 88.6214
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 55.1079
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.0616
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 1303.4756 | 1466.6296
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 3.541
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.9605
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 15.6285
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 66.0719
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79472
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0033418
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.8301
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 100.9782
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 35.3298
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0050378 | 0.0052712
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9417 | 7.3848
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9997 | 24.9984
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 3.541
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 15.6285
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 210.3333 | 246.19
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 79.3894 | 82.4325
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3237.772 | 3232.8083
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0049 | 436.0047
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 210.3333 | 246.19
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 72.8343 | 75.6262
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 531.4 | 532.534
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3484.0369 | 3483.8638
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 266.7267 | 287.6494
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 2.4806 | 2.7474
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 857.0001 | 857.0001
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 709.7034 | 692.3391
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 14388.4736 | 17168.9707
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 6.5551 | 6.8064
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 200.5 | 234.534
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 87.8602 | 91.2281
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2923.342 | 2911.1914
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 339.0002 | 338.9989
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 200.5 | 234.534
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 80.9772 | 84.0812
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3230.1714 | 3225.0325
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 266.7267 | 287.6494
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 2.4806 | 2.7474
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 709.7033 | 692.3318
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 527.1765 | 486.727
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 17088.9531 | 20446.5293
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 128.1671 | 153.349
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 6.8831 | 7.1469
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 97.683 | 101.4274
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 220.1776 | 220.5052
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 946.6247 | 948.2319
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 201.0013 | 235.1203
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 97.683 | 101.4274
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 220.1776 | 220.5052
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 946.6247 | 948.2319
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.2 | 0.20001
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 72.8343 | 75.6262
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 531.3991 | 532.5332
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3484.0369 | 3483.8638
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 210.3333 | 246.19
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 72.6343 | 75.4262
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 531.3125 | 532.4471
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3484.0369 | 3483.8638
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 99.4872 | 103.269
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.1051 | 152.0499
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 99.4872 | 103.269
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.1051 | 152.0499
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 99.4872 | 103.269
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 156.931 | 157.0672
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 667.8068 | 668.6221
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 105.4173 | 123.3882
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 99.4872 | 103.269
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 156.931 | 157.0672
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 667.8068 | 668.6221
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 99.4872 | 103.269
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 156.931 | 157.0672
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 667.8068 | 668.6221
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 105.4173 | 123.3882
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 99.4872 | 103.269
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 156.931 | 157.0672
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 667.8068 | 668.6221
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 105.4173 | 123.3882
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 647.1015 | 647.1015
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 105.4173 | 123.3882
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 647.1015 | 647.1015
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 37.3932
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 156.815
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 7987.0059 | 9313.9102
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 27.3223
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 114.5466
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 7987.0059 | 9313.9102
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 92838.1484 | 108278.3125
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 55563.4844 | 65451.4688
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.2237 | 98.3341
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 87.5125 | 103.0861
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 29.1708 | 34.362
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 64.8241 | 76.36
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.2478 | 98.3567
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 74.9175 | 77.7971
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 530.7554 | 531.8716
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 209.9458 | 245.7915
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 58341.6562 | 68724.0391
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.2478 | 98.3567
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 55563.4844 | 65451.4688
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 56568.332 | 66560.3281
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.2237 | 98.3341
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1004.8465 | 1108.8599
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 882.1718 | 973.3364
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 122.6747 | 135.5235
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 9.0153 | 9.4468
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.2218 | 4.4284
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 111424.125 | 126258.2422
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 8.673 | 9.0256
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.1754 | 3.255
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 104761.9141 | 117692.3828
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 17.6883 | 18.4724
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.2218 | 4.4284
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 216186.0469 | 243950.6094
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 19.9505 | 20.815
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.0661 | 5.3141
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 13980676 | 15253281
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 16955324 | 18522126
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 71.35 | 74.0925
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 71.35 | 74.0925
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 530.7554 | 531.8716
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 209.9458 | 245.7915
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3484.0369 | 3483.8638
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 209.7123 | 245.5579
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 71.35 | 74.0925
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3484.0369 | 3483.8638
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 22.93 | 23.8111
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3217.8464 | 3216.894
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 22.93 | 23.8111
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 388.5145 | 388.7784
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 209.7123 | 245.5579
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3217.8464 | 3216.894
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 7.5035 | 8.4534
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.0072664 | 0.0081922
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1116 | 3.1117
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 72.7786 | 73.0296
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 74.9673 | 75.2078
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 74.9673 | 75.2078
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 15506.7432 | 18210.4199
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 15467.9766 | 18164.8945
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 38.7668 | 45.526
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 22.93 | 23.8111
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 22.93 | 23.8111
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 388.5145 | 388.7784
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 200.5742 | 234.7195
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3217.8464 | 3216.894
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 200.5742 | 234.7195
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 22.93 | 23.8111
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3217.8464 | 3216.894
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 15.31 | 15.8973
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3129.0718 | 3127.9055
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 15.31 | 15.8973
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 341.5981 | 341.6429
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 200.5742 | 234.7195
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3129.0718 | 3127.9055
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 10.0253 | 11.2862
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.019774 | 0.022274
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4977 | 1.4978
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 77.431 | 77.6783
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 77.8336 | 78.078
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 77.8336 | 78.078
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 4946.1675 | 5802.1294
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 4933.8022 | 5787.624
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 12.3654 | 14.5053
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 15.31 | 15.8973
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 15.31 | 15.8973
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 341.5981 | 341.6429
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 186.3056 | 218.0883
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3129.0718 | 3127.9055
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 186.3056 | 218.0883
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 15.31 | 15.8973
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3129.0718 | 3127.9055
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 5.268 | 5.471
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2911.8601 | 2910.3538
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 5.268 | 5.471
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.9248 | 226.6089
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 186.3056 | 218.0883
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2911.8601 | 2910.3538
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 22.1664 | 24.9449
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.026568 | 0.029934
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9062 | 2.9057
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 81.94 | 82.1851
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 83.3065 | 83.5366
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 83.3065 | 83.5366
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 11241.2129 | 13179.5049
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 11213.1104 | 13146.5566
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 28.103 | 32.9487
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 5.268 | 5.471
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 5.268 | 5.471
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.9248 | 226.6089
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 184.8421 | 216.8711
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2911.8601 | 2910.3538
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 184.8421 | 216.8711
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 5.268 | 5.471
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2911.8601 | 2910.3538
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 4.556 | 4.7308
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2885.1326 | 2883.5564
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 4.556 | 4.7308
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 212.7618 | 212.3932
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 184.8421 | 216.8711
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2885.1326 | 2883.5564
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 24.7252 | 27.8895
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.069329 | 0.078261
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1563 | 1.1565
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 82.971 | 83.2316
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 82.9709 | 83.2319
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 82.9709 | 83.2319
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 1372.3416 | 1614.3618
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 1368.9108 | 1610.326
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 3.4309 | 4.0359
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 4.556 | 4.7308
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 4.556 | 4.7308
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 212.7618 | 212.3932
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 173.8402 | 203.8476
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2885.1326 | 2883.5564
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 173.8402 | 203.8476
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 4.556 | 4.7308
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2885.1326 | 2883.5564
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 1.806 | 1.8753
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2728.4001 | 2726.7024
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 1.806 | 1.8753
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 129.6388 | 129.1544
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 173.8402 | 203.8476
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2728.4001 | 2726.7024
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 48.7446 | 54.9302
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.074341 | 0.08388
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5227 | 2.5227
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.2419 | 85.4617
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 85.9414 | 86.1423
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 85.9414 | 86.1423
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 7568.5566 | 8881.8857
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 7549.6353 | 8859.6807
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 18.9214 | 22.2047
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 1.806 | 1.8753
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 1.806 | 1.8753
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 129.6388 | 129.1544
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 168.5928 | 197.6152
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2728.4001 | 2726.7024
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 168.5928 | 197.6152
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 1.806 | 1.8753
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2728.4001 | 2726.7024
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.11 | 1.1527
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2656.6035 | 2654.5881
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.11 | 1.1527
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 102.5497 | 103.6282
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 168.5928 | 197.6152
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2656.6035 | 2654.5881
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 71.2185 | 80.4461
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.16579 | 0.18696
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.627 | 1.6268
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 84.8771 | 85.2989
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 84.877 | 85.2989
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 84.877 | 85.2989
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 3362.3899 | 3958.6331
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 3353.9839 | 3948.7363
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 8.406 | 9.8966
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.11 | 1.1527
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.11 | 1.1527
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 102.5497 | 103.6282
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 159.1236 | 186.4257
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2656.6035 | 2654.5881
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 159.1236 | 186.4257
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.11 | 1.1527
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2656.6035 | 2654.5881
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.331 | 0.34409
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2494.166 | 2491.8867
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.331 | 0.34409
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 71.3726 | 72.2801
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 159.1236 | 186.4257
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2494.166 | 2491.8867
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 198.6041 | 223.9733
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.24374 | 0.27485
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.3535 | 3.3501
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 86.8568 | 87.1362
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.2836 | 85.4287
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.2836 | 85.4287
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 7180.0063 | 8425.6113
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 7162.0562 | 8404.5469
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 17.95 | 21.064
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.331 | 0.34409
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.331 | 0.34409
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 71.3726 | 72.2801
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 153.1451 | 179.1322
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2494.166 | 2491.8867
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 153.1451 | 179.1322
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.331 | 0.34409
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2494.166 | 2491.8867
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2356.2915 | 2349.5378
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 153.3265 | 179.3137
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2364.5938 | 2358.5713
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 572.9338 | 668.0649
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 3.8712 | 4.2895
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 147.9986 | 155.7457
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2032.2527 | 2125.3506
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 606.3444 | 642.4245
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 7.8189 | 8.6143
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 10.5824 | 11.7182
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 0.72049 | 0.81022
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 3.3604 | 3.4933
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 86.8102 | 87.1209
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.9608 | 76.7955
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 81.5877 | 81.7421
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 5532.6909 | 6654.5986
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 5518.8594 | 6637.9624
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 13.8317 | 16.6365
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 71.35 | 74.0925
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 1.806 | 1.8753
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 530.7554 | 531.8716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 498.2152 | 498.1691
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 1.806 | 1.8753
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 498.2152 | 498.1691
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.9298 | 497.8487
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 71.35 | 74.0925
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 1.806 | 1.8753
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 530.7554 | 531.8716
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 498.2152 | 498.1691
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 1.806 | 1.8753
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 498.2152 | 498.1691
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.9298 | 497.8487
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.23352 | 0.23354
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3484.0369 | 3483.8638
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.061311 | 0.061299
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.18144 | 0.18144
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.1134 | 0.1134
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 93.442 | 95.5858
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 84.5987 | 87.9406
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 159.5346 | 182.4304
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 176.2112 | 198.2903
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 37.8785 | 42.6246
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 149072.3281 | 174377.6719
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 72.6343 | 75.4262
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 531.3125 | 532.4471
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 210.3333 | 246.19
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3484.0369 | 3483.8638
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 97.683 | 101.4274
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 220.1776 | 220.5052
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 201.0013 | 235.1203
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 946.6247 | 948.2319
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 126.1789 | 84.9468
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 266.7265 | 287.6678
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 2.4806 | 2.7474
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 82.1807 | 46.9395
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 6.9277 | 26.414
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.61743 | 0.49504
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 110.7232 | 64.67
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.9224
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 88.1147 | 84.3808
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.84084 | 0.94699
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 66.0719
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 3.541
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 15.6285
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79472
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 4.197
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 38.4551
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 56.7375 | 60.7894
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 47.801
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 13.1139 | 13.9575
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2098
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 59.0533 | 63.2706
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 14.3538 | 15.2773
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 46.7577
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 59.0533 | 63.2706
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 33.3628
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 13.0025 | 13.8389
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.27
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 264.9479 | 225.5053
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 266.7265 | 287.6678
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 2.4806 | 2.7474
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 216.205 | 175.9053
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0.59943
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.94953 | 0.8569
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 267.0956 | 219.9818
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 117.2363 | 116.0184
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.63198 | 0.68875
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 66.0719
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 3.541
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 4.197
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99234
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 709.7034 | 692.3336
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 266.7265 | 287.6678
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 2.4806 | 2.7474
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 743.4164 | 721.6534
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6787 | 1.6433
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 809.689 | 780.4434
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 213.0601 | 223.5033
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34775 | 0.35752
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 4.197
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 527.1766 | 486.718
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 266.7265 | 287.6678
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 2.4806 | 2.7474
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 516.4397 | 467.3568
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4205 | 1.3469
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 579.4244 | 525.0508
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.9224
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 173.9293 | 176.3476
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42598 | 0.45313
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 66.0719
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 3.541
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 15.6285
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79472
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 4.197
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 220.5055
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 118.1066 | 126.5413
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.1471
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.67883
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 201.8098
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.053411 | 0.057173
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 40.6496 | 43.3516
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.81082
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 92378.9219 | 99029.2969
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 45.7577
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 118.1066 | 126.5413
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 34.9587
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.053411 | 0.057173
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 26.0343 | 27.7084
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2686
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 92378.9219 | 99029.2969
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 857.0001 | 857.0001
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 266.7265 | 287.6678
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 2.4806 | 2.7474
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 926.2608 | 926.2608
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.8605 | 1.8461
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1002.186 | 993.3666
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 244.3768 | 260.9671
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.30318 | 0.3062
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 4.197
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 212.4553
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 113.475 | 121.5789
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.15941
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.6837
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 193.3921
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.051316 | 0.054931
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 41.4292 | 44.2075
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76394
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 88756.2188 | 95145.8047
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 37.4551
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 113.475 | 121.5789
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 50.229
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.051316 | 0.054931
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 26.2638 | 27.9527
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2082
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 88756.2188 | 95145.8047
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.96679
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 124.9789 | 83.7468
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 266.7265 | 287.6678
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0050378 | 0.0052712
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 81.1229 | 45.9488
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 7.1278 | 27.4621
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.61652 | 0.4938
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 109.3952 | 63.3672
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.9224
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 88.586 | 84.8028
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.83637 | 0.94228
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 66.0719
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 3.541
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 15.6285
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79472
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 4.197
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 123.7789 | 82.5469
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 266.7265 | 287.6678
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0050378 | 0.0052712
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 80.0668 | 44.9602
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 7.3589 | 28.6531
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.61468 | 0.49163
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 108.0676 | 62.0648
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 88.7768 | 84.9557
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.83457 | 0.94058
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 66.0719
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 3.541
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 4.197
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 130.4938 | 88.6214
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 266.7265 | 287.6678
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0050378 | 0.0052712
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 86.0002 | 49.9855
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 6.3151 | 23.7875
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.61837 | 0.49528
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 115.5015 | 68.6615
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.9224
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 54.3115 | 61.1096
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 85.7673 | 82.0887
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.86386 | 0.97343
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 66.0719
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 3.541
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 15.6285
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79472
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 4.197
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 208770.2188 | 222943.0469
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 59.0533 | 63.2706
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 14.3538 | 15.2773
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 46.7577
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 59.0533 | 63.2706
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 33.3628
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 13.0025 | 13.8389
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.27
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 38.4551
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 56.7375 | 60.7894
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 47.801
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 13.1139 | 13.9575
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2098
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 56.7375 | 60.7894
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 13.7909 | 14.6782
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 56.7375 | 60.7894
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 13.7909 | 14.6782
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 56.7375 | 60.7894
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 13.1319 | 13.9764
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 56.7375 | 60.7894
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.025658 | 0.027465
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 13.1319 | 13.9764
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 44378.1094 | 47572.9023
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 59.0533 | 63.2706
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 13.0172 | 13.8542
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 59.0533 | 63.2706
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.026705 | 0.028587
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 13.0172 | 13.8542
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 46189.4609 | 49514.6484
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 5.2158 | 5.4168
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 253.7416 | 253.4088
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.6261 | 1.3525
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.2668 | 7.2471
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2968.1777 | 2966.8049
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 420.6892 | 419.3163
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.1038 | 1.1025
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.1838 | 2.2711
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.09 | 2.0955
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039246 | 0.039244
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8314e-05 | 1.8296e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 5.268 | 5.471
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.9248 | 226.6089
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.4635 | 1.2172
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.1526 | 7.1325
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2911.8601 | 2910.3538
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 364.3715 | 362.8653
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0768 | 1.0755
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.3347 | 2.4286
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1223 | 2.1301
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.036703 | 0.036715
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7174e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 79.3894 | 82.4325
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0049 | 436.0047
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 210.3333 | 246.19
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.5114 | 6.4887
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3237.772 | 3232.8083
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 690.2834 | 685.3198
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.3309 | 1.335
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 26.688 | 27.8274
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.593 | 2.6201
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.066689 | 0.067077
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.6025e-05 | 2.6036e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 27.3223
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 3993.5029 | 4656.9551
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13493
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 996.4656
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 89.6174 | 93.0526
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0164 | 296.1514
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 201.0013 | 235.1203
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2834 | 3.2134
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1361.6749 | 1322.1022
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1185.8135 | -1225.3864
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.00017478 | -0.040627
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 705.8901 | 722.4213
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.0755 | 5.6006
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.53992 | 0.5546
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.4711e-05 | 8.7727e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 3993.5029 | 4656.9551
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 3993.5029 | 4656.9551
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 97.683 | 101.4274
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 220.1776 | 220.5052
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 201.0013 | 235.1203
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.5059 | 2.5083
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 946.6248 | 948.232
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1600.8638 | -1599.2565
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.33876 | -0.35588
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 846.463 | 846.3622
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5583 | 4.5577
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65592 | 0.65601
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.00012274 | 0.00012264
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 210.8345 | 246.7764
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.030277 | 0.030277
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 58.3322 | 58.3322
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 72.6343 | 75.4262
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 531.3125 | 532.4471
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 210.3333 | 246.19
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.8758 | 6.8591
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.4804 | 1.4887
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 20.5638 | 21.3609
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.3853 | 2.3951
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.076292 | 0.076667
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.009e-05 | 3.0151e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 99.4872 | 103.269
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 156.931 | 157.0672
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 201.0013 | 235.1203
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 667.8068 | 668.6221
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1879.6818 | -1878.8663
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.55865 | -0.58056
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.8741 | 915.959
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 1.806 | 1.8753
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 129.6388 | 129.1544
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 0.59128 | 0.72133
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.2286 | 7.2073
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2728.4001 | 2726.7024
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 180.9117 | 179.2139
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0121 | 1.0106
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 0.99065 | 1.0308
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.0795 | 2.0877
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027512 | 0.02752
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3335e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 22.93 | 23.8111
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 388.5145 | 388.7784
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 209.7123 | 245.5579
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 7.0222 | 7.0039
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3217.8464 | 3216.894
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 670.3578 | 669.4056
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.2242 | 1.2244
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 7.7635 | 8.069
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2141 | 2.2211
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.05537 | 0.055487
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3926e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 22.93 | 23.8111
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 388.5145 | 388.7784
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 200.5742 | 234.7195
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 7.0222 | 7.0039
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3217.8464 | 3216.894
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 670.3578 | 669.4056
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.2242 | 1.2244
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 7.7635 | 8.069
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2141 | 2.2211
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.05537 | 0.055487
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3926e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 22.93 | 23.8111
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 388.5145 | 388.7784
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 9.138 | 10.8384
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 7.0222 | 7.0039
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3217.8464 | 3216.894
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 670.3578 | 669.4056
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.2242 | 1.2244
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 7.7635 | 8.069
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2141 | 2.2211
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.05537 | 0.055487
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3917e-05 | 2.3926e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 15.31 | 15.8973
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 341.5981 | 341.6429
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 200.5742 | 234.7195
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.0637 | 7.045
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3129.0718 | 3127.9055
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 581.5831 | 580.4171
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1737 | 1.1732
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 5.5574 | 5.777
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1788 | 2.1857
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.049494 | 0.049565
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1938e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 15.31 | 15.8973
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 341.5981 | 341.6429
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 14.2686 | 16.6312
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 7.0637 | 7.045
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3129.0718 | 3127.9055
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 581.5831 | 580.4171
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1737 | 1.1732
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 5.5574 | 5.777
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.1788 | 2.1857
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.049494 | 0.049565
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1938e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 15.31 | 15.8973
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 341.5981 | 341.6429
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 186.3056 | 218.0883
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 7.0637 | 7.045
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3129.0718 | 3127.9055
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 581.5831 | 580.4171
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1737 | 1.1732
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 5.5574 | 5.777
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.1788 | 2.1857
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.049494 | 0.049565
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.1939e-05 | 2.1938e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 27.3223
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 3993.5029 | 4656.9551
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13493
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 996.4656
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 5.2158 | 5.4168
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 226.3482 | 226.0295
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.4635 | 1.2172
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.1551 | 7.135
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2910.8601 | 2909.354
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 363.3716 | 361.8654
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0765 | 1.0752
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.3139 | 2.407
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1213 | 2.1291
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.03664 | 0.036651
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7168e-05 | 1.7151e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 5.268 | 5.471
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.9248 | 226.6089
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 184.8421 | 216.8711
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.1526 | 7.1325
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2911.8601 | 2910.3538
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 364.3715 | 362.8653
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0768 | 1.0755
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.3347 | 2.4286
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1223 | 2.1301
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.036703 | 0.036715
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7174e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 105.4173 | 123.3882
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.030277 | 0.030277
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 58.3322 | 58.3322
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 5.2158 | 5.4168
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 499.93 | 499.9502
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.16261 | 0.13525
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 8.0692 | 8.0516
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.3491 | 1.3489
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.4677 | 1.5245
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1462 | 2.1469
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067232 | 0.067248
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8584e-05 | 2.8585e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.0882 | 1.1301
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 74.5113 | 75.4155
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 25.1272 | 29.724
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.0097 | 1.0206
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 311.9835 | 315.7776
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2235.5051 | -2231.7109
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.051307 | -0.051703
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 975.1884 | 974.6499
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1923 | 4.1928
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66367 | 0.66434
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00038054 | 0.00037609
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.4977 | 6.4977
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 68.9117 | 69.816
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 185.8018 | 217.9542
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.94132 | 0.95238
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 288.9659 | 292.7531
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2258.5227 | -2254.7356
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.19041 | -0.18859
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 978.6756 | 978.1625
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1877 | 4.1882
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.65956 | 0.6603
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00041037 | 0.00040531
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.030277 | 0.030277
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 58.3322 | 58.3322
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 15.0098 | 15.0098
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 163.4898 | 163.626
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 23.4067 | 27.4697
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9765 | 1.9779
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 691.1367 | 691.7285
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1856.3519 | -1855.76
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.078986 | -0.078681
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 904.5494 | 904.4131
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3461 | 4.3465
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68196 | 0.68192
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016593 | 0.00016578
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 4.556 | 4.7308
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 212.7618 | 212.3932
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 184.8421 | 216.8711
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.1639 | 7.1437
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2885.1326 | 2883.5564
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 337.6441 | 336.0678
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0666 | 1.0652
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.0766 | 2.16
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1165 | 2.1245
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035269 | 0.035275
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6598e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 4.556 | 4.7308
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 212.7618 | 212.3932
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 11.0019 | 13.0234
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.1639 | 7.1437
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2885.1326 | 2883.5564
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 337.6441 | 336.0678
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0666 | 1.0652
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.0766 | 2.16
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1165 | 2.1245
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035269 | 0.035275
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6598e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 4.556 | 4.7308
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 212.7618 | 212.3932
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 173.8402 | 203.8476
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.1639 | 7.1437
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2885.1326 | 2883.5564
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 337.6441 | 336.0678
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0666 | 1.0652
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.0766 | 2.16
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1165 | 2.1245
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035269 | 0.035275
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6618e-05 | 1.6598e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 1.806 | 1.8753
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 129.6388 | 129.1544
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 173.8402 | 203.8476
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.2286 | 7.2073
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2728.4001 | 2726.7024
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 180.9117 | 179.2139
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0121 | 1.0106
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 0.99065 | 1.0308
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.0795 | 2.0877
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027512 | 0.02752
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3335e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 1.806 | 1.8753
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 129.6388 | 129.1544
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 4.6561 | 5.5111
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.2286 | 7.2073
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2728.4001 | 2726.7024
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 180.9117 | 179.2139
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0121 | 1.0106
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 0.99065 | 1.0308
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.0795 | 2.0877
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027512 | 0.02752
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3335e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.7706 | 1.8385
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 105.5917 | 106.6673
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 15.658 | 18.5345
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.3697 | 1.3817
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 442.7386 | 447.2858
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2104.75 | -2100.2029
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.020688 | -0.020904
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 954.3304 | 953.5297
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2223 | 4.2237
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68046 | 0.68082
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00026639 | 0.00026353
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.084 | 6.084
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 99.9881 | 101.0633
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 185.8018 | 217.9542
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3065 | 1.3186
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 419.4251 | 423.9567
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2128.0635 | -2123.5317
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.12162 | -0.11945
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 958.6367 | 957.8609
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2142 | 4.2155
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.67859 | 0.67902
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00028234 | 0.00027918
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.2567 | 5.2567
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 147.4578 | 148.8152
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 185.8018 | 217.9542
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8159 | 1.8298
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 621.2406 | 627.0828
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1926.2479 | -1920.4058
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.012914 | -0.010135
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 919.4474 | 918.1813
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3028 | 4.3064
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68481 | 0.68462
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018544 | 0.00018359
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 105.4173 | 123.3882
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.030277 | 0.030277
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 58.3322 | 58.3322
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.4265 | 45.428
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 185.8018 | 217.9542
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64421 | 0.64423
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.1984 | 190.2046
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.2903 | -2357.2839
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061047 | -0.061044
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0576 | 990.057
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63579 | 0.63579
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059097 | 0.00059095
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3251 | 7.3251
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5034 | 45.5049
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 185.8018 | 217.9542
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64492 | 0.64494
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1232 | 191.1295
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3652 | -2356.3591
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.2496 | -0.2496
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3243 | 990.3237
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63623 | 0.63624
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059026 | 0.00059024
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 4.4667 | 4.638
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 212.0916 | 211.7163
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 11.0019 | 13.0234
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.1708 | 7.1506
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2884.1326 | 2882.5564
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 336.6441 | 335.0678
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0665 | 1.0651
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.0381 | 2.1199
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1138 | 2.1217
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.035189 | 0.035194
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6592e-05 | 1.6572e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 4.4667 | 4.638
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 120.0192 | 121.1883
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 11.0019 | 13.0234
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5278 | 1.5404
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 503.9983 | 508.9728
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2043.4902 | -2038.5157
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.055655 | -0.056255
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 943.2499 | 942.3099
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2437 | 4.2457
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68431 | 0.68451
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00023217 | 0.00022975
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.6704 | 5.6704
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 114.4093 | 115.5778
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 185.8018 | 217.9542
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.4667 | 1.4795
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 480.3049 | 485.2538
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2067.1836 | -2062.2349
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.086331 | -0.083966
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 947.777 | 946.858
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.2342 | 4.236
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68323 | 0.6835
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00024454 | 0.00024187
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 22.4804 | 22.4804
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 205.5711 | 205.5723
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 9.138 | 10.8384
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.3824 | 2.3824
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 877.7553 | 877.7607
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1669.7333 | -1669.7278
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.031313 | -0.03131
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 858.5145 | 858.5131
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5225 | 4.5225
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.66051 | 0.66051
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012995 | 0.00012995
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 1.806 | 1.8753
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 129.6388 | 129.1544
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 168.5928 | 197.6152
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.2286 | 7.2073
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2728.4001 | 2726.7024
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 180.9117 | 179.2139
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0121 | 1.0106
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 0.99065 | 1.0308
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.0795 | 2.0877
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027512 | 0.02752
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3358e-05 | 1.3335e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 89.6174 | 93.0526
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 303.0413 | 305.7496
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 200.5 | 234.534
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.6815 | 5.6595
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2743.5149 | 2737.7437
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 196.0263 | 190.2551
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 48.552 | 50.7901
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 6.0727 | 6.2808
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.073613 | 0.075345
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 1.9902e-05 | 2.0047e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.11 | 1.1527
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 102.5497 | 103.6282
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 168.5928 | 197.6152
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.2626 | 7.2403
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2656.6035 | 2654.5881
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 109.1149 | 107.0997
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.98979 | 0.98813
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.65757 | 0.68235
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2185 | 4.2199
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025078 | 0.02519
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2405e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.11 | 1.1527
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 102.5497 | 103.6282
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 9.4692 | 11.1895
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.2626 | 7.2403
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2656.6035 | 2654.5881
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 109.1149 | 107.0997
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.98979 | 0.98813
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.65757 | 0.68235
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2185 | 4.2199
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025078 | 0.02519
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2405e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.11 | 1.1527
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 102.5497 | 103.6282
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 159.1236 | 186.4257
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.2626 | 7.2403
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2656.6035 | 2654.5881
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 109.1149 | 107.0997
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.98979 | 0.98813
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.65757 | 0.68235
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2185 | 4.2199
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025078 | 0.02519
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2368e-05 | 1.2405e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.331 | 0.34409
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 71.3726 | 72.2801
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 159.1236 | 186.4257
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.344 | 7.3207
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2494.166 | 2491.8867
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -53.3225 | -55.6017
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.94236 | 0.94066
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.22256 | 0.23121
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1904 | 4.191
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022102 | 0.022183
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1341e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.331 | 0.34409
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 71.3726 | 72.2801
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 6.5698 | 8.0148
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.4052 | 7.3818
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2515.2473 | 2513.0203
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -32.2414 | -34.4683
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.95141 | 0.94974
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.22044 | 0.229
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1904 | 4.191
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022102 | 0.022183
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1341e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.331 | 0.34409
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 71.3726 | 72.2801
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 153.1451 | 179.1322
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.344 | 7.3207
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2494.166 | 2491.8867
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -53.3225 | -55.6017
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.94236 | 0.94066
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.22256 | 0.23121
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1904 | 4.191
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022102 | 0.022183
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1341e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 185.2484 | 217.3158
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 99.0735 | 102.8553
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 198.527 | 198.5271
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 201.0013 | 235.1203
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.304 | 2.3034
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 849.2836 | 849.45
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1698.2048 | -1698.0385
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.41908 | -0.43897
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 872.5988 | 872.8696
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4436 | 4.4417
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.67205 | 0.67237
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013675 | 0.00013684
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 37.3932
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 7987.0059 | 9313.9102
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.5374
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 156.8152
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2390.6733
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.18051
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 993.3081
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1777
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62587
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006854
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 27.3761
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 7987.0059 | 9313.9102
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 114.9643
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5242
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20878
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 996.5438
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 22.4804 | 23.3442
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 387.712 | 387.9643
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 9.138 | 10.8384
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 7.0295 | 7.0113
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3216.8464 | 3215.8943
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 669.3579 | 668.4056
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.2233 | 1.2235
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 7.6165 | 7.9162
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.211 | 2.2179
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055236 | 0.05535
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3883e-05 | 2.3892e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 15.0098 | 15.5856
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 340.8437 | 340.8785
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 14.2686 | 16.6312
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 7.071 | 7.0522
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3128.0718 | 3126.9058
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 580.5831 | 579.4171
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1732 | 1.1726
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 5.4527 | 5.6681
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.1759 | 2.1827
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.04938 | 0.049448
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1909e-05 | 2.1907e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 1.7706 | 1.8385
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 128.9974 | 128.5079
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 4.6561 | 5.5111
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.2351 | 7.2138
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2727.4004 | 2725.7024
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 179.9118 | 178.2139
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0121 | 1.0106
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 0.97253 | 1.012
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.0769 | 2.085
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027444 | 0.027451
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3335e-05 | 1.3312e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.0882 | 1.1301
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 101.987 | 103.0618
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 9.4692 | 11.1895
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.2689 | 7.2465
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2655.6035 | 2653.5884
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 108.115 | 106.0997
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98974 | 0.98808
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.64553 | 0.66986
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2178 | 4.2191
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.025019 | 0.025131
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2348e-05 | 1.2385e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.32451 | 0.33734
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 70.9113 | 71.8159
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 6.5698 | 8.0148
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.4109 | 7.3875
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2514.2473 | 2512.0203
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -33.2413 | -35.4683
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.95134 | 0.94968
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.2164 | 0.2248
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1902 | 4.1907
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022062 | 0.022142
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1296e-05 | 1.1326e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 497.3904 | 497.3091
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.22489 | 0.26328
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6341 | 9.6339
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3722 | 1.3721
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049218 | 0.049223
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1278 | 2.1278
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066575 | 0.066565
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8475e-05 | 2.8472e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 99.4872 | 103.269
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 156.931 | 157.0672
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 105.4173 | 123.3882
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 667.8069 | 668.6221
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1879.6816 | -1878.8663
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.55865 | -0.58056
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.874 | 915.959
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 71.35 | 74.0925
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 530.7554 | 531.8716
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 209.9458 | 245.7915
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.8837 | 6.8669
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.4766 | 1.4847
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 20.1983 | 20.9812
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.3808 | 2.3904
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.076115 | 0.076484
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.0061e-05 | 3.0121e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 99.4872 | 103.269
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 156.931 | 157.0672
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 9.8333 | 11.656
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 667.8068 | 668.6221
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1879.6818 | -1878.8663
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.55865 | -0.58056
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.8741 | 915.959
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9114 | 6.9114
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4516 | 46.4512
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 185.8018 | 217.9542
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65735 | 0.65734
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0504 | 195.0487
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.4382 | -2352.4399
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24179 | -0.24179
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9033 | 989.9035
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63733 | 0.63733
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058056 | 0.00058056
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 5.268 | 5.471
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.9248 | 226.6089
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 186.3056 | 218.0883
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.1526 | 7.1325
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2911.8601 | 2910.3538
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 364.3715 | 362.8653
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0768 | 1.0755
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.3347 | 2.4286
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1223 | 2.1301
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.036703 | 0.036715
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7191e-05 | 1.7174e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.0996 | 52.0988
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 31.9219 | 38.0021
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73086 | 0.73085
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.0808 | 218.0772
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.4077 | -2329.4114
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090351 | -0.0090366
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.0851 | 987.0854
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.6433 | 0.6433
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00052778 | 0.00052778
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.32451 | 0.33734
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.0603 | 52.0599
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 31.697 | 37.7388
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73035 | 0.73034
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9292 | 217.9287
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5593 | -2329.5598
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.033854 | -0.035514
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1099 | 987.1107
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64327 | 0.64327
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052812 | 0.00052812
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 153.3265 | 179.3137
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.4677 | 7.4488
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2364.5938 | 2358.5713
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -182.8949 | -188.9172
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.90857 | 0.90605
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.073966 | 0.074171
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.331 | 0.34409
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 71.3726 | 72.2801
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 5.9785 | 7.2934
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.344 | 7.3207
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2494.166 | 2491.8867
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -53.3225 | -55.6017
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.94236 | 0.94066
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.22256 | 0.23121
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1904 | 4.191
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022102 | 0.022183
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.1311e-05 | 1.1341e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.22489 | 0.26328
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 99.4872 | 103.269
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 156.931 | 157.0672
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 105.4173 | 123.3882
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 667.8069 | 668.6221
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1879.6816 | -1878.8663
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.55865 | -0.58056
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.874 | 915.959
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 99.4872 | 103.269
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 156.931 | 157.0672
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 4.9558 | 5.8667
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 667.8068 | 668.6221
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1879.6818 | -1878.8663
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.55865 | -0.58056
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.8741 | 915.959
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 99.4872 | 103.269
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 156.931 | 157.0672
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 105.4173 | 123.3882
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 667.8069 | 668.6221
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1879.6816 | -1878.8663
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.55865 | -0.58056
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.874 | 915.959
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 99.4872 | 103.269
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 156.931 | 157.0672
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 210.8345 | 246.7764
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 667.8068 | 668.6221
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1879.6818 | -1878.8663
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.55865 | -0.58056
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.8741 | 915.959
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 99.4872 | 103.269
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 156.931 | 157.0672
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 105.4173 | 123.3882
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 667.8069 | 668.6221
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1879.6816 | -1878.8663
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.55865 | -0.58056
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.874 | 915.959
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 99.4872 | 103.269
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.1051 | 152.0499
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8528 | 1.8518
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.57433 | -0.59715
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 920.3876 | 920.6475
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.2859 | 4.2846
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.69035 | 0.69061
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018164 | 0.0001818
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 99.4872 | 103.269
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.1051 | 152.0499
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8528 | 1.8518
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.57433 | -0.59715
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 920.3876 | 920.6475
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.2859 | 4.2846
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.69035 | 0.69061
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018164 | 0.0001818
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 79.3894 | 82.4325
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0035 | 460.0035
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 205.3774 | 240.3233
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.5974 | 6.5755
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3299.7864 | 3295.4045
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 752.2979 | 747.9158
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.3738 | 1.3789
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 25.4746 | 26.5445
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.516 | 2.5373
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.06903 | 0.069375
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7075e-05 | 2.7088e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 105.4173 | 123.3882
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.030277 | 0.030277
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 58.3322 | 58.3322
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 105.4173 | 123.3882
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.030277 | 0.030277
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 58.3322 | 58.3322
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8801 | 1.8801
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 647.1016 | 647.1016
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1900.387 | -1900.387
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.030277 | 0.030277
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 58.3322 | 58.3322
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 27.3223
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 7987.0059 | 9313.9102
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13493
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 996.4656
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 71.35 | 74.0925
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 530.7554 | 531.8716
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 210.3333 | 246.19
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.8837 | 6.8669
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.4766 | 1.4847
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 20.1983 | 20.9812
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.3808 | 2.3904
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.076115 | 0.076484
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.0061e-05 | 3.0121e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 98.6599 | 102.4417
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 222.1428 | 222.4704
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 201.0013 | 235.1203
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5239 | 2.5262
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 955.6248 | 957.2319
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1591.8638 | -1590.2566
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.33672 | -0.35401
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 844.043 | 843.9461
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5698 | 4.5691
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65433 | 0.65441
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00012164 | 0.00012155
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 80.9772 | 84.0812
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5055 | 411.5053
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 205.3774 | 240.3233
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.4049 | 6.3809
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3169.3186 | 3163.4492
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 621.8301 | 615.9607
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.2871 | 1.2903
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 28.7492 | 30.0073
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.7285 | 2.7655
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.064792 | 0.065258
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.4944e-05 | 2.4954e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 99.4872 | 103.269
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 156.931 | 157.0672
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 4.8774 | 5.7893
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.9012 | 1.9022
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 667.8068 | 668.6221
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1879.6818 | -1878.8663
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.55865 | -0.58056
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.8741 | 915.959
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2983 | 4.2975
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.68947 | 0.6897
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017561 | 0.00017554
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 87.8602 | 91.2281
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 339.0002 | 338.9989
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 200.5 | 234.534
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.9919 | 5.9583
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2923.342 | 2911.1914
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 375.8534 | 363.7029
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1271 | 1.1242
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 39.1054 | 41.1331
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 3.8917 | 4.0396
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.064882 | 0.066174
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1633e-05 | 2.164e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 89.6174 | 93.0526
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0413 | 305.7379
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 200.5 | 234.534
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.6815 | 5.6594
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2743.5149 | 2737.7437
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 196.0263 | 190.2551
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 48.552 | 50.7802
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.0727 | 6.2823
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.073613 | 0.075338
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 1.9902e-05 | 2.0046e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 80.9772 | 84.0812
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.105 | 434.1047
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 200.5 | 234.534
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.4924 | 6.4694
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3230.1714 | 3225.0325
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 682.6827 | 677.5438
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3295 | 1.3338
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 27.3874 | 28.5616
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.6149 | 2.6435
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.066716 | 0.067121
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.5947e-05 | 2.5959e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 72.8343 | 75.6262
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 531.3991 | 532.5332
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 210.3333 | 246.19
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.8746 | 6.8579
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3484.0369 | 3483.8638
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 936.5485 | 936.3751
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.481 | 1.4893
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 20.6207 | 21.4179
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.386 | 2.3958
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.076319 | 0.076695
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0095e-05 | 3.0156e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 97.683 | 101.4274
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 220.1776 | 220.5052
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 201.0013 | 235.1203
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.5059 | 2.5083
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 946.6248 | 948.232
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1600.8638 | -1599.2565
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.33876 | -0.35588
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 846.463 | 846.3622
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5583 | 4.5577
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65592 | 0.65601
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00012274 | 0.00012264
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 37.8785 | 42.6237
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15424.9053
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15407.5234
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 7.5583
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 159534.5781 | 182426.4219
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 176211.1719 | 198285.9219
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 30
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 20.46
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [24] - LPH-4 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Remark: 6 - Water exit temperature has been reduced by minimum DT allowed. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [24] - LPH-4 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Remark: 5 - PA side heat transfer limited by minimum temperature difference. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,5

## ELINK (2)
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_75%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7 | #N/A | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342 | #N/A | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 302.6 | 234.534 | 234.534 | 234.534
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20 | #N/A | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 877.2 | 863.7255 | 863.7255 | 863.7255
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25 | 25 | 25
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2 | #N/A | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907 | #N/A | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51 | #N/A | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396 | #N/A | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72 | #N/A | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3 | #N/A | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460 | #N/A | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339 | #N/A | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6 | #N/A | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.27 | 5.27 | #N/A | 5.27
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.8281 | 153.8281 | #N/A | 153.8281
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161 | #N/A | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904 | #N/A | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436 | #N/A | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5 | #N/A | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2 | #N/A | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303 | #N/A | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.7867 | 99.7867 | #N/A | 99.7867
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.48096 | 0.48096 | #N/A | 0.48096
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2 | #N/A | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503 | #N/A | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 8.8073 | 8.8073 | #N/A | 8.8073
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 4.1063e-06 | 4.1063e-06 | #N/A | 4.1063e-06
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 140.5461 | 140.5461 | #N/A | 140.5461
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 77.3859 | 77.3859 | #N/A | 77.3859
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 2.0986 | 2.0986 | #N/A | 2.0986
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 20.8544 | 20.8544 | #N/A | 20.8544
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 4.3295 | 4.3295 | #N/A | 4.3295
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 21.7056 | 21.7056 | #N/A | 21.7056
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 4.3295 | 4.3295 | #N/A | 4.3295
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 21.7056 | 21.7056 | #N/A | 21.7056
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 2.0986 | 2.0986 | #N/A | 2.0986
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 20.8544 | 20.8544 | #N/A | 20.8544
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85 | #N/A | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110 | #N/A | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125 | #N/A | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150 | #N/A | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 203.7692 | 203.7692 | #N/A | 203.7692
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19 | #N/A | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536 | #N/A | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 228.1 | 228.1 | #N/A | 228.1
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1 | #N/A | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041 | #N/A | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778 | #N/A | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124 | #N/A | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33 | #N/A | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79 | #N/A | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392 | #N/A | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim | #N/A | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61 | #N/A | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35 | #N/A | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78 | #N/A | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55 | #N/A | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25 | #N/A | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41 | #N/A | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747 | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42 | #N/A | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75 | #N/A | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15 | #N/A | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9 | #N/A | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09 | #N/A | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91 | #N/A | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5 | #N/A | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8 | #N/A | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9 | #N/A | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0 | #N/A | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904 | #N/A | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306 | #N/A | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03 | #N/A | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92 | #N/A | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08 | #N/A | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989 | #N/A | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011 | #N/A | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954 | #N/A | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046 | #N/A | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873 | #N/A | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027 | #N/A | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942 | #N/A | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058 | #N/A | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393 | #N/A | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607 | #N/A | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 535 | 532.534 | 532.534 | 532.534
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0 | #N/A | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1 | #N/A | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5 | #N/A | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1 | #N/A | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3 | #N/A | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2 | #N/A | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75 | #N/A | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 27.3 | 27.3 | 27.3
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2 | #N/A | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985 | #N/A | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1 | #N/A | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1 | #N/A | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1 | #N/A | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1 | #N/A | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736 | #N/A | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241 | #N/A | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889 | #N/A | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15 | #N/A | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 79.583 | 74.0925 | 74.0925 | 74.0925
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81 | #N/A | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 25.58 | 23.8111 | 23.8111 | 23.8111
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86 | #N/A | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 17.08 | 15.8973 | 15.8973 | 15.8973
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91 | #N/A | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.877 | 5.471 | 5.471 | 5.471
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93 | #N/A | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.082 | 4.7308 | 4.7308 | 4.7308
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 2.014 | 1.8753 | 1.8753 | 1.8753
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.238 | 1.1527 | 1.1527 | 1.1527
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.37 | 0.34409 | 0.34409 | 0.34409
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP | #N/A | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 30
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 70.7778
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6328
~~~4~~-5000~ | Plant Summary: Gross power | kW | 84949.1719 | 89905.2656
~~~7~~-5000~ | Plant Summary: Net power | kW | 76382.5781 | 81261.7344
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 8566.5879 | 8643.5283
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 8141.8418 | 8194.002
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 424.7458 | 449.5263
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 35.2128 | 36.3738
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10223.5615 | 9897.2305
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.6618 | 32.8768
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11370.1719 | 10949.9648
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 241245.2969 | 247170.3125
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.6618 | 32.8768
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.6618 | 32.8768
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.6653 | 30.2472
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12558.7285 | 11901.916
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 266463.3438 | 268658.4375
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 241245.2969 | 247170.3125
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.6618 | 32.8768
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 0.80861 | 0.85125
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.7565 | 0.79906
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 241245.2969 | 247170.3125
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 266463.3438 | 268658.4375
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 2118.3889 | 2170.4167
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 21524160 | 22214586
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 27664248 | 28552904
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 618.6989 | 658.22
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 7034.7129 | 7207.4863
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 6.6254 | 6.9749
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 663.9607 | 669.4303
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 27664.248 | 28552.9043
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 362.1801 | 351.3696
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 337297.7812 | 374289.9688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 8299.2754 | 8565.8711
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 52.4356 | 55.8604
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 150.3115 | 161.6668
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.67928 | 0.6306
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 173040.9219 | 192774.5625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.035451 | 0.034057
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.038 | 5.265
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 21524160 | 22214586
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 21524160 | 22214586
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 4202914.5 | 4339005
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 25727074 | 26553592
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 27664248 | 28552904
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 84949.1719 | 89905.2656
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 776.8948 | 783.1622
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 338.9996 | 291.2141
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 913.4019 | 761.0151
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 219.9757 | 209.8587
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 451.0894 | 430.3209
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 219.9757 | 209.8587
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 451.0894 | 430.3209
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 736.1543 | 775.9045
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 79.0789 | 83.4927
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 1095.5714 | 1177.5482
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 1095.5718 | 1177.5483
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 736.1543 | 775.9045
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 178.3932 | 188.8011
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 849.4917 | 899.0527
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 424.7458 | 449.5263
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 8141.8418 | 8194.002
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 241245.2969 | 247170.3125
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 14.1686 | 14.9158
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 403332.0625 | 397621.6875
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 542398.875 | 544346.5
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 23560.2559 | 24890.4277
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 7491.4194 | 7913.3535
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 16869.459 | 17814.4336
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 2069.4629 | 2186.5027
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 11401.7744 | 12050.8145
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 5108.3857 | 5405.4419
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 10812.9766 | 11449.4111
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 8920.5137 | 9519.5303
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 776.8948 | 783.1622
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 338.9996 | 291.2141
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 913.4019 | 761.0151
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 219.9757 | 209.8587
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 451.0894 | 430.3209
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 219.9757 | 209.8587
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 451.0894 | 430.3209
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 736.1543 | 775.9045
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 79.0789 | 83.4927
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 1095.5714 | 1177.5482
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 1095.5718 | 1177.5483
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 736.1543 | 775.9045
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 242.08 | 255.6992
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 60.52 | 63.9248
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 99.9299 | 101.6485
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 310.948 | 312.2036
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2725.6003 | 2722.4434
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 877.2 | 877.2
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 310.948 | 312.2036
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 66.0719
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 3.541
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.9605
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 15.6285
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0033418
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79472
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 139866.9531 | 149425.9688
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 91818.0156 | 98524.4375
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 22954.5039 | 24631.1094
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 11639.4473 | 12368.6055
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 13454.999 | 13901.8105
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 2111.5203 | 2129.0542
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 2797.3391 | 2988.5193
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 404.327 | 407.3542
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 943.4295 | 950.493
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 96.9402 | 96.4556
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 178.753 | 169.5555
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 139.7315 | 132.6633
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.12888 | 0.12994
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.46904 | 0.47291
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 57.2791 | 57.7542
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 1374.6976 | 1386.0995
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 241245.2969 | 247184.0938
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 266463.3438 | 268673.4062
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 572.7906 | 577.5414
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 204.1042 | 205.6209
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 3.7861 | 3.8176
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.22539 | 0.22726
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.59107 | 0.59594
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 5.1026 | 5.1405
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.5308 | 1.5422
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 3.5718 | 3.5984
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 3.541
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 15.6285
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.27 | 5.27
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.8281 | 153.8281
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.3108 | 5.3108
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 150.0223 | 150.0223
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 632.2855 | 632.2855
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 279.323 | 295.1286
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 5.8188 | 5.9185
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 253.3819 | 253.0765
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2965.3818 | 2964.4006
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.2329 | 1.2978
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 16.7451 | 16.7451
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 164.2944 | 164.3625
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 694.7332 | 695.0291
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 38.2623 | 40.4405
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 318.8181 | 336.8669
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.999 | 23.999
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 88.5249 | 90.0473
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0032 | 460.003
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 310.3009 | 327.8199
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3286.5439 | 3284.3113
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 88.5249 | 90.0473
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0042 | 436.004
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 318.0616 | 336.0678
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3222.7476 | 3220.2075
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 7.7607 | 8.2479
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 671.9551 | 672.3626
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5994 | 22.5993
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 90.2954 | 91.8482
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.104 | 434.1039
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 302.6 | 319.6239
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3214.6116 | 3211.9792
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 90.2954 | 91.8482
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5047 | 411.5046
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 310.3009 | 327.8199
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3151.5093 | 3148.4856
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 7.7009 | 8.1959
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 671.9551 | 672.3626
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 24.3943 | 23.4341
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 149.4225 | 141.194
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 25.3974 | 24.3972
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 25.3974 | 24.3972
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 24.3943 | 23.4341
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 303.3565 | 320.423
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 108.9236 | 110.7968
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 973.8266 | 974.2692
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 226.0548 | 226.1404
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 303.3565 | 320.423
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 99.9299 | 101.6485
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 298.6834
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1360.303 | 1335.405
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 403.3392 | 389.7408
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 3.5718 | 3.5981
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 526.1609 | 484.8946
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 282.9344 | 231.1404
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 54.6383
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1252.0874 | 995.5654
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 32567.1992 | 32143.8945
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 32567.1992 | 32143.8945
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 244.254 | 241.0792
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 8.9937 | 9.1484
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.7867 | 99.8015
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 338.9996 | 291.2141
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 144.8047 | 90.6519
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 502057.2188 | 418137.7812
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 403.339 | 389.7624
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 3.5718 | 3.5981
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 3.5642 | 3.591
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0076183 | 0.0071425
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3723.5483 | 3720.3328
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 11721.3564 | 12594.1826
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9419 | 7.3851
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 25.0002 | 25.0001
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 149.4688 | 141.2328
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.2264 | 1.2041
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 432.9519 | 412.8737
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 432.9519 | 412.8737
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 428.6224 | 408.745
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 21.7056 | 20.6993
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 4.3295 | 4.1287
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 473.6438 | 451.8369
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 95.9992 | 95.9657
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 451.0894 | 430.3209
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 432.9519 | 412.8737
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 95.9792 | 95.9455
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 18.1374 | 17.4472
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 454.5995 | 433.5174
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 880.7316 | 732.9973
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 880.7316 | 732.9973
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 871.9243 | 725.6674
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 140.5461 | 116.9531
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1388 | 80.1299
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 8.8073 | 7.33
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 959.0719 | 799.0657
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.441 | 96.3367
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 913.4019 | 761.015
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 880.7316 | 732.9973
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.4232 | 96.3184
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 32.6702 | 28.0177
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 924.7681 | 769.6472
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 209.8643 | 200.1224
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 209.8643 | 200.1224
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 207.7656 | 198.1212
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 20.8544 | 19.8876
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 2.0986 | 2.0012
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 230.9745 | 220.3516
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.4263 | 95.3836
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 219.9757 | 209.8587
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 209.8643 | 200.1224
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.4034 | 95.3605
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 10.1114 | 9.7363
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 220.3575 | 210.1285
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 432.9519 | 412.8737
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 432.9519 | 412.8737
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 428.6224 | 408.745
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 21.7056 | 20.6993
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 4.3295 | 4.1287
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 473.6438 | 451.8369
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 95.9992 | 95.9657
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 451.0894 | 430.3209
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 432.9519 | 412.8737
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 95.9792 | 95.9455
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 18.1374 | 17.4472
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 454.5995 | 433.5174
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 209.8643 | 200.1224
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 209.8643 | 200.1224
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 207.7656 | 198.1212
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 20.8544 | 19.8876
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 2.0986 | 2.0012
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 230.9745 | 220.3516
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.4263 | 95.3836
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 219.9757 | 209.8587
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 209.8643 | 200.1224
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.4034 | 95.3605
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 10.1114 | 9.7363
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 220.3575 | 210.1285
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.36275 | 0.36858
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 73.5249 | 73.9033
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 8133.1494 | 8723.2637
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 6908.4692 | 7405.0366
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 1224.6805 | 1318.2272
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 25.0644 | 25.4427
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.2137 | 1.2348
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 105.1123 | 105.6105
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 10296.0127 | 10921.0967
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 9051.6143 | 9604.8613
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 1244.3993 | 1316.2356
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 31.5876 | 31.7077
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 1.9745 | 2.0088
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 119.8065 | 120.3503
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 4820.6636 | 5110.1968
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 4514.3022 | 4788.0283
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 306.3611 | 322.1689
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.6921 | 14.7374
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 4.9824 | 5.0676
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 151.7031 | 152.3431
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 10672.3506 | 11087.1211
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 9578.3809 | 9955.1455
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 546.8643 | 560.7134
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 547.1055 | 571.262
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 32.1848 | 31.6407
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 1.7031 | 2.3431
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 16.7451 | 16.7451
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 203.5792 | 203.5792
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 16953.6602 | 17878.1875
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 13003.7227 | 13718.5459
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 2102.4268 | 2210.2793
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 1847.5114 | 1949.3632
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 46.0335 | 45.9655
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 25.0784 | 25.1232
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 224.1231 | 224.218
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 9242.5488 | 9794.9229
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 7414.2236 | 7859.3281
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1584.2157 | 1674.913
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 244.1092 | 260.6817
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 24.2367 | 24.3222
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.8912 | -3.882
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7598 | 15424.9043
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 57.2791 | 57.751
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 241245.2969 | 247170.3125
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 266463.3438 | 268658.4375
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 2118.3889 | 2170.4167
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15407.5234
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15424.9043
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16828.3848
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 20.46
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 30
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 7.5583
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 30.0002
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 89.2993 | 85.7256
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.040383 | 0.038732
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 30.0002
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 85.7974 | 82.3639
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.0388 | 0.037213
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 30.0002
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 89.2993 | 85.7256
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.040383 | 0.038732
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 30.0002
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 85.7974 | 82.3639
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.0388 | 0.037213
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.2982
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 708.8832 | 747.4041
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 687.6167 | 724.9819
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 736.1543 | 775.9045
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 5922.8818 | 6248.1816
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 5922.8818 | 6248.1816
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 761.8742 | 803.0132
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.3084 | 96.3396
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 736.1543 | 775.9045
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 708.8832 | 747.4041
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.2955 | 96.3268
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 27.2711 | 28.5004
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 733.6503 | 773.517
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.2982
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 708.8832 | 747.4041
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 687.6167 | 724.9819
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 736.1543 | 775.9045
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 5922.8818 | 6248.1816
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 5922.8818 | 6248.1816
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 761.8742 | 803.0132
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.3084 | 96.3396
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 736.1543 | 775.9045
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 708.8832 | 747.4041
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.2955 | 96.3268
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 27.2711 | 28.5004
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 733.6503 | 773.517
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.3084 | 96.3396
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 71.2931 | 71.2931
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.9218 | 6.9218
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.9218 | 6.9218
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 74.9993 | 74.9993
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 74.5636 | 78.7828
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 72.3267 | 76.4193
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 79.0789 | 83.4927
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 279.323 | 295.1286
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.429 | 45.4294
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.2088 | 190.2103
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 279.323 | 295.1286
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3792 | 7.3792
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5065 | 45.5068
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.141 | 191.1425
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 81.8418 | 86.4098
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 94.31 | 94.3785
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 79.0789 | 83.4927
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 74.5636 | 78.7828
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 94.2901 | 94.3589
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 4.5153 | 4.7099
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 77.1687 | 81.5354
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1180.5334 | 1201.3307
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 107.3929 | 109.2848
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 107.3929 | 109.2848
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 1056.9429 | 1136.4507
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 1025.2346 | 1102.3572
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 1095.5714 | 1177.5481
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 159.409 | 168.4335
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 159.409 | 168.4335
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 110.8402 | 112.7321
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 142.1197 | 142.1864
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 605.1828 | 605.5906
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 1522.7216 | 1636.66
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.678 | 96.7117
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 1095.5714 | 1177.5481
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 1056.9429 | 1136.4507
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.4741 | 96.5099
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 38.6285 | 41.0974
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 1469.0322 | 1579.5392
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1180.5334 | 1201.3307
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 107.3929 | 109.2848
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 107.3929 | 109.2848
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 50 | 50
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 1056.9431 | 1136.4508
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 1025.2349 | 1102.3573
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 1095.5717 | 1177.5482
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 159.4091 | 168.4335
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 159.4091 | 168.4335
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 110.8402 | 112.7321
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 142.1197 | 142.1864
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 605.1828 | 605.5906
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 1522.7219 | 1636.6602
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.678 | 96.7117
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 1095.5717 | 1177.5482
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 1056.9431 | 1136.4508
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.4741 | 96.5099
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 38.6285 | 41.0974
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 1469.0326 | 1579.5393
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 0.80861 | 0.85125
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 278.5143 | 294.2774
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 279.323 | 295.1286
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.429 | 45.4294
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.2088 | 190.2103
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0068832 | 0.0068761
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99312 | 0.99312
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 9.2275e-10 | 8.7331e-10
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 17659.7168 | 16961.4629
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 8648.8496 | 8306.9717
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 9010.8672 | 8654.4922
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 8605.8203 | 8265.6436
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 8966.0371 | 8611.4346
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 87.8602 | 84.3851
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.058188 | 0.059185
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 0.99999 | 1
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.30821 | 0.32443
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.4325 | 1.4572
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.50157 | 0.51013
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 3.9949 | 4.2357
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.3349 | 0.34058
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 6.6332 | 6.9975
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.099647 | 0.10135
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 4.5174 | 4.6995
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.03949 | 0.040176
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 2.0011 | 2.1261
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.024275 | 0.024696
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 4.05 | 4.304
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0072549 | 0.0073716
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 3.0657 | 3.2915
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 1.0892 | 1.108
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 758.4005 | 801.0674
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 306.62 | 323.8641
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.95408 | 0.9538
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7401 | 10.74
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.048497 | 0.048814
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.9515 | 0.95119
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00038762 | 0.00038616
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99854 | 0.99854
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010696 | 0.0010696
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95468 | 0.95453
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.045318 | 0.045473
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92118 | 0.9213
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.078817 | 0.0787
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99602 | 0.99604
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0039756 | 0.0039606
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.9415 | 0.9424
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.058502 | 0.057598
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96868 | 0.9685
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0037952 | 0.0038527
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.027525 | 0.027651
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94249 | 0.9422
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.05751 | 0.057796
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.95797 | 0.95731
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.042032 | 0.042689
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 9.2275e-10 | 8.7331e-10
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50194 | 0.50158
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49806 | 0.49842
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 149.4019 | 94.4162
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 55.1079
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.0616
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 1971.0919 | 1987.1426
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 3.541
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.9605
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 15.6285
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 66.0719
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79472
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0033418
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.8311
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 100.9782
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 35.3298
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0076183 | 0.0071421
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9419 | 7.3852
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 25.0002 | 24.9988
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 3.541
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 15.6285
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 318.0616 | 336.0678
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 88.5249 | 90.0473
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3222.7476 | 3220.2075
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0042 | 436.004
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 318.0616 | 336.0678
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 81.2155 | 82.6122
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 535 | 535.124
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3484.0393 | 3482.8892
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 403.3392 | 389.7408
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 3.5718 | 3.5981
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 877.2 | 877.2
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 721.3113 | 704.0826
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 23085.5762 | 24522.2734
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 7.3094 | 7.4351
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 302.6 | 319.6239
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 97.9705 | 99.6553
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2885.6704 | 2879.0205
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 338.9995 | 339.0006
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 302.6 | 319.6239
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 90.2954 | 91.8482
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3214.6116 | 3211.9792
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 403.3392 | 389.7408
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 3.5718 | 3.5981
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 721.3112 | 704.0838
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 526.1608 | 484.8638
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 27649.7539 | 29562.0137
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 207.3731 | 221.7151
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 7.6751 | 7.8071
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 108.9236 | 110.7968
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 226.0548 | 226.1404
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 973.8266 | 974.2692
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 303.3565 | 320.423
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 108.9236 | 110.7968
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 226.0548 | 226.1404
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 973.8266 | 974.2692
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.2 | 0.2
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 81.2155 | 82.6122
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 534.9996 | 535.1237
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3484.0393 | 3482.8892
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 318.0616 | 336.0678
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 81.0155 | 82.4122
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 534.9143 | 535.0386
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3484.0393 | 3482.8892
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 110.8402 | 112.7321
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.3365 | 152.3088
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 110.8402 | 112.7321
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.3365 | 152.3088
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 110.8402 | 112.7321
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 157.7357 | 157.8038
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 671.955 | 672.3629
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 159.409 | 168.4335
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 110.8402 | 112.7321
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 157.7357 | 157.8038
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 671.955 | 672.3629
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 110.8402 | 112.7321
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 157.7357 | 157.8038
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 671.955 | 672.3629
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 159.4091 | 168.4335
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 110.8402 | 112.7321
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 157.7357 | 157.8038
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 671.955 | 672.3629
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 159.409 | 168.4335
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 159.4091 | 168.4335
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 37.3932
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 156.815
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 11845.7637 | 12496.3633
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 27.3223
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 114.5466
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 11845.7637 | 12496.3633
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 137691.0469 | 145275.6562
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 84949.1719 | 89905.2656
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.5098 | 98.548
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 133.7949 | 141.6008
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 44.5983 | 47.2003
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 99.1074 | 104.8895
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.5301 | 98.5678
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 83.5621 | 85.0027
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 534.3031 | 534.4175
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 317.5981 | 335.5786
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 89196.625 | 94400.5234
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.5301 | 98.5678
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 84949.1719 | 89905.2656
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 86234.2422 | 91229.9141
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.5098 | 98.548
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1285.0681 | 1324.6475
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 1127.7323 | 1162.4038
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 157.3358 | 162.2437
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 10.1967 | 10.371
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 4.7668 | 4.8448
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 153301.8281 | 159875.4844
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 9.6167 | 9.7503
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.3817 | 3.4093
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 141649.9688 | 147474.0938
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 19.8134 | 20.1213
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 4.7668 | 4.8448
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 294951.8125 | 307349.5938
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 22.2876 | 22.6237
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 5.7201 | 5.8137
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 17720680 | 18284810
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 21524160 | 22214586
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 79.583 | 80.955
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 79.583 | 80.955
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 534.3031 | 534.4175
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 317.5981 | 335.5786
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3484.0393 | 3482.8892
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 317.3646 | 335.345
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 79.583 | 80.955
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3484.0393 | 3482.8892
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 25.58 | 26.0165
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3216.1196 | 3215.0195
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 25.58 | 26.0165
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 389.8145 | 389.666
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 317.3646 | 335.345
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3216.1196 | 3215.0195
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 10.1606 | 10.5464
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.009856 | 0.010234
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1111 | 3.1117
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 73.3373 | 73.3749
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 75.504 | 75.5419
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 75.504 | 75.5419
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 23619.3027 | 24952.8086
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 23560.2559 | 24890.4277
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 59.0482 | 62.382
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 25.58 | 26.0165
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 25.58 | 26.0165
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 389.8145 | 389.666
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 302.9824 | 320.096
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3216.1196 | 3215.0195
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 302.9824 | 320.096
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 25.58 | 26.0165
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3216.1196 | 3215.0195
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 17.08 | 17.3697
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3126.8857 | 3125.7993
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 17.08 | 17.3697
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 342.3405 | 342.1319
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 302.9824 | 320.096
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3126.8857 | 3125.7993
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 13.5446 | 14.0573
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.026752 | 0.027776
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4977 | 1.4978
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 77.9852 | 78.0274
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 78.3809 | 78.4225
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 78.3809 | 78.4225
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 7510.1943 | 7933.1865
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 7491.4194 | 7913.3535
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 18.7755 | 19.8329
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 17.08 | 17.3697
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 17.08 | 17.3697
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 342.3405 | 342.1319
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 279.1023 | 294.9044
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3126.8857 | 3125.7993
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 279.1023 | 294.9044
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 17.08 | 17.3697
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3126.8857 | 3125.7993
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 5.877 | 5.9777
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2908.7532 | 2907.7908
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 5.877 | 5.9777
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.651 | 226.3971
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 279.1023 | 294.9044
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2908.7532 | 2907.7908
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 29.6662 | 30.7861
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.035637 | 0.037008
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9062 | 2.9057
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 82.4998 | 82.547
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 83.8321 | 83.8763
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 83.8321 | 83.8763
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 16911.7402 | 17859.082
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 16869.459 | 17814.4336
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 42.2793 | 44.6477
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 5.877 | 5.9777
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 5.877 | 5.9777
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.651 | 226.3971
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 277.9927 | 293.7365
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2908.7532 | 2907.7908
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 277.9927 | 293.7365
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 5.877 | 5.9777
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2908.7532 | 2907.7908
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 5.082 | 5.169
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2881.887 | 2880.9263
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 5.082 | 5.169
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 212.3696 | 212.1075
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 277.9927 | 293.7365
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2881.887 | 2880.9263
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 33.2176 | 34.4722
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.093305 | 0.096879
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1564 | 1.1565
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 83.6006 | 83.6669
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 83.6009 | 83.6671
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 83.6009 | 83.6671
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 2074.6494 | 2191.9829
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 2069.4629 | 2186.5027
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 5.1866 | 5.48
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 5.082 | 5.169
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 5.082 | 5.169
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 212.3696 | 212.1075
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 261.7295 | 276.8177
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2881.887 | 2880.9263
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 261.7295 | 276.8177
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 5.082 | 5.169
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2881.887 | 2880.9263
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 2.014 | 2.049
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2724.6687 | 2723.8159
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 2.014 | 2.049
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 128.8454 | 128.6105
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 261.7295 | 276.8177
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2724.6687 | 2723.8159
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 65.5072 | 68.0286
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.10016 | 0.1041
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5233 | 2.5227
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.5746 | 85.6285
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 86.4603 | 86.5033
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 86.4603 | 86.5033
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 11430.3506 | 12081.0166
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 11401.7744 | 12050.8145
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 28.5758 | 30.2025
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 2.014 | 2.049
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 2.014 | 2.049
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 128.8454 | 128.6105
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 253.5319 | 268.097
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2724.6687 | 2723.8159
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 253.5319 | 268.097
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 2.014 | 2.049
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2724.6687 | 2723.8159
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.238 | 1.2595
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2651.9521 | 2651.051
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.238 | 1.2595
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 105.6857 | 106.1857
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 253.5319 | 268.097
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2651.9521 | 2651.051
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 96.2876 | 100.1166
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.22306 | 0.23173
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.6268 | 1.6268
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 85.9563 | 86.0151
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 85.9564 | 86.0151
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 85.9564 | 86.0151
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 5121.1885 | 5418.9893
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 5108.3857 | 5405.4419
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 12.803 | 13.5475
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.238 | 1.2595
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.238 | 1.2595
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 105.6857 | 106.1857
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 238.9514 | 252.6021
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2651.9521 | 2651.051
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 238.9514 | 252.6021
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.238 | 1.2595
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2651.9521 | 2651.051
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.37 | 0.37596
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2488.6399 | 2487.4712
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.37 | 0.37596
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 73.9944 | 74.3739
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 238.9514 | 252.6021
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2488.6399 | 2487.4712
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 267.4097 | 278.2499
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.3279 | 0.34065
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.3459 | 3.3501
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 87.6155 | 87.7162
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.6762 | 85.7068
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.6762 | 85.7068
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 10840.0771 | 11478.1064
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 10812.9766 | 11449.4111
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 27.1002 | 28.6952
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.37 | 0.37596
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.37 | 0.37596
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 73.9944 | 74.3739
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 228.9078 | 241.8187
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2488.6399 | 2487.4712
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 228.9078 | 241.8187
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.37 | 0.37596
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2488.6399 | 2487.4712
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2337.9866 | 2335.0486
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 229.0892 | 242.0001
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2348.3352 | 2345.7197
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 849.1328 | 895.7984
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 5.0345 | 5.2176
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 168.6629 | 171.6888
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2274.7305 | 2308.5884
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 704.4923 | 719.4026
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 10.0124 | 10.3508
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 13.7394 | 14.2354
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 0.96222 | 1
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 3.7563 | 3.8168
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 87.5884 | 87.6902
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.5028 | 76.4135
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 81.9491 | 81.9807
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 8942.8711 | 9543.3887
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 8920.5137 | 9519.5303
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 22.3572 | 23.8584
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 79.583 | 80.955
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 2.014 | 2.049
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 534.303 | 534.4175
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 498.3212 | 497.8007
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 2.014 | 2.049
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 498.3212 | 497.8007
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.9309 | 497.3919
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 79.583 | 80.955
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 2.014 | 2.049
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 534.303 | 534.4175
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 498.3212 | 497.8007
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 2.014 | 2.049
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 498.3212 | 497.8007
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.9309 | 497.3919
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.23352 | 0.2336
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3484.0393 | 3482.8892
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.061311 | 0.061232
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.18144 | 0.18144
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.1134 | 0.1134
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 92.5073 | 95.3355
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.7524 | 87.7103
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 241.2453 | 247.1841
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 266.4633 | 268.6734
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 57.2791 | 57.7542
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 223169.4844 | 235654.1406
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 81.0155 | 82.4122
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 534.9143 | 535.0386
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 318.0616 | 336.0678
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3484.0393 | 3482.8892
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 108.9236 | 110.7968
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 226.0548 | 226.1404
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 303.3565 | 320.423
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 973.8266 | 974.2692
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 144.8047 | 90.6519
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 403.339 | 389.7624
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 3.5718 | 3.5981
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 98.8401 | 51.6769
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 4.0338 | 21.2019
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.668 | 0.51222
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 131.3855 | 70.8687
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.9224
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 139.4603 | 116.1494
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.80337 | 0.93214
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 66.0719
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 3.541
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 15.6285
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79472
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 4.197
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 38.4551
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 85.7974 | 82.3639
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 47.801
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 19.8305 | 18.9111
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2098
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 89.2993 | 85.7256
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 21.7056 | 20.6993
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 46.7577
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 89.2993 | 85.7256
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 33.3628
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 19.6621 | 18.7504
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.27
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 282.9344 | 231.1406
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 403.339 | 389.7624
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 3.5718 | 3.5981
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 235.1016 | 181.5634
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0.5402
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.98737 | 0.86956
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 287.7981 | 226.3298
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 183.2084 | 158.9702
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.61154 | 0.68105
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 66.0719
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 3.541
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 4.197
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99234
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 721.3113 | 704.0775
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 403.339 | 389.7624
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 3.5718 | 3.5981
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 757.9541 | 736.3684
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.6939 | 1.6587
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 824.6564 | 795.3997
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 325.9907 | 306.5091
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34369 | 0.35323
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 4.197
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 526.1609 | 484.8639
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 403.339 | 389.7624
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 3.5718 | 3.5981
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 515.1992 | 465.1249
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4189 | 1.3439
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 578.1714 | 522.8068
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.9224
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 262.679 | 238.3511
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42652 | 0.45423
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 66.0719
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 3.541
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 15.6285
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79472
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 4.197
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 220.7578
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 178.5986 | 171.4513
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.14639
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.67936
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 202.0738
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.080767 | 0.077464
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 61.4695 | 58.7672
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.81041
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 139693.7188 | 134175.2188
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 45.7577
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 178.5986 | 171.4513
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 34.9587
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.080767 | 0.077464
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 39.3686 | 37.5423
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2686
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 139693.7188 | 134175.2188
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 877.2 | 877.2
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 403.339 | 389.7624
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 3.5718 | 3.5981
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 950.8564 | 950.8564
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.884 | 1.8694
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1028.9951 | 1019.9326
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 376.1472 | 359.9052
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.29786 | 0.30082
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 4.197
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 212.4552
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 171.5948 | 164.7277
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.15941
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.6837
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 193.392
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.077599 | 0.074426
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 62.6484 | 59.897
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76394
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 134215.5312 | 128913.4375
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 37.4551
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 171.5948 | 164.7277
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 50.229
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.077599 | 0.074426
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 39.7156 | 37.8733
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2082
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 134215.5312 | 128913.4375
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.96679
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 143.6047 | 89.452
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 403.339 | 389.7624
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0076183 | 0.0071421
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 97.7534 | 50.6767
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 4.1353 | 22.0061
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.66722 | 0.51102
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 130.0515 | 69.5642
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.9224
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 140.2252 | 116.7363
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.79899 | 0.92745
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 66.0719
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 3.541
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 15.6285
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79472
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 4.197
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 142.4047 | 88.252
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 403.339 | 389.7624
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0076183 | 0.0071421
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 96.6685 | 49.6785
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 4.2538 | 22.9214
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.66552 | 0.50891
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 128.7178 | 68.2601
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 140.5461 | 116.9531
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.79717 | 0.92573
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 66.0719
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 3.541
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 4.197
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 149.4019 | 94.4162
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 403.339 | 389.7624
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0076183 | 0.0071421
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 103.0201 | 54.8275
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 3.696 | 19.1267
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.66921 | 0.51256
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 136.5 | 74.9625
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.9224
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 82.1289 | 82.7977
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 135.7712 | 113.0039
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.8252 | 0.95809
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 66.0719
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 3.541
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 15.6285
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79472
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 4.197
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 315698.5 | 302066.4375
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 89.2993 | 85.7256
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 21.7056 | 20.6993
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 46.7577
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 89.2993 | 85.7256
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 33.3628
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 19.6621 | 18.7504
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.27
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 38.4551
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 85.7974 | 82.3639
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 47.801
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 19.8305 | 18.9111
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2098
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 85.7974 | 82.3639
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 20.8544 | 19.8876
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 85.7974 | 82.3639
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 20.8544 | 19.8876
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 85.7974 | 82.3639
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 19.8578 | 18.9366
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 85.7974 | 82.3639
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.0388 | 0.037213
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 19.8578 | 18.9366
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 67107.7656 | 64456.7188
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 89.2993 | 85.7256
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 19.6843 | 18.7711
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 89.2993 | 85.7256
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.040383 | 0.038732
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 19.6843 | 18.7711
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 69846.8594 | 67087.6094
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 5.8188 | 5.9185
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 253.3819 | 253.0765
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.2329 | 1.2978
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.212 | 7.2024
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2965.3818 | 2964.4006
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 417.8932 | 416.912
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.1008 | 1.1001
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.4434 | 2.4877
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.1059 | 2.1089
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039303 | 0.039289
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8289e-05 | 1.8274e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 5.877 | 5.9777
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.651 | 226.3971
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.1096 | 1.168
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.0971 | 7.0875
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2908.7532 | 2907.7908
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 361.2646 | 360.3021
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0735 | 1.0728
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.6134 | 2.6609
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1449 | 2.1491
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.036802 | 0.0368
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7154e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 88.5249 | 90.0473
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0042 | 436.004
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 318.0616 | 336.0678
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.4448 | 6.4342
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3222.7476 | 3220.2075
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 675.2592 | 672.7189
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.3439 | 1.3462
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 30.1401 | 30.7248
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.6764 | 2.6908
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.067879 | 0.068085
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.606e-05 | 2.6067e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 27.3223
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 5922.8818 | 6248.1816
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13493
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 996.4656
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 99.9299 | 101.6485
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.0157 | 298.7063
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 303.3565 | 320.423
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2785 | 3.2349
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1360.303 | 1335.5337
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1187.1855 | -1211.9548
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.035857 | -0.060756
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 708.331 | 718.5779
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 5.7974 | 5.6418
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.54237 | 0.55147
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.5145e-05 | 8.7004e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 5922.8818 | 6248.1816
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 5922.8818 | 6248.1816
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 108.9236 | 110.7968
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 226.0548 | 226.1404
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 303.3565 | 320.423
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.558 | 2.5585
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 973.8266 | 974.2692
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1573.662 | -1573.2194
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.37376 | -0.38309
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 839.886 | 839.9382
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5874 | 4.5865
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65187 | 0.65198
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.00011971 | 0.00011971
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 318.8181 | 336.8669
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.031068 | 0.031068
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 56.9378 | 56.9378
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 81.0155 | 82.4122
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 534.9143 | 535.0386
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 318.0616 | 336.0678
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.828 | 6.8191
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.5065 | 1.5103
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 22.9505 | 23.3653
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.4145 | 2.4197
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.077447 | 0.077585
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.0283e-05 | 3.0296e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 110.8402 | 112.7321
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 157.7357 | 157.8038
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 303.3565 | 320.423
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 671.9552 | 672.3626
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1875.5333 | -1875.126
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.62498 | -0.63686
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.7547 | 915.7972
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2969 | 4.2964
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 2.014 | 2.049
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 128.8454 | 128.6105
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 0.99333 | 1.0665
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.17 | 7.1601
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2724.6687 | 2723.8159
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 177.1802 | 176.3273
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0082 | 1.0075
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 1.1098 | 1.1303
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.1032 | 2.1075
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027589 | 0.027597
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3304e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 25.58 | 26.0165
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 389.8145 | 389.666
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 317.3646 | 335.345
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 6.9709 | 6.9617
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3216.1196 | 3215.0195
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 668.6311 | 667.5309
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.2256 | 1.2254
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 8.6763 | 8.8326
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2349 | 2.2386
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.05578 | 0.055808
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3959e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 25.58 | 26.0165
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 389.8145 | 389.666
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 302.9824 | 320.096
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 6.9709 | 6.9617
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3216.1196 | 3215.0195
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 668.6311 | 667.5309
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.2256 | 1.2254
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 8.6763 | 8.8326
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2349 | 2.2386
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.05578 | 0.055808
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3959e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 25.58 | 26.0165
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 389.8145 | 389.666
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 14.3822 | 15.249
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 6.9709 | 6.9617
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3216.1196 | 3215.0195
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 668.6311 | 667.5309
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.2256 | 1.2254
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 8.6763 | 8.8326
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2349 | 2.2386
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.05578 | 0.055808
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3967e-05 | 2.3959e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 17.08 | 17.3697
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 342.3405 | 342.1319
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 302.9824 | 320.096
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 7.0112 | 7.0019
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3126.8857 | 3125.7993
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 579.3972 | 578.3107
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1729 | 1.1724
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 6.2137 | 6.3252
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.1991 | 2.2028
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.049773 | 0.049785
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.195e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 17.08 | 17.3697
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 342.3405 | 342.1319
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 23.8801 | 25.1915
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 7.0112 | 7.0019
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3126.8857 | 3125.7993
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 579.3972 | 578.3107
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1729 | 1.1724
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 6.2137 | 6.3252
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.1991 | 2.2028
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.049773 | 0.049785
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.195e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 17.08 | 17.3697
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 342.3405 | 342.1319
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 279.1023 | 294.9044
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 7.0112 | 7.0019
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3126.8857 | 3125.7993
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 579.3972 | 578.3107
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1729 | 1.1724
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 6.2137 | 6.3252
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.1991 | 2.2028
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.049773 | 0.049785
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.1961e-05 | 2.195e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 27.3223
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 5922.8818 | 6248.1816
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13493
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 996.4656
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 5.8188 | 5.9185
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 226.0666 | 225.8114
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.1096 | 1.168
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.0996 | 7.09
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2907.7532 | 2906.7908
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 360.2646 | 359.3022
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0732 | 1.0725
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.5902 | 2.6373
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1438 | 2.148
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.036737 | 0.036735
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7144e-05 | 1.7131e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 5.877 | 5.9777
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.651 | 226.3971
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 277.9927 | 293.7365
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.0971 | 7.0875
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2908.7532 | 2907.7908
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 361.2646 | 360.3021
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0735 | 1.0728
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.6134 | 2.6609
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1449 | 2.1491
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.036802 | 0.0368
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7154e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 159.4091 | 168.4335
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.031068 | 0.031068
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 56.9378 | 56.9378
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 5.8188 | 5.9185
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 500.233 | 499.7486
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.12329 | 0.12978
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 8.0189 | 8.0096
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.349 | 1.3485
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.6375 | 1.6668
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1484 | 2.1485
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067311 | 0.067257
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8597e-05 | 2.8577e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.2137 | 1.2348
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 77.1238 | 77.502
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 38.0479 | 40.0679
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.041 | 1.0456
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 322.9474 | 324.5352
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2224.5413 | -2222.9534
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.052495 | -0.052758
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 973.6211 | 973.3914
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.194 | 4.1943
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66557 | 0.66584
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00036791 | 0.00036614
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.5519 | 6.5519
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 71.5246 | 71.9029
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 279.323 | 295.1286
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.97318 | 0.97778
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 299.9137 | 301.4983
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2247.5747 | -2245.9902
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.18593 | -0.18516
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 977.1834 | 976.9641
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1892 | 4.1894
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.66167 | 0.66196
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00039604 | 0.00039404
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.031068 | 0.031068
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 56.9378 | 56.9378
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 16.7451 | 16.7451
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 164.2944 | 164.3625
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 38.2623 | 40.4405
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9843 | 1.985
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 694.7333 | 695.0292
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1852.7552 | -1852.4594
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.090272 | -0.090118
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 903.8487 | 903.7804
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.348 | 4.3482
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68184 | 0.68182
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016509 | 0.00016501
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 5.082 | 5.169
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 212.3696 | 212.1075
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 277.9927 | 293.7365
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.108 | 7.0984
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2881.887 | 2880.9263
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 334.3983 | 333.4378
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0632 | 1.0624
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.3247 | 2.3669
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1395 | 2.1437
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035354 | 0.035352
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6576e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 5.082 | 5.169
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 212.3696 | 212.1075
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 16.2632 | 16.9187
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.108 | 7.0984
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2881.887 | 2880.9263
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 334.3983 | 333.4378
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0632 | 1.0624
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.3247 | 2.3669
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1395 | 2.1437
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035354 | 0.035352
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6576e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 5.082 | 5.169
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 212.3696 | 212.1075
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 261.7295 | 276.8177
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.108 | 7.0984
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2881.887 | 2880.9263
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 334.3983 | 333.4378
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0632 | 1.0624
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.3247 | 2.3669
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1395 | 2.1437
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035354 | 0.035352
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6589e-05 | 1.6576e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 2.014 | 2.049
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 128.8454 | 128.6105
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 261.7295 | 276.8177
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.17 | 7.1601
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2724.6687 | 2723.8159
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 177.1802 | 176.3273
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0082 | 1.0075
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 1.1098 | 1.1303
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.1032 | 2.1075
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027589 | 0.027597
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3304e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 2.014 | 2.049
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 128.8454 | 128.6105
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 7.2042 | 7.6542
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.17 | 7.1601
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2724.6687 | 2723.8159
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 177.1802 | 176.3273
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0082 | 1.0075
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 1.1098 | 1.1303
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.1032 | 2.1075
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027589 | 0.027597
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3304e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.9745 | 2.0088
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 108.7193 | 109.218
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 23.4674 | 24.573
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.4045 | 1.41
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 455.9657 | 458.076
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2091.5229 | -2089.4126
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.021336 | -0.021442
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 951.9878 | 951.6103
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2266 | 4.2273
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68148 | 0.68163
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00025822 | 0.00025696
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.1382 | 6.1382
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 103.1144 | 103.6129
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 279.323 | 295.1286
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3417 | 1.3473
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 432.6099 | 434.7125
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2114.8787 | -2112.7761
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.11608 | -0.11507
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 956.3689 | 956.0029
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2181 | 4.2187
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.67982 | 0.68
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00027331 | 0.00027191
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.3108 | 5.3108
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 150.0223 | 150.0223
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 279.323 | 295.1286
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8421 | 1.8421
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 632.2855 | 632.2855
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1915.203 | -1915.203
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.0084685 | -0.0084685
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 917.0516 | 917.0516
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3096 | 4.3096
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68443 | 0.68443
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018197 | 0.00018197
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 159.409 | 168.4335
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.031068 | 0.031068
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 56.9378 | 56.9378
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.429 | 45.4294
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 279.323 | 295.1286
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64424 | 0.64425
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.2089 | 190.2104
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.2798 | -2357.2781
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061042 | -0.061041
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0566 | 990.0564
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63579 | 0.63579
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059094 | 0.00059094
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3792 | 7.3792
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5065 | 45.5069
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 279.323 | 295.1286
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64496 | 0.64496
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1411 | 191.1427
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3474 | -2356.3459
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.25035 | -0.25035
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3253 | 990.3251
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63624 | 0.63624
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059023 | 0.00059022
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 4.9824 | 5.0676
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 211.6805 | 211.415
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 16.2632 | 16.9187
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.1148 | 7.1052
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2880.887 | 2879.9265
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 333.3984 | 332.4379
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0631 | 1.0623
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.2815 | 2.323
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1365 | 2.1407
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.03527 | 0.035267
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6562e-05 | 1.6549e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 4.9824 | 5.0676
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 123.4267 | 123.9711
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 16.2632 | 16.9187
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5644 | 1.5702
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 518.5051 | 520.8245
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2028.9835 | -2026.6641
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.057441 | -0.057708
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 940.4945 | 940.0497
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2497 | 4.2507
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68486 | 0.68493
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00022523 | 0.00022416
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.7245 | 5.7245
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 117.8152 | 118.3593
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 279.323 | 295.1286
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.5038 | 1.5097
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 494.7392 | 497.0461
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2052.7493 | -2050.4424
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.080241 | -0.079138
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 945.0842 | 944.6489
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.2397 | 4.2406
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68398 | 0.68408
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00023691 | 0.00023574
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 25.0205 | 25.0205
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 210.818 | 210.8185
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 14.3822 | 15.249
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.4314 | 2.4314
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 901.6562 | 901.6583
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1645.8323 | -1645.8302
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.032899 | -0.032898
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 852.2228 | 852.2223
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5515 | 4.5515
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.65669 | 0.65669
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012659 | 0.00012659
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 2.014 | 2.049
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 128.8454 | 128.6105
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 253.5319 | 268.097
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.17 | 7.1601
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2724.6687 | 2723.8159
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 177.1802 | 176.3273
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0082 | 1.0075
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 1.1098 | 1.1303
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.1032 | 2.1075
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027589 | 0.027597
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3315e-05 | 1.3304e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 99.9299 | 101.6485
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 310.948 | 312.1971
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 302.6 | 319.6239
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.6163 | 5.6056
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2725.6003 | 2722.4434
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 178.1117 | 174.9548
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 55.4062 | 56.5834
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 6.727 | 6.8467
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.078958 | 0.079889
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 2.0339e-05 | 2.0412e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.238 | 1.2595
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 105.6857 | 106.1857
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 253.5319 | 268.097
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.2014 | 7.1913
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2651.9521 | 2651.051
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 104.4635 | 103.5624
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.9855 | 0.98474
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.7314 | 0.74384
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2225 | 4.2232
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025406 | 0.025459
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2493e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.238 | 1.2595
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 105.6857 | 106.1857
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 14.5805 | 15.495
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.2014 | 7.1913
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2651.9521 | 2651.051
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 104.4635 | 103.5624
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.9855 | 0.98474
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.7314 | 0.74384
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2225 | 4.2232
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025406 | 0.025459
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2493e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.238 | 1.2595
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 105.6857 | 106.1857
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 238.9514 | 252.6021
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.2014 | 7.1913
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2651.9521 | 2651.051
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 104.4635 | 103.5624
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.9855 | 0.98474
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.7314 | 0.74384
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2225 | 4.2232
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025406 | 0.025459
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2476e-05 | 1.2493e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.37 | 0.37596
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 73.9944 | 74.3739
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 238.9514 | 252.6021
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.28 | 7.2698
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2488.6399 | 2487.4712
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -58.8486 | -60.0172
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.9379 | 0.9371
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.24821 | 0.25217
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1921 | 4.1923
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022335 | 0.022369
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1411e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.37 | 0.37596
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 73.9944 | 74.3739
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 11.037 | 11.8499
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.3412 | 7.331
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2509.8826 | 2508.7424
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -37.606 | -38.7462
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.94705 | 0.94626
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.24582 | 0.24973
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1921 | 4.1923
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022335 | 0.022369
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1411e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.37 | 0.37596
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 73.9944 | 74.3739
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 228.9078 | 241.8187
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.28 | 7.2698
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2488.6399 | 2487.4712
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -58.8486 | -60.0172
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.9379 | 0.9371
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.24821 | 0.25217
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1921 | 4.1923
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022335 | 0.022369
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1411e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 278.5143 | 294.2774
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 110.4265 | 112.3185
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 203.7776 | 203.7778
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 303.3565 | 320.423
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.3515 | 2.3512
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 873.1451 | 873.2237
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1674.3435 | -1674.2648
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.46184 | -0.47243
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 867.3748 | 867.5141
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4619 | 4.4609
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.6696 | 0.66976
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013335 | 0.00013339
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 37.3932
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 11845.7637 | 12496.3633
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.5374
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 156.8152
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2390.6733
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.18051
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 993.3081
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1777
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62587
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006854
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 27.3761
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 11845.7637 | 12496.3633
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 114.9643
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5242
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20878
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 996.5438
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 25.0784 | 25.5064
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 388.9782 | 388.8235
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 14.3822 | 15.249
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 6.9782 | 6.969
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3215.1196 | 3214.0195
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 667.6311 | 666.5309
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.2246 | 1.2244
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 8.512 | 8.6653
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.2314 | 2.2352
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055637 | 0.055663
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3932e-05 | 2.3924e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 16.7451 | 17.0291
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 341.5572 | 341.3435
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 23.8801 | 25.1915
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 7.0184 | 7.0092
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3125.8857 | 3124.7993
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 578.3973 | 577.3107
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1723 | 1.1718
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 6.0965 | 6.2059
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.1959 | 2.1996
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.049652 | 0.049663
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1929e-05 | 2.1919e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 1.9745 | 2.0088
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 128.1893 | 127.9518
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 7.2042 | 7.6542
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.1765 | 7.1666
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2723.6687 | 2722.8159
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 176.1802 | 175.3274
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0082 | 1.0074
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 1.0895 | 1.1096
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.1003 | 2.1045
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027517 | 0.027524
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3292e-05 | 1.3281e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.2137 | 1.2348
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 105.1123 | 105.6105
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 14.5805 | 15.495
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.2076 | 7.1975
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2650.9521 | 2650.051
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 103.4636 | 102.5624
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98546 | 0.9847
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.71801 | 0.73022
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2218 | 4.2224
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.025345 | 0.025398
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2456e-05 | 1.2473e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.36275 | 0.36858
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 73.5249 | 73.9033
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 11.037 | 11.8499
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.3469 | 7.3367
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2508.8826 | 2507.7424
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -38.606 | -39.7462
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.94699 | 0.9462
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.24131 | 0.24515
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1918 | 4.192
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022293 | 0.022327
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1382e-05 | 1.1395e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 497.3914 | 496.8514
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.3402 | 0.35946
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6341 | 9.6327
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3722 | 1.3717
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049218 | 0.049252
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1278 | 2.1274
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066575 | 0.066507
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8475e-05 | 2.8453e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 110.8402 | 112.7321
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 157.7357 | 157.8038
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 159.4091 | 168.4335
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 671.9551 | 672.3629
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.1256
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.62498 | -0.63686
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.7548 | 915.7972
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2969 | 4.2965
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 79.583 | 80.955
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 534.3031 | 534.4175
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 317.5981 | 335.5786
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.8358 | 6.8269
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.5019 | 1.5055
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 22.5424 | 22.9498
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.4095 | 2.4146
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.077249 | 0.077383
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.025e-05 | 3.0262e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 110.8402 | 112.7321
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 157.7357 | 157.8038
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 15.4616 | 16.4438
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 671.9552 | 672.3626
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.126
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.62498 | -0.63686
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.7547 | 915.7972
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2969 | 4.2964
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9655 | 6.9655
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4606 | 46.4606
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 279.323 | 295.1286
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65747 | 0.65747
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0928 | 195.093
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.3958 | -2352.3955
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24256 | -0.24255
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9018 | 989.9018
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63734 | 0.63734
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058047 | 0.00058046
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 5.877 | 5.9777
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.651 | 226.3971
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 279.1023 | 294.9044
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.0971 | 7.0875
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2908.7532 | 2907.7908
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 361.2646 | 360.3021
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0735 | 1.0728
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.6134 | 2.6609
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1449 | 2.1491
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.036802 | 0.0368
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7167e-05 | 1.7154e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.1085 | 52.1086
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 49.4251 | 52.2773
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73098 | 0.73098
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.1178 | 218.1184
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.3706 | -2329.3701
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090194 | -0.0090192
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.0809 | 987.0809
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.64331 | 0.64331
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.0005277 | 0.0005277
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.36275 | 0.36858
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.0692 | 52.0692
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 49.0849 | 51.9178
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73046 | 0.73046
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9698 | 217.9703
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5188 | -2329.5183
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.038644 | -0.039342
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1074 | 987.1077
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64328 | 0.64328
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052804 | 0.00052804
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 229.0892 | 242.0001
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.4167 | 7.4084
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2348.3352 | 2345.7197
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -199.1534 | -201.7688
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.90178 | 0.90068
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.074523 | 0.074614
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.37 | 0.37596
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 73.9944 | 74.3739
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 10.0436 | 10.7834
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.28 | 7.2698
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2488.6399 | 2487.4712
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -58.8486 | -60.0172
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.9379 | 0.9371
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.24821 | 0.25217
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1921 | 4.1923
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022335 | 0.022369
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.1398e-05 | 1.1411e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.3402 | 0.35946
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 110.8402 | 112.7321
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 157.7357 | 157.8038
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 159.4091 | 168.4335
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 671.9551 | 672.3629
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.1256
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.62498 | -0.63686
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.7548 | 915.7972
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2969 | 4.2965
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 110.8402 | 112.7321
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 157.7357 | 157.8038
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 7.7607 | 8.2479
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 671.9552 | 672.3626
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.126
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.62498 | -0.63686
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.7547 | 915.7972
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2969 | 4.2964
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 110.8402 | 112.7321
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 157.7357 | 157.8038
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 159.409 | 168.4335
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 671.9551 | 672.3629
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.1256
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.62498 | -0.63686
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.7548 | 915.7972
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2969 | 4.2965
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 110.8402 | 112.7321
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 157.7357 | 157.8038
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 318.8181 | 336.8669
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 671.9552 | 672.3626
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.126
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.62498 | -0.63686
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.7547 | 915.7972
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2969 | 4.2964
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 110.8402 | 112.7321
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 157.7357 | 157.8038
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 159.409 | 168.4335
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 671.9551 | 672.3629
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1875.5334 | -1875.1256
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.62498 | -0.63686
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.7548 | 915.7972
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2969 | 4.2965
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 110.8402 | 112.7321
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.3365 | 152.3088
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8539 | 1.8534
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.64349 | -0.65588
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 920.8002 | 920.9299
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.283 | 4.2824
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.69106 | 0.69119
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018163 | 0.00018171
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 110.8402 | 112.7321
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.3365 | 152.3088
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8539 | 1.8534
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.64349 | -0.65588
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 920.8002 | 920.9299
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.283 | 4.2824
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.69106 | 0.69119
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018163 | 0.00018171
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 88.5249 | 90.0473
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0032 | 460.003
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 310.3009 | 327.8199
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.5333 | 6.5231
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3286.5439 | 3284.3113
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 739.0553 | 736.8227
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.3898 | 1.3927
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 28.7111 | 29.2578
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.5812 | 2.5924
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.070086 | 0.070268
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7114e-05 | 2.7122e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 159.409 | 168.4335
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.031068 | 0.031068
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 56.9378 | 56.9378
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 159.4091 | 168.4335
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.031068 | 0.031068
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 56.9378 | 56.9378
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.031068 | 0.031068
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 56.9378 | 56.9378
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 27.3223
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 11845.7637 | 12496.3633
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13493
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 996.4656
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 79.583 | 80.955
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 534.3031 | 534.4175
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 318.0616 | 336.0678
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.8358 | 6.8269
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.5019 | 1.5055
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 22.5424 | 22.9498
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.4095 | 2.4146
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.077249 | 0.077383
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.025e-05 | 3.0262e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 110.0128 | 111.9048
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 228.0075 | 228.0933
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 303.3565 | 320.423
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5758 | 2.5762
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 982.8267 | 983.2693
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1564.6619 | -1564.2192
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.37221 | -0.38165
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 837.4348 | 837.4899
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5995 | 4.5986
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65019 | 0.6503
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00011867 | 0.00011867
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 90.2954 | 91.8482
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5047 | 411.5046
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 310.3009 | 327.8199
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.3344 | 6.3231
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3151.5093 | 3148.4856
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 604.0209 | 600.9971
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.297 | 1.2988
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 32.5707 | 33.2209
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.8424 | 2.8622
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.06623 | 0.066481
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.4977e-05 | 2.4983e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 110.8402 | 112.7321
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 157.7357 | 157.8038
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 7.7009 | 8.1959
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.908 | 1.9085
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 671.9552 | 672.3626
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1875.5333 | -1875.126
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.62498 | -0.63686
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.7547 | 915.7972
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2969 | 4.2964
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.69007 | 0.69018
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017493 | 0.0001749
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 97.9705 | 99.6553
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 338.9995 | 339.0006
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 302.6 | 319.6239
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.8911 | 5.8743
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2885.6704 | 2879.0205
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 338.1818 | 331.5319
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1177 | 1.1159
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 45.405 | 46.5215
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 4.3739 | 4.4665
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.069024 | 0.069797
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1664e-05 | 2.1672e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 99.9299 | 101.6485
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 310.948 | 312.1971
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 302.6 | 319.6239
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.6163 | 5.6056
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2725.6003 | 2722.4434
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 178.1117 | 174.9548
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 55.4062 | 56.5834
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 6.727 | 6.8467
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.078958 | 0.079889
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.0339e-05 | 2.0412e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 90.2954 | 91.8482
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.104 | 434.1039
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 302.6 | 319.6239
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.4251 | 6.4144
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3214.6116 | 3211.9792
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 667.1229 | 664.4907
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3428 | 1.3452
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 30.9462 | 31.5494
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.7028 | 2.718
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.067959 | 0.068174
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.5984e-05 | 2.5991e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 81.2155 | 82.6122
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 534.9996 | 535.1237
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 318.0616 | 336.0678
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.8269 | 6.8181
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3484.0393 | 3482.8892
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 936.5507 | 935.4005
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.5072 | 1.511
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 23.0075 | 23.4223
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.4152 | 2.4204
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.077475 | 0.077613
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0288e-05 | 3.0301e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 108.9236 | 110.7968
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 226.0548 | 226.1404
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 303.3565 | 320.423
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.558 | 2.5585
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 973.8266 | 974.2692
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1573.662 | -1573.2194
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.37376 | -0.38309
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 839.886 | 839.9382
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5874 | 4.5865
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65187 | 0.65198
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.00011971 | 0.00011971
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 57.2791 | 57.751
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15424.9043
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15407.5234
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 7.5583
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 241245.2969 | 247170.3125
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 266463.3438 | 268658.4375
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 30
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 20.46
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Remark: 6 - Water exit temperature has been reduced by minimum DT allowed. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,5

## ELINK
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
72¦79¦76¦81¦78¦98¦89¦68¦85¦~-100~~~~~ | INPUTS - C:\Users\Admin\Documents\Thermoflow\MYFILES29\UJTNY_What if_100%_RevA.tfx: Case number for file used to start calculation (<0 = Skip case) |  | 0 | 0 | #N/A | 0
~2006~~1~~-2006~ | Computation Settings: Pressure damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~2~~-2006~ | Computation Settings: Flow damping factor (0.5=none, 1.0=default, 10=max) |  | 1 | 1 | #N/A | 1
~2006~~3~~-2006~ | Computation Settings: Convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~4~~-2006~ | Computation Settings: Minimum computing loops |  | 30 | 30 | #N/A | 30
~2006~~5~~-2006~ | Computation Settings: Maximum computing loops |  | 60 | 60 | #N/A | 60
~2006~~6~~-2006~ | Computation Settings: Script convergence tolerance (0.1=tight, 1.0=default, >1=loose) |  | 1 | 1 | #N/A | 1
~2006~~7~~-2006~ | Computation Settings: Maximum Script computing loops |  | 20 | 20 | #N/A | 20
~~1~1~~-1000~ | Site Menu: Site altitude | m | 7 | 7 | #N/A | 7
~~1~2~~-1000~ | Site Menu: Ambient temperature | C | 32.18 | 30 | 30 | 30
~~1~3~~-1000~ | Site Menu: Ambient relative humidity | % | 59.56 | 75 | 75 | 75
~~1~4~~-1000~ | Site Menu: Ambient wet bulb temperature | C | 25.6342 | 25.6342 | #N/A | 25.6342
~~1~5~~-1000~ | Site Menu: Ambient pressure | bar | 1.0124 | 1.0124 | 1.0124 | 1.0124
91¦~7~1~10~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | t/h | 387.7 | 234.534 | 234.534 | 234.534
91¦~7~1~124~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Evaporation load in wing wall | % | 20 | 20 | #N/A | 20
91¦~7~1~18~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | C | 893.9999 | 863.7255 | 863.7255 | 863.7255
91¦~7~1~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25 | 25 | 25
91¦~7~1~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Minor heat loss | % | 2 | 2 | #N/A | 2
91¦~7~1~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Blowdown | % | 0.25 | 0.25 | #N/A | 0.25
91¦~7~1~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace gage pressure | millibar | -0.24907 | -0.24907 | #N/A | -0.24907
91¦~7~1~38~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air flow/combustion air | % | 51 | 51 | #N/A | 51
91¦~7~1~36~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Primary air pressure | millibar | 149.4396 | 149.4396 | #N/A | 149.4396
91¦~7~1~6~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Secondary air pressure drop | millibar | 64.72 | 64.72 | #N/A | 64.72
91¦~7~1~143~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Cyclone pressure drop | millibar | 17.3 | 17.3 | #N/A | 17.3
91¦~7~1~12~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX2 wing wall outlet temperature | C | 460 | 460 | #N/A | 460
91¦~7~1~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HX3 Cyclone wall outlet temperature | C | 339 | 339 | #N/A | 339
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content (for emission level definition) | % | 6 | 6 | #N/A | 6
91¦~7~1~152~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production based on HHV heat input | ng/J | 0 | 0 | #N/A | 0
~25~1~7~~-27~ | Deaerator [25] - DAER : Deaerator design pressure | bar | 5.27 | 5.27 | #N/A | 5.27
~25~1~8~~-27~ | Deaerator [25] - DAER : Deaerator outlet temperature @ design | C | 153.8281 | 153.8281 | #N/A | 153.8281
~25~1~5~~-27~ | Deaerator [25] - DAER : Additional water level at inlet (water level rise from inlet to DA water surface) | m | 0.4161 | 0.4161 | #N/A | 0.4161
~25~1~6~~-27~ | Deaerator [25] - DAER : Additional water level at outlet (water level difference from DA water surface to outlet) | m | 0.3904 | 0.3904 | #N/A | 0.3904
~68~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Specified outlet temperature | C | 436 | 436 | #N/A | 436
~68~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
~78~1~1~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Specified outlet temperature | C | 411.5 | 411.5 | #N/A | 411.5
~78~1~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Minimum superheat after desuperheating | C | 15 | 15 | #N/A | 15
73¦74¦91¦~48~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~48~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Assumed gas temperature drop | C | 1.2 | 1.2 | #N/A | 1.2
73¦74¦91¦~65~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~65~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~2~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~2~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~82~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~82~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
73¦74¦91¦~83~5~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed draft loss | millibar | 4.9813 | 4.9813 | #N/A | 4.9813
73¦74¦91¦~83~5~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Assumed gas temperature drop | C | 1 | 1 | #N/A | 1
~42~1~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Desired water exit temperature | C | 303 | 303 | #N/A | 303
~42~1~9~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss as % of water heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~42~1~6~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~42~1~8~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Assumed water side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~12~1~1~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified collection efficiency at design | % | 99.782 | 99.782 | #N/A | 99.782
91¦~12~1~96~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per energy input at design | ng/J | 8.599 | 8.599 | #N/A | 8.599
91¦~12~1~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified emission per flue gas flow at design | mg/Nm^3 | 25 | 25 | #N/A | 25
91¦~12~1~9~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Specified flue gas velocity at design | m/s | 1.2192 | 1.2192 | #N/A | 1.2192
91¦~12~1~26~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Reference O2 content | % | 6 | 6 | #N/A | 6
91¦~12~1~65~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined dimensionless K |  | 0.48065 | 0.48065 | #N/A | 0.48065
91¦~12~1~66~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate migration velocity | m/s | 0.21336 | 0.21336 | #N/A | 0.21336
91¦~12~1~67~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : User-defined particulate resistiviry | ohm-cm | 100000000 | 100000000 | #N/A | 100000000
91¦~12~1~68~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature drop (including dustwork) | C | 1.2 | 1.2 | #N/A | 1.2
91¦~52~1~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan design point overall pressure rise | millibar | 50.5503 | 50.5503 | #N/A | 50.5503
91¦~52~1~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~52~1~8~~-65~ | Boiler Assembly [1]: Fan [52] : Flow margin | % | 0 | 0 | #N/A | 0
91¦~52~1~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~52~1~5~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~7~~-65~ | Boiler Assembly [1]: Fan [52] : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~52~1~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~52~1~16~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss | kW | 11.2555 | 11.2555 | #N/A | 11.2555
91¦~52~1~13~~-65~ | Boiler Assembly [1]: Fan [52] : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~52~1~10~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~52~1~11~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal inlet volume flow for off-design fan curve | m^3/s | 179.5939 | 179.5939 | #N/A | 179.5939
91¦~52~1~12~~-65~ | Boiler Assembly [1]: Fan [52] : Nominal corrected pressure rise for off-design fan curve | millibar | 77.1724 | 77.1724 | #N/A | 77.1724
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~72~1~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~72~1~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~72~1~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~72~1~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~72~1~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~7~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~72~1~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~72~1~16~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss | kW | 2.6891 | 2.6891 | #N/A | 2.6891
91¦~72~1~13~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~72~1~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~72~1~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 26.7221 | 26.7221 | #N/A | 26.7221
91¦~72~1~12~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~9~1~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~9~1~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~9~1~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~9~1~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~9~1~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~7~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~9~1~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~9~1~16~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss | kW | 5.5477 | 5.5477 | #N/A | 5.5477
91¦~9~1~13~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~9~1~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~9~1~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal inlet volume flow for off-design fan curve | m^3/s | 27.8128 | 27.8128 | #N/A | 27.8128
91¦~9~1~12~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~81~1~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan design point overall pressure rise | millibar | 166.8743 | 166.8743 | #N/A | 166.8743
91¦~81~1~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~81~1~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~81~1~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~81~1~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~7~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~81~1~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~81~1~16~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss | kW | 5.5477 | 5.5477 | #N/A | 5.5477
91¦~81~1~13~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~81~1~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~81~1~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 27.8128 | 27.8128 | #N/A | 27.8128
91¦~81~1~12~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 178.198 | 178.198 | #N/A | 178.198
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~85~1~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan design point overall pressure rise | millibar | 81.9056 | 81.9056 | #N/A | 81.9056
91¦~85~1~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure margin | % | 0 | 0 | #N/A | 0
91¦~85~1~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Flow margin | % | 0 | 0 | #N/A | 0
91¦~85~1~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan nominal isentropic efficiency | % | 80 | 80 | #N/A | 80
91¦~85~1~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~7~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Design point RPM |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99 | #N/A | 99
91¦~85~1~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1 | #N/A | 1
91¦~85~1~16~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss | kW | 2.6891 | 2.6891 | #N/A | 2.6891
91¦~85~1~13~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan off-design control damper dP | millibar | 0 | 0 | #N/A | 0
91¦~85~1~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal RPM for off-design fan curve |  | 1200 | 1200 | #N/A | 1200
91¦~85~1~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal inlet volume flow for off-design fan curve | m^3/s | 26.7221 | 26.7221 | #N/A | 26.7221
91¦~85~1~12~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Nominal corrected pressure rise for off-design fan curve | millibar | 87.4635 | 87.4635 | #N/A | 87.4635
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
91¦~21~1~70~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : FW temperature at heater exit | C | 85 | 85 | #N/A | 85
91¦~21~1~63~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~21~1~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~21~1~72~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~21~1~34~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~22~1~70~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : FW temperature at heater exit | C | 110 | 110 | #N/A | 110
91¦~22~1~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~22~1~72~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~22~1~34~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~23~1~70~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : FW temperature at heater exit | C | 125 | 125 | #N/A | 125
91¦~23~1~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~23~1~72~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~23~1~34~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~24~1~70~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : FW temperature at heater exit | C | 150 | 150 | #N/A | 150
91¦~24~1~63~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~24~1~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach temperature difference | C | 5.6 | 5.6 | #N/A | 5.6
91¦~24~1~72~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~24~1~34~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~32~1~70~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : FW temperature at heater exit | C | 204.2 | 204.2 | #N/A | 204.2
91¦~32~1~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal temperature difference (TTD) | C | -0.19 | -0.19 | #N/A | -0.19
91¦~32~1~63~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~32~1~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach temperature difference | C | 6.536 | 6.536 | #N/A | 6.536
91¦~32~1~72~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~32~1~34~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~46~1~70~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : FW temperature at heater exit | C | 228.1 | 228.1 | #N/A | 228.1
91¦~46~1~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal temperature difference (TTD) | C | -4.1 | -4.1 | #N/A | -4.1
91¦~46~1~63~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Residual superheat at desuperheater exit | C | 5 | 5 | #N/A | 5
91¦~46~1~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach temperature difference | C | 7.041 | 7.041 | #N/A | 7.041
91¦~46~1~72~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~46~1~34~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Min. pinch temp. difference | C | 0.27778 | 0.27778 | #N/A | 0.27778
91¦~10~1~1~~-24~ | Fuel Source [10] - Coal : Fuel supply pressure | bar | 1.0124 | 1.0124 | #N/A | 1.0124
91¦~10~1~2~~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33 | #N/A | 33
91¦~10~1~3~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 79 | 79 | #N/A | 79
91¦~10~1~9~~-24~ | Fuel Source [10] - Coal : Fuel LHV price: user-defined | USD/GJ | 2.4392 | 2.4392 | #N/A | 2.4392
~10~4~15~100~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim | #N/A | Perf. Test WI sim
~10~2~19~100~-24~ | Fuel Source [10] - Coal : Solid type (0=coal,1=coke,3=biomass,9=other) |  | 0 | 0 | #N/A | 0
~10~1~53~100~-24~ | Fuel Source [10] - Coal : Weight percent of Moisture | % | 40.05 | 30 | 30 | 30
~10~1~54~100~-24~ | Fuel Source [10] - Coal : Weight percent of Ash | % | 6.61 | 6.61 | #N/A | 6.61
~10~1~55~100~-24~ | Fuel Source [10] - Coal : Weight percent of C | % | 39.35 | 39.35 | #N/A | 39.35
~10~1~56~100~-24~ | Fuel Source [10] - Coal : Weight percent of H | % | 2.78 | 2.78 | #N/A | 2.78
~10~1~58~100~-24~ | Fuel Source [10] - Coal : Weight percent of N | % | 0.55 | 0.55 | #N/A | 0.55
~10~1~65~100~-24~ | Fuel Source [10] - Coal : Weight percent of Cl | % | 0 | 0 | #N/A | 0
~10~1~59~100~-24~ | Fuel Source [10] - Coal : Weight percent of S | % | 0.25 | 0.25 | #N/A | 0.25
~10~1~57~100~-24~ | Fuel Source [10] - Coal : Weight percent of O | % | 10.41 | 10.41 | #N/A | 10.41
~10~1~60~100~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747 | 16747 | 16747
~10~1~52~100~-24~ | Fuel Source [10] - Coal : Weight percent of Volatile Matter | % | 28.42 | 28.42 | #N/A | 28.42
~10~1~91~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 25 C, dry | kJ/kg-C | 1.2978 | 1.2978 | #N/A | 1.2978
~10~1~92~100~-24~ | Fuel Source [10] - Coal : Specific heat (Cp) at 300 C, dry | kJ/kg-C | 2.0933 | 2.0933 | #N/A | 2.0933
~10~1~64~100~-24~ | Fuel Source [10] - Coal : Hardgrove grindability index (HGI) |  | 46 | 46 | #N/A | 46
~10~1~75~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SiO2 | % | 18 | 18 | #N/A | 18
~10~1~76~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Al2O3 | % | 19 | 19 | #N/A | 19
~10~1~77~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Fe2O3 | % | 23.5 | 23.5 | #N/A | 23.5
~10~1~78~100~-24~ | Fuel Source [10] - Coal : Ash weight % of CaO | % | 18.5 | 18.5 | #N/A | 18.5
~10~1~79~100~-24~ | Fuel Source [10] - Coal : Ash weight % of MgO | % | 7.1 | 7.1 | #N/A | 7.1
~10~1~80~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Na2O | % | 5 | 5 | #N/A | 5
~10~1~81~100~-24~ | Fuel Source [10] - Coal : Ash weight % of K2O | % | 0.5 | 0.5 | #N/A | 0.5
~10~1~82~100~-24~ | Fuel Source [10] - Coal : Ash weight % of TiO2 | % | 0.7 | 0.7 | #N/A | 0.7
~10~1~83~100~-24~ | Fuel Source [10] - Coal : Ash weight % of P2O5 | % | 0.04 | 0.04 | #N/A | 0.04
~10~1~84~100~-24~ | Fuel Source [10] - Coal : Ash weight % of SO3 | % | 7.66 | 7.66 | #N/A | 7.66
~10~1~85~100~-24~ | Fuel Source [10] - Coal : Ash weight % of Other | % | 0 | 0 | #N/A | 0
~10~1~86~100~-24~ | Fuel Source [10] - Coal : Ash Initial Deformation Temperature (reducing atm.) | C | 1095 | 1095 | #N/A | 1095
~10~1~61~100~-24~ | Fuel Source [10] - Coal : Ash softening temperature (reducing atm.) | C | 1130 | 1130 | #N/A | 1130
91¦~11~1~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~11~1~21~~-1~ | Gas/Air Source [11] - SA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~11~1~22~~-1~ | Gas/Air Source [11] - SA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~8~1~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~8~1~21~~-1~ | Gas/Air Source [8] - PA #1 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~8~1~22~~-1~ | Gas/Air Source [8] - PA #1 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~80~1~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 211.168 | 211.168 | #N/A | 211.168
91¦~80~1~21~~-1~ | Gas/Air Source [80] - PA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~80~1~22~~-1~ | Gas/Air Source [80] - PA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
91¦~84~1~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 239.5 | 239.5 | #N/A | 239.5
91¦~84~1~21~~-1~ | Gas/Air Source [84] - SA #2 : Heat price: user-defined | USD/GJ | 0 | 0 | #N/A | 0
91¦~84~1~22~~-1~ | Gas/Air Source [84] - SA #2 : Mass price: user-defined | USD/tonne | 0 | 0 | #N/A | 0
83¦91¦~45~1~12~~-168~ | General Pump [45] - CP : Assumed isentropic efficiency for TD mode | % | 75 | 75 | #N/A | 75
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~6~1~12~~-168~ | General Pump [6] - CWP-2 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~27~1~12~~-168~ | General Pump [27] - CWP-1 : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Rating / design point load |  | 1.0349 | 1.0349 | #N/A | 1.0349
83¦91¦~35~1~12~~-168~ | General Pump [35] - BFP-C : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Rating / design point load |  | 1.75 | 1.75 | #N/A | 1.75
83¦91¦~50~1~12~~-168~ | General Pump [50] - BFP-B : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
83¦91¦~59~1~12~~-168~ | General Pump [59] - BFP-A : Assumed isentropic efficiency for TD mode | % | 50 | 50 | #N/A | 50
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Rating / design point load |  | 1.3899 | 1.3899 | #N/A | 1.3899
91¦~44~1~1~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15 | #N/A | 15
91¦~44~1~2~~-46~ | Makeup / Blowdown [44] : Makeup quality |  | 1 | 1 | #N/A | 1
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9 | #N/A | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09 | #N/A | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91 | #N/A | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
~14~1~3~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~5~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air desired temperature change | C | 175 | 175 | #N/A | 175
~14~1~17~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss as percent of heat transfer | % | 0.5 | 0.5 | #N/A | 0.5
~14~1~6~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Secondary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~7~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Primary air assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~14~1~8~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External gas assumed pressure drop for TD mode | millibar | 12.4533 | 12.4533 | #N/A | 12.4533
~53~1~4~~-107~ | Pipe (PCE) [53] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~53~1~9~~-107~ | Pipe (PCE) [53] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~54~1~4~~-107~ | Pipe (PCE) [54] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~54~1~9~~-107~ | Pipe (PCE) [54] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~55~1~4~~-107~ | Pipe (PCE) [55] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~55~1~9~~-107~ | Pipe (PCE) [55] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~56~1~4~~-107~ | Pipe (PCE) [56] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~56~1~9~~-107~ | Pipe (PCE) [56] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~57~1~4~~-107~ | Pipe (PCE) [57] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~57~1~9~~-107~ | Pipe (PCE) [57] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~58~1~4~~-107~ | Pipe (PCE) [58] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 2 | 2 | #N/A | 2
~58~1~9~~-107~ | Pipe (PCE) [58] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~1~1~4~~-107~ | Pipe (PCE) [1] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~1~1~9~~-107~ | Pipe (PCE) [1] : Heat Loss | kJ/kg | 1 | 1 | #N/A | 1
~4~1~4~~-107~ | Pipe (PCE) [4] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1.8 | 1.8 | #N/A | 1.8
~4~1~9~~-107~ | Pipe (PCE) [4] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
~77~1~4~~-107~ | Pipe (PCE) [77] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 1 | 1 | #N/A | 1
~77~1~9~~-107~ | Pipe (PCE) [77] : Heat Loss | kJ/kg | 9 | 9 | #N/A | 9
~79~1~4~~-107~ | Pipe (PCE) [79] : Assumed pressure drop for TD mode (as % of exit pressure) | % | 0 | 0 | #N/A | 0
~79~1~9~~-107~ | Pipe (PCE) [79] : Heat Loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~63~1~84~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Condenser pressure | bar | 0.175 | 0.175 | #N/A | 0.175
91¦~63~1~72~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Assumed water-side pressure drop for TD mode | bar | 0.41368 | 0.41368 | #N/A | 0.41368
91¦~63~1~34~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Min. pinch temp. difference | C | 2 | 2 | #N/A | 2
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904 | #N/A | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306 | #N/A | 0.00096306
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97 | #N/A | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03 | #N/A | 0.03
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92 | #N/A | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08 | #N/A | 0.08
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989 | #N/A | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011 | #N/A | 0.011
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954 | #N/A | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046 | #N/A | 0.046
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873 | #N/A | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1 | #N/A | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027 | #N/A | 0.027
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942 | #N/A | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058 | #N/A | 0.058
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393 | #N/A | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607 | #N/A | 0.0607
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333 | #N/A | 0.33333
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5 | #N/A | 0.5
91¦~38~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | C | 537.2 | 532.534 | 532.534 | 532.534
~38~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss as % of steam heat transfer | % | 0 | 0 | #N/A | 0
~38~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~38~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Assumed steam side pressure drop for TD mode | % | 9 | 9 | #N/A | 9
91¦~41~1~4~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Desired steam outlet temperature | C | 434.1 | 434.1 | #N/A | 434.1
~41~1~9~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss as % of steam heat transfer | % | 0.75 | 0.75 | #N/A | 0.75
~41~1~6~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Minimum temperature difference | C | 5 | 5 | #N/A | 5
~41~1~8~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Assumed steam side pressure drop for TD mode | % | 8.5 | 8.5 | #N/A | 8.5
~13~2~2~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 1 | 1 | #N/A | 1
~13~1~5~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~13~1~6~~-32~ | Boiler Assembly [1]: Valve [13] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~8~~-32~ | Boiler Assembly [1]: Valve [13] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~13~1~7~~-32~ | Boiler Assembly [1]: Valve [13] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~31~2~2~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 3 | 3 | #N/A | 3
~31~1~5~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~31~1~6~~-32~ | Boiler Assembly [1]: Valve [31] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~8~~-32~ | Boiler Assembly [1]: Valve [31] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~31~1~7~~-32~ | Boiler Assembly [1]: Valve [31] : Specified pressure drop | bar | 0.2 | 0.2 | #N/A | 0.2
~69~2~2~~-32~ | Valve [69] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~69~1~5~~-32~ | Valve [69] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~69~1~6~~-32~ | Valve [69] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~8~~-32~ | Valve [69] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~69~1~7~~-32~ | Valve [69] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~70~2~2~~-32~ | Valve [70] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~70~1~5~~-32~ | Valve [70] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~70~1~6~~-32~ | Valve [70] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~8~~-32~ | Valve [70] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~70~1~7~~-32~ | Valve [70] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~71~2~2~~-32~ | Valve [71] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 2 | 2 | #N/A | 2
~71~1~5~~-32~ | Valve [71] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~71~1~6~~-32~ | Valve [71] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~8~~-32~ | Valve [71] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~71~1~7~~-32~ | Valve [71] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~73~2~2~~-32~ | Valve [73] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~73~1~5~~-32~ | Valve [73] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~73~1~6~~-32~ | Valve [73] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~8~~-32~ | Valve [73] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~73~1~7~~-32~ | Valve [73] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~74~2~2~~-32~ | Valve [74] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 5 | 5 | #N/A | 5
~74~1~5~~-32~ | Valve [74] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~74~1~6~~-32~ | Valve [74] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~8~~-32~ | Valve [74] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~74~1~7~~-32~ | Valve [74] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
~75~2~2~~-32~ | Valve [75] : Pressure control 0:Upset 1:VWO 2:Dnset 3:dP 4:Rubber 5:Closed |  | 0 | 0 | #N/A | 0
~75~1~5~~-32~ | Valve [75] : Pressure drop at valve wide open (dP/P) | % | 0 | 0 | #N/A | 0
~75~1~6~~-32~ | Valve [75] : Upstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~8~~-32~ | Valve [75] : Downstream set point | bar | 3.4473 | 3.4473 | #N/A | 3.4473
~75~1~7~~-32~ | Valve [75] : Specified pressure drop | bar | 0 | 0 | #N/A | 0
91¦~51~1~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75 | #N/A | 2.75
91¦~51~1~21~~-14~ | Water Sink [51] - Outfall : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~51~1~22~~-14~ | Water Sink [51] - Outfall : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
91¦~3~1~2~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135 | #N/A | 1.0135
91¦~3~1~3~~-9~ | Water Source [3] - Intake : Temperature | C | 29.22 | 27.3 | 27.3 | 27.3
91¦~3~1~4~~-9~ | Water Source [3] - Intake : Steam quality |  | -2 | -2 | #N/A | -2
91¦~3~1~5~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 163.2936 | 163.2936 | #N/A | 163.2936
91¦~3~1~21~~-9~ | Water Source [3] - Intake : Heat price: user-defined | USD/GJ | 4.7393 | 4.7393 | #N/A | 4.7393
91¦~3~1~22~~-9~ | Water Source [3] - Intake : Mass price: user-defined | USD/tonne | 12.0735 | 12.0735 | #N/A | 12.0735
~40~1~53~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985 | #N/A | 0.0985
~40~1~5~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condensate subcooling at condenser pressure | C | 0 | 0 | #N/A | 0
~40~1~9~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | C | 10 | 10 | 10 | 10
~~1~2~~-1005~ | Miscellaneous: Misc. auxiliary as fraction of gross plant output |  | 0.01 | 0.01 | #N/A | 0.01
~~1~3~~-1005~ | Miscellaneous: Misc. auxiliary power | kW | 0 | 0 | #N/A | 0
~~1~4~~-1005~ | Miscellaneous: LHV efficiency of alternate boiler | % | 93 | 93 | #N/A | 93
~~1~6~~-1005~ | Miscellaneous: Step Up Transformer loss as fraction of gross plant output |  | 0.005 | 0.005 | #N/A | 0.005
91¦~10~1~1~1~-7000~ | Energy Inflow: Multiplier of Fuel Source [10] - Coal |  | 1 | 1 | #N/A | 1
91¦~16~1~1~3~-7000~ | Power Device: Multiplier of ST Assembly [1]: ST Group [16] - ST Assembly [1]-G |  | 1 | 1 | #N/A | 1
91¦~7~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux |  | 1 | 1 | #N/A | 1
91¦~42~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux |  | 1 | 1 | #N/A | 1
91¦~12~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux |  | 1 | 1 | #N/A | 1
91¦~52~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [52] : aux |  | 1 | 1 | #N/A | 1
91¦~72~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~81~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~85~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux |  | 1 | 1 | #N/A | 1
91¦~9~1~1~4~-7000~ | Auxiliary Device: Multiplier of Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux |  | 1 | 1 | #N/A | 1
91¦~27~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [27] - CWP-1 |  | 1 | 1 | #N/A | 1
91¦~35~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [35] - BFP-C |  | 1 | 1 | #N/A | 1
91¦~45~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [45] - CP |  | 1 | 1 | #N/A | 1
91¦~50~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [50] - BFP-B |  | 1 | 1 | #N/A | 1
91¦~59~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [59] - BFP-A |  | 1 | 1 | #N/A | 1
91¦~6~1~1~4~-7000~ | Auxiliary Device: Multiplier of General Pump [6] - CWP-2 |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦~16~1~5~~-4100~ | ST Assembly [1]: Throttle pressure / first stage exit pressure |  | 1.3 | 1.3 | #N/A | 1.3
86¦87¦68¦86¦86¦~16~1~7~~-4100~ | ST Assembly [1]: Nameplate throttle pressure / current value |  | 1.05 | 1.05 | #N/A | 1.05
86¦87¦68¦86¦86¦~16~1~25~~-4100~ | ST Assembly [1]: Nameplate throttle temperature / current value |  | 1 | 1 | #N/A | 1
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~1~-4100~ | ST Assembly [1]: Leakage flow (Valve Stem leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 1 to LP section inlet) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~1~-4100~ | ST Assembly [1]: Leakage flow (HPT HP leak 2 to SSR) | t/h | 0 | 0 | #N/A | 0
86¦87¦68¦86¦86¦~16~1~8~~-4100~ | ST Assembly [1]: Sealing steam condenser pressure | bar | 0.82736 | 0.82736 | #N/A | 0.82736
86¦87¦68¦86¦86¦~16~1~9~~-4100~ | ST Assembly [1]: Sealing steam regulator pressure | bar | 1.241 | 1.241 | #N/A | 1.241
86¦87¦68¦86¦86¦~16~1~13~~-4100~ | ST Assembly [1]: Maximum sealing steam regulator temperature | C | 148.8889 | 148.8889 | #N/A | 148.8889
86¦87¦68¦86¦86¦~16~1~14~~-4100~ | ST Assembly [1]: Desuperheating water temperature | C | 15 | 15 | #N/A | 15
86¦87¦68¦86¦86¦~16~1~10~~-4100~ | ST Assembly [1]: ST misc auxiliary power (% of generator rating) | % | 0.05 | 0.05 | #N/A | 0.05
91¦~16~1~4~2000~-4100~ | ST Assembly [1]: Generator design point power factor |  | 0.9 | 0.9 | 0.9 | 0.9
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator rating / design point load |  | 1.05 | 1.05 | #N/A | 1.05
89¦~16~3~18~2000~-4100~ | ST Assembly [1]: Generator mechanical loss as % of generator total loss @ rating | % | 12 | 12 | #N/A | 12
91¦~16~1~2~~-11~ | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 86.45 | 74.0925 | 74.0925 | 74.0925
91¦~16~1~40~~-11~ | ST Assembly [1]: ST Group [16] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.81 | 0.81 | #N/A | 0.81
91¦~16~1~7~~-11~ | ST Assembly [1]: ST Group [16] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~16~5~15~~-11~ | ST Assembly [1]: ST Group [16] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~16~1~4~~-11~ | ST Assembly [1]: ST Group [16] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~16~1~5~~-11~ | ST Assembly [1]: ST Group [16] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~16~1~6~~-11~ | ST Assembly [1]: ST Group [16] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~16~1~11~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~16~1~12~~-11~ | ST Assembly [1]: ST Group [16] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~17~1~2~~-11~ | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 27.68 | 23.8111 | 23.8111 | 23.8111
91¦~17~1~40~~-11~ | ST Assembly [1]: ST Group [17] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.86 | 0.86 | #N/A | 0.86
91¦~17~1~7~~-11~ | ST Assembly [1]: ST Group [17] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~17~5~15~~-11~ | ST Assembly [1]: ST Group [17] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~17~1~4~~-11~ | ST Assembly [1]: ST Group [17] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~17~1~5~~-11~ | ST Assembly [1]: ST Group [17] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~17~1~6~~-11~ | ST Assembly [1]: ST Group [17] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~17~1~11~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~17~1~12~~-11~ | ST Assembly [1]: ST Group [17] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~18~1~2~~-11~ | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 18.75 | 15.8973 | 15.8973 | 15.8973
91¦~18~1~40~~-11~ | ST Assembly [1]: ST Group [18] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.91 | 0.91 | #N/A | 0.91
91¦~18~1~7~~-11~ | ST Assembly [1]: ST Group [18] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~18~5~15~~-11~ | ST Assembly [1]: ST Group [18] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~18~1~4~~-11~ | ST Assembly [1]: ST Group [18] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~18~1~5~~-11~ | ST Assembly [1]: ST Group [18] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~18~1~6~~-11~ | ST Assembly [1]: ST Group [18] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~18~1~11~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~18~1~12~~-11~ | ST Assembly [1]: ST Group [18] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~19~1~2~~-11~ | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 6.36 | 5.471 | 5.471 | 5.471
91¦~19~1~40~~-11~ | ST Assembly [1]: ST Group [19] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.93 | 0.93 | #N/A | 0.93
91¦~19~1~7~~-11~ | ST Assembly [1]: ST Group [19] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~19~5~15~~-11~ | ST Assembly [1]: ST Group [19] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~19~1~4~~-11~ | ST Assembly [1]: ST Group [19] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~19~1~5~~-11~ | ST Assembly [1]: ST Group [19] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~19~1~6~~-11~ | ST Assembly [1]: ST Group [19] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~19~1~11~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~19~1~12~~-11~ | ST Assembly [1]: ST Group [19] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~20~1~2~~-11~ | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 5.5 | 4.7308 | 4.7308 | 4.7308
91¦~20~1~40~~-11~ | ST Assembly [1]: ST Group [20] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~20~1~7~~-11~ | ST Assembly [1]: ST Group [20] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~20~5~15~~-11~ | ST Assembly [1]: ST Group [20] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~20~1~4~~-11~ | ST Assembly [1]: ST Group [20] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~20~1~5~~-11~ | ST Assembly [1]: ST Group [20] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~20~1~6~~-11~ | ST Assembly [1]: ST Group [20] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~20~1~11~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~20~1~12~~-11~ | ST Assembly [1]: ST Group [20] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~36~1~2~~-11~ | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 2.18 | 1.8753 | 1.8753 | 1.8753
91¦~36~1~40~~-11~ | ST Assembly [1]: ST Group [36] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~36~1~7~~-11~ | ST Assembly [1]: ST Group [36] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~36~5~15~~-11~ | ST Assembly [1]: ST Group [36] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~36~1~4~~-11~ | ST Assembly [1]: ST Group [36] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~36~1~5~~-11~ | ST Assembly [1]: ST Group [36] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~36~1~6~~-11~ | ST Assembly [1]: ST Group [36] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~36~1~11~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~36~1~12~~-11~ | ST Assembly [1]: ST Group [36] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~37~1~2~~-11~ | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 1.34 | 1.1527 | 1.1527 | 1.1527
91¦~37~1~40~~-11~ | ST Assembly [1]: ST Group [37] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~37~1~7~~-11~ | ST Assembly [1]: ST Group [37] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~37~5~15~~-11~ | ST Assembly [1]: ST Group [37] : Design point dry exhaust loss | kJ/kg | 0 | 0 | #N/A | 0
91¦~37~1~4~~-11~ | ST Assembly [1]: ST Group [37] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~37~1~5~~-11~ | ST Assembly [1]: ST Group [37] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~37~1~6~~-11~ | ST Assembly [1]: ST Group [37] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~37~1~11~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~37~1~12~~-11~ | ST Assembly [1]: ST Group [37] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
91¦~39~1~2~~-11~ | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | bar | 0.4 | 0.34409 | 0.34409 | 0.34409
91¦~39~1~40~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatic estimate of design point dry step efficiency |  | 0.95 | 0.95 | #N/A | 0.95
91¦~39~1~7~~-11~ | ST Assembly [1]: ST Group [39] : Design point stop valve (and/or internal piping) pressure drop (% of inlet pressure) | % | 0 | 0 | #N/A | 0
72¦79¦91¦~39~5~6~~-11~ | ST Assembly [1]: ST Group [39] : Correction factor to automatically computed design point dry exhaust loss | kJ/kg | 2.3259 | 2.3259 | #N/A | 2.3259
91¦~39~1~4~~-11~ | ST Assembly [1]: ST Group [39] : Reference pressure ratio for steam turbine expansion step |  | 1.35 | 1.35 | #N/A | 1.35
91¦~39~1~5~~-11~ | ST Assembly [1]: ST Group [39] : Condensation quality (Wilson line) |  | 0.97 | 0.97 | #N/A | 0.97
91¦~39~1~6~~-11~ | ST Assembly [1]: ST Group [39] : Moisture efficiency penalty (Baumann coefficient) |  | 0.72 | 0.72 | #N/A | 0.72
91¦~39~1~11~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical efficiency | % | 99.75 | 99.75 | #N/A | 99.75
91¦~39~1~12~~-11~ | ST Assembly [1]: ST Group [39] : Sizing flow / design point flow |  | 1 | 1 | #N/A | 1
~1~1~~~-5007~ | Boiler: Label 1 |  | ESP | ESP | #N/A | ESP
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
~~~1~~-5000~ | Plant Summary: Ambient pressure | bar | 1.0124 | 1.0124
~~~2~~-5000~ | Plant Summary: Ambient temperature | C | 32.18 | 30
~~~3~~-5000~ | Plant Summary: Ambient RH | % | 59.56 | 70.7778
~~~20~~-5000~ | Plant Summary: Ambient wet bulb temperature | C | 25.6342 | 25.6328
~~~4~~-5000~ | Plant Summary: Gross power | kW | 110027.0938 | 99960.1641
~~~7~~-5000~ | Plant Summary: Net power | kW | 98810.8672 | 90304.7812
~~~29~~-5000~ | Plant Summary: Total auxiliaries and transformer losses | kW | 11216.2236 | 9655.3809
~~~14~~-5000~ | Plant Summary: Plant auxiliary | kW | 10666.0879 | 9155.5791
~~~27~~-5000~ | Plant Summary: Transformer losses | kW | 550.1355 | 499.8008
~~~5~~-5000~ | Plant Summary: Gross electric efficiency(LHV) | % | 35.5933 | 36.5354
~~~6~~-5000~ | Plant Summary: Gross heat rate(LHV) | kJ/kWh | 10114.2646 | 9853.459
~~~8~~-5000~ | Plant Summary: Net electric efficiency(LHV) | % | 31.9649 | 33.0064
~~~9~~-5000~ | Plant Summary: Net heat rate(LHV) | kJ/kWh | 11262.3555 | 10906.9912
~~~10~~-5000~ | Plant Summary: Net fuel/energy input(LHV) | kW | 309123.0938 | 273598.1875
~~~11~~-5000~ | Plant Summary: Net process heat output | kW | 0 | 0
~~~12~~-5000~ | Plant Summary: CHP efficiency | % | 31.9649 | 33.0064
~~~13~~-5000~ | Plant Summary: PURPA efficiency | % | 31.9649 | 33.0064
~~~17~~-5000~ | Plant Summary: Net electric efficiency(HHV) | % | 28.9397 | 30.3664
~~~18~~-5000~ | Plant Summary: Net heat rate(HHV) | kJ/kWh | 12439.6396 | 11855.2061
~~~19~~-5000~ | Plant Summary: Net fuel/energy input(HHV) | kW | 341436.5625 | 297383.8438
~~~21~~-5000~ | Plant Summary: Energy chargeable to power | kW | 309123.0938 | 273598.1875
~~~22~~-5000~ | Plant Summary: Electric efficiency on chargeable energy | % | 31.9649 | 33.0064
~~~23~~-5000~ | Plant Summary: Water consumption | t/h | 1.1103 | 0.96474
~~~24~~-5000~ | Plant Summary: Water discharge | t/h | 0.96925 | 0.88415
~~~34~~-5000~ | Plant Summary: Net gaseous fuel input(LHV) | kW | 0 | 0
~~~35~~-5000~ | Plant Summary: Net liquid fuel input(LHV) | kW | 0 | 0
~~~36~~-5000~ | Plant Summary: Net solid fuel input(LHV) | kW | 309123.0938 | 273598.1875
~~~37~~-5000~ | Plant Summary: Net gaseous fuel input(HHV) | kW | 0 | 0
~~~38~~-5000~ | Plant Summary: Net liquid fuel input(HHV) | kW | 0 | 0
~~~39~~-5000~ | Plant Summary: Net solid fuel input(HHV) | kW | 341436.5625 | 297383.8438
~~~30~~-5000~ | Plant Summary: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~~~31~~-5000~ | Plant Summary: Fuel/Heat expense | USD/hr | 2714.4275 | 2402.4812
~~~32~~-5000~ | Plant Summary: Heat export price | USD/GJ | 4.7393 | 4.7393
~~~33~~-5000~ | Plant Summary: Process revenue | USD/hr | 0 | 0
~~~26~~-5000~ | Plant Summary: Revision date |  | 2021-02-26 | 2021-02-26
~~~49~~-5000~ | Plant Summary: Total for costed components + linked files | USD | 24926490 | 23589240
~~~50~~-5000~ | Plant Summary: Total incl. soft cost allowance | USD | 32036946 | 30319896
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL: Operating Hours per Year |  | 8100 | 8100
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~1~~~-8000~ | FINANCIAL: Annual Electricity Export [E6 kWh] |  | 800.368 | 731.4688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~2~~~-8000~ | FINANCIAL: Annual Heat Export | TJ | 0 | 0
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~3~~~-8000~ | FINANCIAL: Annual Fuel LHV Import | TJ | 9014.0293 | 7978.123
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~18~~~-8000~ | FINANCIAL: Annual Water Import | 10^6 l | 9.0971 | 7.9047
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL: Annual CO2 Emission | ktonne | 850.7756 | 741.007
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL: Total Investment | kUSD | 32036.9453 | 30319.8965
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL: Specific Investment (Estimated plant specific cost) | USD/kW | 324.2249 | 335.7507
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~6~~~-8000~ | FINANCIAL: Cumulative Net Cash Flow | kUSD | 442153.9688 | 409279.0938
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~5~~~-8000~ | FINANCIAL: Initial Equity | kUSD | 9611.084 | 9095.9688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~10~~~-8000~ | FINANCIAL: Internal Rate of Return on Investment (ROI) | % | 58.447 | 57.317
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~8~~~-8000~ | FINANCIAL: Internal Rate of Return on Equity (ROE) | % | 170.2605 | 166.508
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL: Years for Equity Payback |  | 0.59818 | 0.61193
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~9~~~-8000~ | FINANCIAL: Net Present Value | kUSD | 228323.7812 | 211113.2344
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL: Break-even electricity price | USD/kWh | 0.03486 | 0.034507
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~12~~~-8000~ | FINANCIAL: Break-even fuel LHV price | USD/GJ | 5.1153 | 5.2349
70¦82¦86¦87¦85¦72¦83¦~4~101~~~-8000~ | PEACE Cost Report: Sum of Costs for Equipment and PEACE Components | USD | 24926490 | 23589240
70¦82¦86¦87¦85¦72¦83¦~4~102~~~-8000~ | PEACE Cost Report: Sum of User-defined Costs | USD | 0 | 0
70¦82¦86¦87¦85¦72¦83¦~4~103~~~-8000~ | PEACE Cost Report: Sum of PEACE Components, Linked Files, and User-defined Costs (Contractor's Internal Cost) | USD | 24926490 | 23589240
70¦82¦86¦87¦85¦72¦83¦~4~104~~~-8000~ | PEACE Cost Report: Contractor's Soft & Miscellaneous Costs | USD | 4867072 | 4607624
70¦82¦86¦87¦85¦72¦83¦~4~105~~~-8000~ | PEACE Cost Report: Contractor's Price | USD | 29793562 | 28196864
70¦82¦86¦87¦85¦72¦83¦~4~107~~~-8000~ | PEACE Cost Report: Total - Owner's Cost* | USD | 32036946 | 30319896
~1~16~~4100~-5003~ | Generator / Motor Power: ST Assembly [1] generator power | kW | 110027.0938 | 99960.1641
~4~7~144~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux | kW | 989.8578 | 864.7477
~4~42~113~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux | kW | 0 | 0
~4~12~139~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux | kW | 429.9547 | 321.2974
~4~52~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [52] : aux | kW | 1165.7252 | 841.8731
~4~72~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux | kW | 281.2412 | 232.0762
~4~81~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux | kW | 577.0046 | 475.9778
~4~85~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux | kW | 281.2412 | 232.0762
~4~9~65~~-5003~ | Generator / Motor Power: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux | kW | 577.0046 | 475.9778
~4~27~168~~-5003~ | Generator / Motor Power: General Pump [27] - CWP-1 | kW | 938.1762 | 856.7526
~4~35~168~~-5003~ | Generator / Motor Power: General Pump [35] - BFP-C | kW | 0 | 0
~4~45~168~~-5003~ | Generator / Motor Power: General Pump [45] - CP | kW | 101.2423 | 92.3548
~4~50~168~~-5003~ | Generator / Motor Power: General Pump [50] - BFP-B | kW | 1527.5677 | 1348.0876
~4~59~168~~-5003~ | Generator / Motor Power: General Pump [59] - BFP-A | kW | 1527.5679 | 1348.0878
~4~6~168~~-5003~ | Generator / Motor Power: General Pump [6] - CWP-2 | kW | 938.1762 | 856.7526
~4~~~4101~-5003~ | Generator / Motor Power: ST Assembly [1] steam turbine auxiliary | kW | 231.0569 | 209.9163
~4~~~2000~-5003~ | Generator / Motor Power: Specified total misc. auxiliary | kW | 1100.271 | 999.6016
~4~~~2001~-5003~ | Generator / Motor Power: Transformer losses | kW | 550.1355 | 499.8008
~~~14~~-5000~ | Generator / Motor Power: Plant auxiliary | kW | 10666.0879 | 9155.5791
93¦~10~3~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer | kW | 309123.0938 | 273598.1875
91¦~10~1~1~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal heat transfer multiplier |  | 1 | 1
82¦71¦~10~5~10~1~-7000~ | Energy Inflow: Fuel Source [10] - Coal status |  | Charged as Fuel(LHV) | Charged as Fuel(LHV)
93¦~8~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer | kW | 0 | 0
91¦~8~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~8~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [8] - PA #1 status |  | Ignored | Ignored
93¦~11~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer | kW | 0 | 0
91¦~11~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 heat transfer multiplier |  | 1 | 1
82¦71¦~11~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [11] - SA #1 status |  | Ignored | Ignored
93¦~80~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer | kW | 0 | 0
91¦~80~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~80~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [80] - PA #2 status |  | Ignored | Ignored
93¦~84~3~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer | kW | 0 | 0
91¦~84~1~1~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 heat transfer multiplier |  | 1 | 1
82¦71¦~84~5~10~1~-7000~ | Energy Inflow: Gas/Air Source [84] - SA #2 status |  | Ignored | Ignored
93¦~44~3~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer | kW | 19.4543 | 16.9043
91¦~44~1~1~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~1~-7000~ | Energy Inflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~3~3~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer | kW | 514765.125 | 439315.6562
91¦~3~1~1~1~-7000~ | Energy Inflow: Water Source [3] - Intake heat transfer multiplier |  | 1 | 1
82¦71¦~3~5~10~1~-7000~ | Energy Inflow: Water Source [3] - Intake status |  | Ignored | Ignored
93¦~44~3~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer | kW | 0 | 0
91¦~44~1~1~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] heat transfer multiplier |  | 1 | 1
82¦71¦~44~5~10~2~-7000~ | Energy Outflow: Makeup / Blowdown [44] status |  | Ignored | Ignored
93¦~51~3~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer | kW | 692253.4375 | 601425.8125
91¦~51~1~1~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall heat transfer multiplier |  | 1 | 1
82¦71¦~51~5~10~2~-7000~ | Energy Outflow: Water Sink [51] - Outfall status |  | Ignored | Ignored
93¦~16~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [16] shaft power | kW | 30338.1348 | 27571.6953
93¦~17~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [17] shaft power | kW | 9286.5107 | 8772.8965
93¦~18~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [18] shaft power | kW | 21973.248 | 19738.8516
93¦~19~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [19] shaft power | kW | 2657.5557 | 2423.5625
93¦~20~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [20] shaft power | kW | 14690.1602 | 13379.1855
93¦~36~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [36] shaft power | kW | 6641.1538 | 6020.9575
93¦~37~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [37] shaft power | kW | 13977.8457 | 12715.1357
93¦~39~3~1~3~-7000~ | Power Device: ST Assembly [1]: ST Group [39] shaft power | kW | 12019.8828 | 10769.3164
93¦~7~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux power | kW | 989.8578 | 864.7477
91¦~7~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux multiplier |  | 1 | 1
82¦71¦~7~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Circulating Fluidized Bed [7] : aux status |  | power consumer | power consumer
93¦~42~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux power | kW | 0 | 0
91¦~42~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux multiplier |  | 1 | 1
82¦71¦~42~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Economiser (PCE) [42] - ECO : aux status |  | power consumer | power consumer
93¦~12~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux power | kW | 429.9547 | 321.2974
91¦~12~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux multiplier |  | 1 | 1
82¦71¦~12~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : aux status |  | power consumer | power consumer
93¦~52~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux power | kW | 1165.7252 | 841.8731
91¦~52~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux multiplier |  | 1 | 1
82¦71¦~52~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [52] : aux status |  | power consumer | power consumer
93¦~72~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux power | kW | 281.2412 | 232.0762
91¦~72~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~72~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [72] - PA Fan #1 : aux status |  | power consumer | power consumer
93¦~81~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux power | kW | 577.0046 | 475.9778
91¦~81~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~81~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [81] - SA Fan #2 : aux status |  | power consumer | power consumer
93¦~85~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux power | kW | 281.2412 | 232.0762
91¦~85~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux multiplier |  | 1 | 1
82¦71¦~85~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [85] - PA Fan #2 : aux status |  | power consumer | power consumer
93¦~9~3~2~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux power | kW | 577.0046 | 475.9778
91¦~9~1~1~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux multiplier |  | 1 | 1
82¦71¦~9~5~10~4~-7000~ | Auxiliary Device: Boiler Assembly [1]: Fan [9] - SA Fan #1 : aux status |  | power consumer | power consumer
93¦~27~3~2~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 power | kW | 938.1762 | 856.7526
91¦~27~1~1~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 multiplier |  | 1 | 1
82¦71¦~27~5~10~4~-7000~ | Auxiliary Device: General Pump [27] - CWP-1 status |  | power consumer | power consumer
93¦~35~3~2~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C power | kW | 0 | 0
91¦~35~1~1~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C multiplier |  | 1 | 1
82¦71¦~35~5~10~4~-7000~ | Auxiliary Device: General Pump [35] - BFP-C status |  | power consumer | power consumer
93¦~45~3~2~4~-7000~ | Auxiliary Device: General Pump [45] - CP power | kW | 101.2423 | 92.3548
91¦~45~1~1~4~-7000~ | Auxiliary Device: General Pump [45] - CP multiplier |  | 1 | 1
82¦71¦~45~5~10~4~-7000~ | Auxiliary Device: General Pump [45] - CP status |  | power consumer | power consumer
93¦~50~3~2~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B power | kW | 1527.5677 | 1348.0876
91¦~50~1~1~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B multiplier |  | 1 | 1
82¦71¦~50~5~10~4~-7000~ | Auxiliary Device: General Pump [50] - BFP-B status |  | power consumer | power consumer
93¦~59~3~2~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A power | kW | 1527.5679 | 1348.0878
91¦~59~1~1~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A multiplier |  | 1 | 1
82¦71¦~59~5~10~4~-7000~ | Auxiliary Device: General Pump [59] - BFP-A status |  | power consumer | power consumer
93¦~6~3~2~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 power | kW | 938.1762 | 856.7526
91¦~6~1~1~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 multiplier |  | 1 | 1
82¦71¦~6~5~10~4~-7000~ | Auxiliary Device: General Pump [6] - CWP-2 status |  | power consumer | power consumer
93¦~7~4~57~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by waterwall | t/h | 310.16 | 282.928
93¦~7~4~296~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam produced by evaporator wing wall | t/h | 77.54 | 70.732
93¦~7~4~54~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam pressure | bar | 108.5314 | 105.0868
93¦~7~4~55~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam temperature | C | 317.0735 | 314.6673
93¦~7~4~56~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam enthalpy | kJ/kg | 2709.3022 | 2715.9788
93¦~7~4~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Furnace temperature | C | 893.9999 | 893.9999
93¦~7~4~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Waterwall mean water temperature | C | 317.0735 | 314.6673
93¦~7~4~19~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | % | 20 | 25
82¦71¦~7~6~1~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas N2 mol% | % | 65.91 | 66.0719
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas O2 mol% | % | 2.9438 | 3.541
93¦~7~4~104~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas CO2 mol% | % | 13.2498 | 13.9605
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas H2O mol% | % | 17.1003 | 15.6285
93¦~7~4~191~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas SO2 mol% | % | 0.0031714 | 0.0033418
82¦71¦~7~6~2~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Flue gas Ar mol% | % | 0.79282 | 0.79472
93¦~7~4~289~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total heat transfer to water/steam side | kW | 176073.375 | 162777.9062
93¦~7~4~5~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to waterwall | kW | 116337.5469 | 107399.7734
93¦~7~4~297~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to evaporator wing wall | kW | 29084.3867 | 26849.9434
93¦~7~4~7~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX2 wing wall | kW | 15375.0781 | 13853.2969
93¦~7~4~8~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat transfer to HX3 Cyclone wall | kW | 15276.3691 | 14674.9004
82¦71¦~7~6~3~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon in ash | kW | 2705.6272 | 2356.6296
93¦~7~4~13~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat losses | kW | 3521.4675 | 3255.5579
93¦~7~4~321~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash (bed drain) sensible heat | kW | 517.7778 | 456.2106
93¦~7~4~322~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash sensible heat | kW | 1208.1481 | 1064.4912
93¦~7~4~43~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat absorption rate | kW/m^2 | 97.8249 | 98.6417
93¦~7~4~41~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Heat release rate | kW/m^2 | 183.6435 | 176.2226
93¦~7~4~42~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Volumetric fuel release rate | kW/m^3 | 126.7684 | 130.9036
93¦~7~4~305~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : SO2 removal efficiency | % | 90 | 90
93¦~7~4~302~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Sulfur removed | t/h | 0.16514 | 0.14383
93¦~7~4~301~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reagent consumption | t/h | 0.60102 | 0.52347
93¦~7~4~339~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel mass flow | t/h | 73.3954 | 63.928
82¦71¦~7~6~4~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel consumption per day | tonne/day | 1761.4883 | 1534.2719
93¦~7~4~17~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (LHV) | kW | 309123.0938 | 273607.7812
93¦~7~4~49~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel input (HHV) | kW | 341436.5625 | 297394.2812
93¦~7~4~28~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel delivery power | kW | 733.9534 | 639.2799
93¦~7~4~246~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Ash handling power | kW | 255.9044 | 225.4678
93¦~7~4~47~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Forced circulation pump power | kW | 0 | 0
93¦~7~4~16~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fuel ash flow | t/h | 4.8514 | 4.2256
93¦~7~4~24~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Unburnt carbon flow | t/h | 0.28881 | 0.25156
93¦~7~4~312~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solids added to ash due to reagent addition | t/h | 0.75737 | 0.65965
93¦~7~4~326~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Inert bed material feed | t/h | 0.5 | 0.5
93¦~7~4~327~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Total solid produced from combustion | t/h | 6.3976 | 5.6367
93¦~7~4~314~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Bottom ash flow | t/h | 1.9193 | 1.691
93¦~7~4~317~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Fly ash flow | t/h | 4.4783 | 3.9457
91¦~7~1~150~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Reference O2 content | % | 6 | 6
93¦~7~4~103~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas O2 content | % | 2.9438 | 3.541
93¦~7~4~105~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Exit flue gas H2O content | % | 17.1003 | 15.6285
93¦~7~4~431~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg from combustion | kg/hr | 0 | 0
93¦~7~4~432~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Hg in exit gas | kg/hr | 0 | 0
93¦~7~4~193~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : HCl in exit gas | kg/hr | 0 | 0
93¦~7~4~194~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx production | kg/hr | 0 | 0
93¦~7~4~333~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas | ppmv | 0 | 0
93¦~7~4~336~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx mass concentration in exit flue gas | ppm | 0 | 0
93¦~7~4~334~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, actual O2%) | ppmvd | 0 | 0
93¦~7~4~335~~-144~ | Boiler Assembly [1]: Circulating Fluidized Bed [7] : NOx volume concentration in exit flue gas (dry base, reference O2%) | ppmvd | 0 | 0
~25~6~1~~-27~ | Deaerator [25] - DAER : Mode |  | TD | TD
~25~6~3~~-27~ | Deaerator [25] - DAER : DA pressure specification |  | Specified by user | Specified by user
~25~4~4~~-27~ | Deaerator [25] - DAER : Operating pressure | bar | 5.27 | 5.27
~25~4~5~~-27~ | Deaerator [25] - DAER : Temperature | C | 153.8281 | 153.8281
93¦~25~4~7~~-27~ | Deaerator [25] - DAER : FW inlet pressure | bar | 5.3108 | 5.3108
93¦~25~4~8~~-27~ | Deaerator [25] - DAER : FW inlet temperature | C | 150.0223 | 150.0223
93¦~25~4~28~~-27~ | Deaerator [25] - DAER : FW inlet enthalpy | kJ/kg | 632.2855 | 632.2855
93¦~25~4~9~~-27~ | Deaerator [25] - DAER : FW inlet mass flow | t/h | 358.765 | 326.891
93¦~25~4~23~~-27~ | Deaerator [25] - DAER : Additional water head at inlet | bar | 0.04083 | 0.04083
93¦~25~4~10~~-27~ | Deaerator [25] - DAER : Heating stream pressure | bar | 6.297 | 6.1192
93¦~25~4~12~~-27~ | Deaerator [25] - DAER : Heating stream temperature | C | 252.8501 | 253.113
93¦~25~4~11~~-27~ | Deaerator [25] - DAER : Heating stream enthalpy | kJ/kg | 2962.6248 | 2963.7898
93¦~25~4~13~~-27~ | Deaerator [25] - DAER : Heating stream mass flow | t/h | 1.5596 | 1.4286
93¦~25~4~17~~-27~ | Deaerator [25] - DAER : Flash in pressure | bar | 16.894 | 16.894
93¦~25~4~18~~-27~ | Deaerator [25] - DAER : Flash in temperature | C | 164.6357 | 164.499
93¦~25~4~19~~-27~ | Deaerator [25] - DAER : Flash in enthalpy | kJ/kg | 696.2255 | 695.631
93¦~25~4~20~~-27~ | Deaerator [25] - DAER : Flash in mass flow | t/h | 48.855 | 44.6733
93¦~25~4~14~~-27~ | Deaerator [25] - DAER : FW outlet pressure | bar | 3.4473 | 3.4473
93¦~25~4~15~~-27~ | Deaerator [25] - DAER : FW outlet temperature | C | 138.3289 | 138.3289
93¦~25~4~29~~-27~ | Deaerator [25] - DAER : FW outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~25~4~16~~-27~ | Deaerator [25] - DAER : FW outlet mass flow | t/h | 409.1796 | 372.9929
93¦~25~4~24~~-27~ | Deaerator [25] - DAER : Additional water head at outlet | bar | 0.038309 | 0.038309
~68~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Temperature drop | C | 23.9992 | 23.9992
~68~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet pressure | bar | 96.1447 | 93.0932
~68~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet temperature | C | 460.0024 | 460.0027
~68~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet mass flow | t/h | 397.9526 | 362.8685
~68~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Inlet enthalpy | kJ/kg | 3275.2939 | 3279.822
~68~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet pressure | bar | 96.1447 | 93.0932
~68~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet temperature | C | 436.0033 | 436.0036
~68~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet mass flow | t/h | 408.2104 | 372.1087
~68~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Outlet enthalpy | kJ/kg | 3209.927 | 3215.0935
~68~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray mass flow | t/h | 10.2577 | 9.2402
~68~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [68] : Spray water enthalpy | kJ/kg | 673.9968 | 673.179
~78~3~22~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Temperature drop | C | 22.5989 | 22.5991
~78~3~3~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet pressure | bar | 98.0676 | 94.9551
~78~3~4~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet temperature | C | 434.1031 | 434.1035
~78~3~5~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet mass flow | t/h | 387.7 | 353.66
~78~3~6~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Inlet enthalpy | kJ/kg | 3201.3213 | 3206.6785
~78~3~11~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet pressure | bar | 98.0676 | 94.9551
~78~3~12~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet temperature | C | 411.5042 | 411.5043
~78~3~13~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet mass flow | t/h | 397.9526 | 362.8685
~78~3~14~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Outlet enthalpy | kJ/kg | 3136.2087 | 3142.3862
~78~3~9~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray mass flow | t/h | 10.2526 | 9.2085
~78~3~10~~-19~ | Boiler Assembly [1]: Desuperheater [78] : Spray water enthalpy | kJ/kg | 673.9968 | 673.179
82¦71¦~2~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~2~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~2~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~2~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 : Heat loss | kW | 31.258 | 25.9397
82¦71¦~48~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Mode |  | ED | ED
73¦74¦93¦~48~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~48~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Temperature drop | C | 1.2 | 1.2
73¦74¦93¦~48~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out : Heat loss | kW | 191.4111 | 156.2902
82¦71¦~65~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Mode |  | ED | ED
73¦74¦93¦~65~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~65~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Temperature drop | C | 1 | 1
73¦74¦93¦~65~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 : Heat loss | kW | 32.5433 | 27.0058
82¦71¦~82~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~82~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~82~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~82~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [82] - PA Duct In #2 : Heat loss | kW | 32.5433 | 27.0058
82¦71¦~83~8~2~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Mode |  | ED | ED
73¦74¦93¦~83~4~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Pressure drop | millibar | 4.9813 | 4.9813
82¦71¦~83~8~1~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Temperature drop | C | 1 | 1
73¦74¦93¦~83~4~5~~-122~ | Boiler Assembly [1]: Duct - Classic [83] - SA Duct In #2 : Heat loss | kW | 31.258 | 25.9397
~42~10~1~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Mode |  | TD | TD
~42~1~35~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet mass flow | t/h | 388.6693 | 354.5441
~42~1~36~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet pressure | bar | 118.2992 | 114.5446
~42~1~38~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet enthalpy | kJ/kg | 974.4664 | 974.3673
~42~1~37~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water inlet temperature | C | 226.1392 | 226.1398
~42~3~12~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit mass flow | t/h | 388.6693 | 354.5441
~42~3~13~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit pressure | bar | 108.5314 | 105.0868
~42~3~14~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit temperature | C | 303 | 301.2446
~42~3~15~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water exit enthalpy | kJ/kg | 1359.2157 | 1349.5137
~42~1~24~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas mass flow | t/h | 516.8243 | 431.4653
~42~1~105~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Flyash mass flow | t/h | 4.4783 | 3.9456
~42~1~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas inlet temperature | C | 524.1158 | 494.2766
~42~3~3~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas exit temperature | C | 281.8529 | 231.1398
~42~3~20~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Dew point temperature | C | 56.5243 | 54.6383
~42~3~10~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water flow from air | t/h | 0 | 0
~42~3~11~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Condensed water enthalpy from air | kJ/kg | 1246.3896 | 995.5626
~42~3~17~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in non-condensing section | kW | 41539.5898 | 36946.6562
~42~3~18~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat transfer in condensing section | kW | 0 | 0
~42~3~19~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Total heat transfer to liquid | kW | 41539.5898 | 36946.6562
~42~3~26~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Heat loss | kW | 311.5469 | 277.0999
~42~1~16~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Radiant heat influx | kW | 0 | 0
~42~3~29~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Gas side pressure drop | millibar | 2.4907 | 2.4907
~42~3~28~~-113~ | Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Water side pressure drop | bar | 9.7678 | 9.4578
89¦~12~3~6~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate collection efficiency | % | 99.782 | 99.7996
89¦~12~3~5~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Electricity consumption | kW | 429.9547 | 321.2973
91¦~12~1~81~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas pressure | bar | 0.9749 | 0.9749
91¦~12~1~82~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas temperature | C | 143.6583 | 90.6411
91¦~12~1~84~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas volume flow | m^3/hr | 641553.5625 | 462831.9688
91¦~12~1~83~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas mass flow | t/h | 516.8241 | 431.4364
91¦~12~1~93~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate flow | t/h | 4.4783 | 3.9456
89¦~12~3~3~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Particulate removal | t/h | 4.4686 | 3.9377
91¦~12~1~95~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate flow | t/h | 0.0097615 | 0.007906
89¦~12~3~8~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per energy input | ng/J | 3643.4297 | 3685.5325
89¦~12~3~25~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Inlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 11469.1475 | 12476.376
89¦~12~3~7~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per energy input | ng/J | 7.9416 | 7.3849
89¦~12~3~24~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Outlet particulate load per gas flow @ 6% O2, dry | mg/Nm^3 | 24.9994 | 24.9994
89¦~12~3~4~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Pressure drop | millibar | 8.0946 | 8.0946
89¦~12~3~97~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Heat loss | kW | 191.467 | 156.3337
89¦~12~3~2~~-139~ | Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP : Flue gas velocity | m/s | 1.211 | 1.2013
82¦71¦~9~5~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~9~5~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~9~1~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of existing units |  | 1 | 1
93¦~9~3~20~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Number of operating units |  | 1 | 1
93¦~9~3~19~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Total shaft power | kW | 554.769 | 457.019
93¦~9~3~1~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Shaft power per unit | kW | 554.769 | 457.019
93¦~9~3~2~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan compression power per unit | kW | 549.2214 | 452.4488
93¦~9~3~3~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan inlet volume flow per unit | m^3/s | 27.8128 | 22.9125
93¦~9~3~4~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~9~3~5~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~9~3~6~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~9~3~11~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~9~3~8~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Current RPM |  | 1200 | 1200
93¦~9~3~9~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical loss per unit | kW | 5.5477 | 4.5702
93¦~9~3~10~~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~9~6~1~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Mode |  | Design | Design
91¦~9~1~7~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate power | kW | 605.8548 | 499.7766
91¦~9~1~19~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate efficiency | % | 96.1656 | 96.0367
91¦~9~1~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~9~2~8~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~9~7~2~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electricity consumption | kW | 577.0046 | 475.9778
93¦~9~7~6~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Shaft power | kW | 554.769 | 457.019
93¦~9~7~4~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Efficiency | % | 96.1464 | 96.0169
93¦~9~7~3~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Electrical loss | kW | 22.2355 | 18.9588
89¦~9~3~5~2~-65~ | Boiler Assembly [1]: Fan [9] - SA Fan #1 : Motor: Nameplate motor shaft power | kW | 582.5074 | 479.8699
82¦71¦~52~5~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~52~5~20~~-65~ | Boiler Assembly [1]: Fan [52] : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~52~1~19~~-65~ | Boiler Assembly [1]: Fan [52] : Number of existing units |  | 1 | 1
93¦~52~3~20~~-65~ | Boiler Assembly [1]: Fan [52] : Number of operating units |  | 1 | 1
93¦~52~3~19~~-65~ | Boiler Assembly [1]: Fan [52] : Total shaft power | kW | 1125.5491 | 811.3737
93¦~52~3~1~~-65~ | Boiler Assembly [1]: Fan [52] : Shaft power per unit | kW | 1125.5491 | 811.3737
93¦~52~3~2~~-65~ | Boiler Assembly [1]: Fan [52] : Fan compression power per unit | kW | 1114.2936 | 803.2599
93¦~52~3~3~~-65~ | Boiler Assembly [1]: Fan [52] : Fan inlet volume flow per unit | m^3/s | 179.5939 | 129.454
93¦~52~3~4~~-65~ | Boiler Assembly [1]: Fan [52] : Fan pressure rise (before control damper) | millibar | 50.5503 | 50.5503
93¦~52~3~5~~-65~ | Boiler Assembly [1]: Fan [52] : Fan overall pressure rise | millibar | 50.5503 | 50.5503
93¦~52~3~6~~-65~ | Boiler Assembly [1]: Fan [52] : Fan isentropic efficiency | % | 80 | 80
93¦~52~3~11~~-65~ | Boiler Assembly [1]: Fan [52] : Fan polytropic efficiency | % | 80.1304 | 80.1268
93¦~52~3~8~~-65~ | Boiler Assembly [1]: Fan [52] : Current RPM |  | 1200 | 1200
93¦~52~3~9~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical loss per unit | kW | 11.2555 | 8.1137
93¦~52~3~10~~-65~ | Boiler Assembly [1]: Fan [52] : Mechanical efficiency | % | 99 | 99
82¦71¦~52~6~1~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Mode |  | Design | Design
91¦~52~1~7~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate power | kW | 1224.0114 | 883.9667
91¦~52~1~19~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate efficiency | % | 96.5707 | 96.3952
91¦~52~1~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~52~2~8~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Number of operating units |  | 1 | 1
93¦~52~7~2~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electricity consumption | kW | 1165.7251 | 841.8731
93¦~52~7~6~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Shaft power | kW | 1125.5491 | 811.3737
93¦~52~7~4~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Efficiency | % | 96.5536 | 96.3772
93¦~52~7~3~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Electrical loss | kW | 40.176 | 30.4994
89¦~52~3~5~2~-65~ | Boiler Assembly [1]: Fan [52] : Motor: Nameplate motor shaft power | kW | 1181.8264 | 851.9422
82¦71¦~72~5~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~72~5~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~72~1~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of existing units |  | 1 | 1
93¦~72~3~20~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Number of operating units |  | 1 | 1
93¦~72~3~19~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Total shaft power | kW | 268.9126 | 221.5198
93¦~72~3~1~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Shaft power per unit | kW | 268.9126 | 221.5198
93¦~72~3~2~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan compression power per unit | kW | 266.2235 | 219.3046
93¦~72~3~3~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan inlet volume flow per unit | m^3/s | 26.7221 | 22.014
93¦~72~3~4~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~72~3~5~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~72~3~6~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan isentropic efficiency | % | 80 | 80
93¦~72~3~11~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~72~3~8~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Current RPM |  | 1200 | 1200
93¦~72~3~9~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical loss per unit | kW | 2.6891 | 2.2152
93¦~72~3~10~~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Mechanical efficiency | % | 99 | 99
82¦71¦~72~6~1~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Mode |  | Design | Design
91¦~72~1~7~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate power | kW | 295.3033 | 243.68
91¦~72~1~19~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate efficiency | % | 95.6382 | 95.474
91¦~72~1~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~72~2~8~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Number of operating units |  | 1 | 1
93¦~72~7~2~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electricity consumption | kW | 281.2412 | 232.0762
93¦~72~7~6~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Shaft power | kW | 268.9126 | 221.5198
93¦~72~7~4~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Efficiency | % | 95.6164 | 95.4513
93¦~72~7~3~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Electrical loss | kW | 12.3286 | 10.5564
89¦~72~3~5~2~-65~ | Boiler Assembly [1]: Fan [72] - PA Fan #1 : Motor: Nameplate motor shaft power | kW | 282.3582 | 232.5958
82¦71¦~81~5~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~81~5~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~81~1~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of existing units |  | 1 | 1
93¦~81~3~20~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Number of operating units |  | 1 | 1
93¦~81~3~19~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Total shaft power | kW | 554.769 | 457.019
93¦~81~3~1~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Shaft power per unit | kW | 554.769 | 457.019
93¦~81~3~2~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan compression power per unit | kW | 549.2214 | 452.4488
93¦~81~3~3~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan inlet volume flow per unit | m^3/s | 27.8128 | 22.9125
93¦~81~3~4~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan pressure rise (before control damper) | millibar | 166.8743 | 166.8743
93¦~81~3~5~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan overall pressure rise | millibar | 166.8743 | 166.8743
93¦~81~3~6~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~81~3~11~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Fan polytropic efficiency | % | 80.4257 | 80.4255
93¦~81~3~8~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Current RPM |  | 1200 | 1200
93¦~81~3~9~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical loss per unit | kW | 5.5477 | 4.5702
93¦~81~3~10~~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~81~6~1~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Mode |  | Design | Design
91¦~81~1~7~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate power | kW | 605.8548 | 499.7766
91¦~81~1~19~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate efficiency | % | 96.1656 | 96.0367
91¦~81~1~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~81~2~8~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~81~7~2~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electricity consumption | kW | 577.0046 | 475.9778
93¦~81~7~6~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Shaft power | kW | 554.769 | 457.019
93¦~81~7~4~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Efficiency | % | 96.1464 | 96.0169
93¦~81~7~3~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Electrical loss | kW | 22.2355 | 18.9588
89¦~81~3~5~2~-65~ | Boiler Assembly [1]: Fan [81] - SA Fan #2 : Motor: Nameplate motor shaft power | kW | 582.5074 | 479.8699
82¦71¦~85~5~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mode |  | TD - Fixed RPM | TD - Fixed RPM
82¦71¦~85~5~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Actual operating mode |  | TD - Fixed RPM | TD - Fixed RPM
91¦~85~1~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of existing units |  | 1 | 1
93¦~85~3~20~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Number of operating units |  | 1 | 1
93¦~85~3~19~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Total shaft power | kW | 268.9126 | 221.5198
93¦~85~3~1~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Shaft power per unit | kW | 268.9126 | 221.5198
93¦~85~3~2~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan compression power per unit | kW | 266.2235 | 219.3046
93¦~85~3~3~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan inlet volume flow per unit | m^3/s | 26.7221 | 22.014
93¦~85~3~4~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan pressure rise (before control damper) | millibar | 81.9056 | 81.9056
93¦~85~3~5~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan overall pressure rise | millibar | 81.9056 | 81.9056
93¦~85~3~6~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan isentropic efficiency | % | 80 | 80
93¦~85~3~11~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Fan polytropic efficiency | % | 80.2169 | 80.22
93¦~85~3~8~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Current RPM |  | 1200 | 1200
93¦~85~3~9~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical loss per unit | kW | 2.6891 | 2.2152
93¦~85~3~10~~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Mechanical efficiency | % | 99 | 99
82¦71¦~85~6~1~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Mode |  | Design | Design
91¦~85~1~7~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate power | kW | 295.3033 | 243.68
91¦~85~1~19~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate efficiency | % | 95.6382 | 95.474
91¦~85~1~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate / Design point load |  | 1.05 | 1.05
76¦~85~2~8~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Number of operating units |  | 1 | 1
93¦~85~7~2~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electricity consumption | kW | 281.2412 | 232.0762
93¦~85~7~6~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Shaft power | kW | 268.9126 | 221.5198
93¦~85~7~4~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Efficiency | % | 95.6164 | 95.4513
93¦~85~7~3~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Electrical loss | kW | 12.3286 | 10.5564
89¦~85~3~5~2~-65~ | Boiler Assembly [1]: Fan [85] - PA Fan #2 : Motor: Nameplate motor shaft power | kW | 282.3582 | 232.5958
91¦~21~1~13~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell pressure | bar | 0.39216 | 0.38108
91¦~21~1~71~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Saturation temperature | C | 75.3816 | 74.6966
89¦~21~3~7~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer | kW | 11224.3428 | 9964.7432
82¦71¦~21~5~1~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in condensing section | kW | 9506.7051 | 8448.71
89¦~21~3~6~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Heat transfer in drain cooler | kW | 1717.6375 | 1516.0331
91¦~21~1~101~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Feedwater temperature rise (overall) | C | 26.9283 | 26.2385
82¦71¦~21~5~2~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Terminal difference | C | 2 | 2
82¦71¦~21~5~3~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Drain cooler approach | C | 5.6 | 5.6
91¦~21~1~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~21~1~82~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Nameplate steam pressure | bar | 0 | 0
89¦~21~3~52~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell length | m | 0 | 0
89¦~21~3~53~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Shell inner diameter | m | 0 | 0
89¦~21~3~56~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall length | m | 0 | 0
89¦~21~3~27~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Overall outer diameter | m | 0 | 0
89¦~21~3~45~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total dry weight | kg | 0 | 0
89¦~21~3~57~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~21~5~5~~-102~ | Feedwater Heater (PCE) [21] - LPH-7 : Total estimated installed cost | USD | 0 | 0
91¦~22~1~13~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell pressure | bar | 1.3137 | 1.2767
91¦~22~1~71~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Saturation temperature | C | 107.417 | 106.5803
89¦~22~3~7~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer | kW | 13418.8516 | 12166.4004
82¦71¦~22~5~1~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in condensing section | kW | 11821.7529 | 10710.04
89¦~22~3~6~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Heat transfer in drain cooler | kW | 1597.0977 | 1456.3602
91¦~22~1~101~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Feedwater temperature rise (overall) | C | 32.0362 | 31.8842
82¦71¦~22~5~2~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Terminal difference | C | 2 | 2
82¦71¦~22~5~3~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Drain cooler approach | C | 5.6 | 5.6
91¦~22~1~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~22~1~82~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Nameplate steam pressure | bar | 0 | 0
89¦~22~3~52~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell length | m | 0 | 0
89¦~22~3~53~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Shell inner diameter | m | 0 | 0
89¦~22~3~56~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall length | m | 0 | 0
89¦~22~3~27~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Overall outer diameter | m | 0 | 0
89¦~22~3~45~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total dry weight | kg | 0 | 0
89¦~22~3~57~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~22~5~5~~-102~ | Feedwater Heater (PCE) [22] - LPH-6 : Total estimated installed cost | USD | 0 | 0
91¦~23~1~13~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell pressure | bar | 2.1373 | 2.0769
91¦~23~1~71~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Saturation temperature | C | 122.3229 | 121.4086
89¦~23~3~7~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer | kW | 6286.4082 | 5696.2925
82¦71¦~23~5~1~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in condensing section | kW | 5902.043 | 5343.0137
89¦~23~3~6~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Heat transfer in drain cooler | kW | 384.3651 | 353.2784
91¦~23~1~101~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Feedwater temperature rise (overall) | C | 14.9028 | 14.8257
82¦71¦~23~5~2~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Terminal difference | C | 2 | 2
82¦71¦~23~5~3~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Drain cooler approach | C | 5.6 | 5.6
91¦~23~1~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~23~1~82~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Nameplate steam pressure | bar | 0 | 0
89¦~23~3~52~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell length | m | 0 | 0
89¦~23~3~53~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Shell inner diameter | m | 0 | 0
89¦~23~3~56~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall length | m | 0 | 0
89¦~23~3~27~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Overall outer diameter | m | 0 | 0
89¦~23~3~45~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total dry weight | kg | 0 | 0
89¦~23~3~57~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~23~5~5~~-102~ | Feedwater Heater (PCE) [23] - LPH-5 : Total estimated installed cost | USD | 0 | 0
91¦~24~1~13~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell pressure | bar | 5.3922 | 5.2395
91¦~24~1~71~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Saturation temperature | C | 154.7026 | 153.6069
89¦~24~3~7~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer | kW | 12643.4219 | 11872.5488
82¦71¦~24~5~1~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in condensing section | kW | 11362.7988 | 10663.9824
89¦~24~3~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in desuperheating section | kW | 616.6586 | 590.6871
89¦~24~3~6~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Heat transfer in drain cooler | kW | 663.9647 | 617.8793
91¦~24~1~101~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Feedwater temperature rise (overall) | C | 29.6672 | 30.5819
82¦71¦~24~5~2~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Terminal difference | C | 4.7026 | 3.6069
82¦71¦~24~5~3~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Drain cooler approach | C | 5.6 | 5.6
91¦~24~1~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~24~1~82~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Nameplate steam pressure | bar | 0 | 0
89¦~24~3~52~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell length | m | 0 | 0
89¦~24~3~53~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Shell inner diameter | m | 0 | 0
89¦~24~3~56~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall length | m | 0 | 0
89¦~24~3~27~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Overall outer diameter | m | 0 | 0
89¦~24~3~45~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total dry weight | kg | 0 | 0
89¦~24~3~57~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~24~5~5~~-102~ | Feedwater Heater (PCE) [24] - LPH-4 : Total estimated installed cost | USD | 0 | 0
91¦~32~1~13~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell pressure | bar | 16.894 | 16.894
91¦~32~1~71~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Saturation temperature | C | 204.01 | 204.01
89¦~32~3~7~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer | kW | 21750.9238 | 19906.2051
82¦71¦~32~5~1~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in condensing section | kW | 16685.2031 | 15278.1064
89¦~32~3~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in desuperheating section | kW | 2700.5259 | 2457.9729
89¦~32~3~6~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Heat transfer in drain cooler | kW | 2365.1956 | 2170.126
91¦~32~1~101~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Feedwater temperature rise (overall) | C | 46.123 | 46.2597
82¦71¦~32~5~2~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Terminal difference | C | -0.19001 | -0.19001
82¦71¦~32~5~3~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Drain cooler approach | C | 6.536 | 6.536
91¦~32~1~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total heat transfer area | m^2 | 363.941 | 363.941
91¦~32~1~82~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Nameplate steam pressure | bar | 17.4667 | 17.4667
89¦~32~3~52~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell length | m | 10.0793 | 10.0793
89¦~32~3~53~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Shell inner diameter | m | 0.94351 | 0.94351
89¦~32~3~56~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall length | m | 11.5465 | 11.5465
89¦~32~3~27~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Overall outer diameter | m | 0.96256 | 0.96256
89¦~32~3~45~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total dry weight | kg | 9076.585 | 9076.585
89¦~32~3~57~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total operating (wet) weight | kg | 10543.6572 | 10543.6572
82¦71¦~32~5~5~~-102~ | Feedwater Heater (PCE) [32] - HPH-2 : Total estimated installed cost | USD | 0 | 0
91¦~46~1~13~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell pressure | bar | 25.1632 | 25.1583
91¦~46~1~71~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Saturation temperature | C | 224.3029 | 224.2925
89¦~46~3~7~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer | kW | 11661.0791 | 10643.0107
82¦71¦~46~5~1~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in condensing section | kW | 9369.709 | 8547.4238
89¦~46~3~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in desuperheating section | kW | 1988.4463 | 1819.4714
89¦~46~3~6~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Heat transfer in drain cooler | kW | 302.9235 | 276.1151
91¦~46~1~101~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Feedwater temperature rise (overall) | C | 23.8913 | 23.8916
82¦71¦~46~5~2~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Terminal difference | C | -3.7971 | -3.8075
82¦71¦~46~5~3~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Drain cooler approach | C | 7.041 | 7.041
91¦~46~1~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~46~1~82~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Nameplate steam pressure | bar | 0 | 0
89¦~46~3~52~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell length | m | 0 | 0
89¦~46~3~53~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Shell inner diameter | m | 0 | 0
89¦~46~3~56~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall length | m | 0 | 0
89¦~46~3~27~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Overall outer diameter | m | 0 | 0
89¦~46~3~45~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total dry weight | kg | 0 | 0
89¦~46~3~57~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total operating (wet) weight | kg | 0 | 0
82¦71¦~46~5~5~~-102~ | Feedwater Heater (PCE) [46] - HPH-1 : Total estimated installed cost | USD | 0 | 0
93¦~10~3~1~~-24~ | Fuel Source [10] - Coal : Pressure | bar | 1.0124 | 1.0124
93¦~10~3~2~~-24~ | Fuel Source [10] - Coal : Temperature | C | 33 | 33
93¦~10~3~3~~-24~ | Fuel Source [10] - Coal : Enthalpy | kJ/kg | 15181.7617 | 15424.9033
93¦~10~3~4~~-24~ | Fuel Source [10] - Coal : Mass flow | t/h | 73.3954 | 63.9258
93¦~10~3~10~~-24~ | Fuel Source [10] - Coal : Energy flow (LHV) | kW | 309123.0938 | 273598.1875
93¦~10~3~11~~-24~ | Fuel Source [10] - Coal : Energy flow (HHV) | kW | 341436.5625 | 297383.8438
93¦~10~3~25~~-24~ | Fuel Source [10] - Coal : Fuel LHV price | USD/GJ | 2.4392 | 2.4392
93¦~10~3~26~~-24~ | Fuel Source [10] - Coal : Fuel expense | USD/hr | 2714.4275 | 2402.4812
~10~4~15~200~-24~ | Fuel Source [10] - Coal : Fuel name |  | Perf. Test WI sim | Perf. Test WI sim
~10~10~2~200~-24~ | Fuel Source [10] - Coal : Fuel type |  | Solid | Solid
~10~3~50~200~-24~ | Fuel Source [10] - Coal : LHV @ 25C | kJ/kg | 15162.0674 | 15407.5234
~10~3~49~200~-24~ | Fuel Source [10] - Coal : HHV @ 25C | kJ/kg | 16747 | 16747
~10~3~20~200~-24~ | Fuel Source [10] - Coal : Fuel supply temperature | C | 33 | 33
~10~10~3~200~-24~ | Fuel Source [10] - Coal : Total LHV + Sensible heat referenced to 25C | kJ/kg | 15181.7607 | 15424.9043
~10~10~4~200~-24~ | Fuel Source [10] - Coal : Total fuel enthalpy referenced to 0C | kJ/kg | 16839.0098 | 16828.3848
~10~3~42~200~-24~ | Fuel Source [10] - Coal : Weight % of C | % | 39.35 | 39.35
~10~3~43~200~-24~ | Fuel Source [10] - Coal : Weight % of H | % | 2.78 | 2.78
~10~3~48~200~-24~ | Fuel Source [10] - Coal : Weight % of O | % | 10.41 | 20.46
~10~3~44~200~-24~ | Fuel Source [10] - Coal : Weight % of N | % | 0.55 | 0.55
~10~3~46~200~-24~ | Fuel Source [10] - Coal : Weight % of S | % | 0.25 | 0.25
~10~3~41~200~-24~ | Fuel Source [10] - Coal : Weight % of Ar | % | 0 | 0
~10~3~45~200~-24~ | Fuel Source [10] - Coal : Weight % of Chlorine | % | 0 | 0
~10~3~47~200~-24~ | Fuel Source [10] - Coal : Weight % of Ash | % | 6.61 | 6.61
~10~3~30~200~-24~ | Fuel Source [10] - Coal : Weight % of Moisture | % | 40.05 | 30
~10~3~23~200~-24~ | Fuel Source [10] - Coal : Equivalent molecular weight |  | 6.9687 | 7.5583
93¦~8~3~1~~-1~ | Gas/Air Source [8] - PA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~8~3~2~~-1~ | Gas/Air Source [8] - PA #1 : Temperature | C | 32.1803 | 30.0002
93¦~8~3~3~~-1~ | Gas/Air Source [8] - PA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~8~3~4~~-1~ | Gas/Air Source [8] - PA #1 : Mass flow | t/h | 114.4249 | 94.8916
93¦~8~3~5~~-1~ | Gas/Air Source [8] - PA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~8~3~11~~-1~ | Gas/Air Source [8] - PA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~8~3~12~~-1~ | Gas/Air Source [8] - PA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~8~3~13~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~8~3~14~~-1~ | Gas/Air Source [8] - PA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~8~3~15~~-1~ | Gas/Air Source [8] - PA #1 : SO2 mole percent | % | 0 | 0
93¦~8~3~16~~-1~ | Gas/Air Source [8] - PA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~8~3~20~~-1~ | Gas/Air Source [8] - PA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~8~3~21~~-1~ | Gas/Air Source [8] - PA #1 : CO2 mass flow | t/h | 0.051746 | 0.042873
93¦~11~3~1~~-1~ | Gas/Air Source [11] - SA #1 : Pressure | bar | 1.0124 | 1.0124
93¦~11~3~2~~-1~ | Gas/Air Source [11] - SA #1 : Temperature | C | 32.1803 | 30.0002
93¦~11~3~3~~-1~ | Gas/Air Source [11] - SA #1 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~11~3~4~~-1~ | Gas/Air Source [11] - SA #1 : Mass flow | t/h | 109.9377 | 91.1703
93¦~11~3~5~~-1~ | Gas/Air Source [11] - SA #1 : Molecular weight |  | 28.6575 | 28.6422
93¦~11~3~11~~-1~ | Gas/Air Source [11] - SA #1 : N2 mole percent | % | 75.8741 | 75.7646
93¦~11~3~12~~-1~ | Gas/Air Source [11] - SA #1 : O2 mole percent | % | 20.3577 | 20.3283
93¦~11~3~13~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~11~3~14~~-1~ | Gas/Air Source [11] - SA #1 : H2O mole percent | % | 2.825 | 2.9652
93¦~11~3~15~~-1~ | Gas/Air Source [11] - SA #1 : SO2 mole percent | % | 0 | 0
93¦~11~3~16~~-1~ | Gas/Air Source [11] - SA #1 : Ar mole percent | % | 0.91378 | 0.91246
93¦~11~3~20~~-1~ | Gas/Air Source [11] - SA #1 : Liquid H2O mole percent | % | 0 | 0
93¦~11~3~21~~-1~ | Gas/Air Source [11] - SA #1 : CO2 mass flow | t/h | 0.049716 | 0.041192
93¦~80~3~1~~-1~ | Gas/Air Source [80] - PA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~80~3~2~~-1~ | Gas/Air Source [80] - PA #2 : Temperature | C | 32.1803 | 30.0002
93¦~80~3~3~~-1~ | Gas/Air Source [80] - PA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~80~3~4~~-1~ | Gas/Air Source [80] - PA #2 : Mass flow | t/h | 114.4249 | 94.8916
93¦~80~3~5~~-1~ | Gas/Air Source [80] - PA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~80~3~11~~-1~ | Gas/Air Source [80] - PA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~80~3~12~~-1~ | Gas/Air Source [80] - PA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~80~3~13~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~80~3~14~~-1~ | Gas/Air Source [80] - PA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~80~3~15~~-1~ | Gas/Air Source [80] - PA #2 : SO2 mole percent | % | 0 | 0
93¦~80~3~16~~-1~ | Gas/Air Source [80] - PA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~80~3~20~~-1~ | Gas/Air Source [80] - PA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~80~3~21~~-1~ | Gas/Air Source [80] - PA #2 : CO2 mass flow | t/h | 0.051746 | 0.042873
93¦~84~3~1~~-1~ | Gas/Air Source [84] - SA #2 : Pressure | bar | 1.0124 | 1.0124
93¦~84~3~2~~-1~ | Gas/Air Source [84] - SA #2 : Temperature | C | 32.1803 | 30.0002
93¦~84~3~3~~-1~ | Gas/Air Source [84] - SA #2 : Enthalpy | kJ/kg | 7.3473 | 5.1202
93¦~84~3~4~~-1~ | Gas/Air Source [84] - SA #2 : Mass flow | t/h | 109.9377 | 91.1703
93¦~84~3~5~~-1~ | Gas/Air Source [84] - SA #2 : Molecular weight |  | 28.6575 | 28.6422
93¦~84~3~11~~-1~ | Gas/Air Source [84] - SA #2 : N2 mole percent | % | 75.8741 | 75.7646
93¦~84~3~12~~-1~ | Gas/Air Source [84] - SA #2 : O2 mole percent | % | 20.3577 | 20.3283
93¦~84~3~13~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mole percent | % | 0.029447 | 0.029404
93¦~84~3~14~~-1~ | Gas/Air Source [84] - SA #2 : H2O mole percent | % | 2.825 | 2.9652
93¦~84~3~15~~-1~ | Gas/Air Source [84] - SA #2 : SO2 mole percent | % | 0 | 0
93¦~84~3~16~~-1~ | Gas/Air Source [84] - SA #2 : Ar mole percent | % | 0.91378 | 0.91246
93¦~84~3~20~~-1~ | Gas/Air Source [84] - SA #2 : Liquid H2O mole percent | % | 0 | 0
93¦~84~3~21~~-1~ | Gas/Air Source [84] - SA #2 : CO2 mass flow | t/h | 0.049716 | 0.041192
82¦71¦~6~10~3~~-168~ | General Pump [6] - CWP-2 : Mode |  | TD | TD
82¦71¦~6~10~7~~-168~ | General Pump [6] - CWP-2 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~6~10~6~~-168~ | General Pump [6] - CWP-2 : Pump head | m | 21.3099 | 21.2982
83¦93¦~6~3~15~~-168~ | General Pump [6] - CWP-2 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~6~3~18~~-168~ | General Pump [6] - CWP-2 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~6~3~16~~-168~ | General Pump [6] - CWP-2 : Pressure drop across valve | bar | 0 | 0
83¦93¦~6~3~12~~-168~ | General Pump [6] - CWP-2 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~6~3~13~~-168~ | General Pump [6] - CWP-2 : Shaft work per station | kW | 904.7342 | 825.7756
82¦71¦~6~10~1~~-168~ | General Pump [6] - CWP-2 : Hydraulic work per station | kW | 877.5922 | 801.0024
82¦71¦~6~10~2~~-168~ | General Pump [6] - CWP-2 : Electricity consumption per station | kW | 938.1761 | 856.7526
83¦93¦~6~3~5~~-168~ | General Pump [6] - CWP-2 : Suction flow | t/h | 7559.2622 | 6903.356
83¦93¦~6~3~27~~-168~ | General Pump [6] - CWP-2 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~6~3~28~~-168~ | General Pump [6] - CWP-2 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~6~3~4~~-168~ | General Pump [6] - CWP-2 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~6~3~8~~-168~ | General Pump [6] - CWP-2 : Discharge flow | t/h | 7559.2622 | 6903.356
83¦93¦~6~3~29~~-168~ | General Pump [6] - CWP-2 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~6~3~6~~-168~ | General Pump [6] - CWP-2 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~6~3~7~~-168~ | General Pump [6] - CWP-2 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~6~6~1~1000~-168~ | General Pump [6] - CWP-2 : Motor: Mode |  | Design | Design
91¦~6~1~7~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate power | kW | 970.9543 | 886.686
91¦~6~1~19~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate efficiency | % | 96.4478 | 96.397
91¦~6~1~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~6~2~8~1000~-168~ | General Pump [6] - CWP-2 : Motor: Number of operating units |  | 1 | 1
93¦~6~7~2~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electricity consumption | kW | 938.1761 | 856.7526
93¦~6~7~6~1000~-168~ | General Pump [6] - CWP-2 : Motor: Shaft power | kW | 904.7342 | 825.7756
93¦~6~7~4~1000~-168~ | General Pump [6] - CWP-2 : Motor: Efficiency | % | 96.4354 | 96.3844
93¦~6~7~3~1000~-168~ | General Pump [6] - CWP-2 : Motor: Electrical loss | kW | 33.442 | 30.9769
89¦~6~3~5~1000~-168~ | General Pump [6] - CWP-2 : Motor: Nameplate motor shaft power | kW | 936.344 | 854.6267
82¦71¦~27~10~3~~-168~ | General Pump [27] - CWP-1 : Mode |  | TD | TD
82¦71¦~27~10~7~~-168~ | General Pump [27] - CWP-1 : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~27~10~6~~-168~ | General Pump [27] - CWP-1 : Pump head | m | 21.3099 | 21.2982
83¦93¦~27~3~15~~-168~ | General Pump [27] - CWP-1 : Pressure rise before control valve | bar | 2.0812 | 2.0812
83¦93¦~27~3~18~~-168~ | General Pump [27] - CWP-1 : Pressure rise after valve pressure drop | bar | 2.0812 | 2.0812
83¦93¦~27~3~16~~-168~ | General Pump [27] - CWP-1 : Pressure drop across valve | bar | 0 | 0
83¦93¦~27~3~12~~-168~ | General Pump [27] - CWP-1 : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~27~3~13~~-168~ | General Pump [27] - CWP-1 : Shaft work per station | kW | 904.7342 | 825.7756
82¦71¦~27~10~1~~-168~ | General Pump [27] - CWP-1 : Hydraulic work per station | kW | 877.5922 | 801.0024
82¦71¦~27~10~2~~-168~ | General Pump [27] - CWP-1 : Electricity consumption per station | kW | 938.1761 | 856.7526
83¦93¦~27~3~5~~-168~ | General Pump [27] - CWP-1 : Suction flow | t/h | 7559.2622 | 6903.356
83¦93¦~27~3~27~~-168~ | General Pump [27] - CWP-1 : Suction pressure | bar | 1.0135 | 1.0135
83¦93¦~27~3~28~~-168~ | General Pump [27] - CWP-1 : Suction temperature | C | 29.2416 | 27.3223
83¦93¦~27~3~4~~-168~ | General Pump [27] - CWP-1 : Suction enthalpy | kJ/kg | 122.5732 | 114.5466
83¦93¦~27~3~8~~-168~ | General Pump [27] - CWP-1 : Discharge flow | t/h | 7559.2622 | 6903.356
83¦93¦~27~3~29~~-168~ | General Pump [27] - CWP-1 : Discharge pressure | bar | 3.0947 | 3.0947
83¦93¦~27~3~6~~-168~ | General Pump [27] - CWP-1 : Discharge temperature | C | 29.2957 | 27.3761
83¦93¦~27~3~7~~-168~ | General Pump [27] - CWP-1 : Discharge enthalpy | kJ/kg | 122.9911 | 114.9643
82¦71¦~27~6~1~1000~-168~ | General Pump [27] - CWP-1 : Motor: Mode |  | Design | Design
91¦~27~1~7~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate power | kW | 970.9543 | 886.686
91¦~27~1~19~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate efficiency | % | 96.4478 | 96.397
91¦~27~1~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~27~2~8~1000~-168~ | General Pump [27] - CWP-1 : Motor: Number of operating units |  | 1 | 1
93¦~27~7~2~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electricity consumption | kW | 938.1761 | 856.7526
93¦~27~7~6~1000~-168~ | General Pump [27] - CWP-1 : Motor: Shaft power | kW | 904.7342 | 825.7756
93¦~27~7~4~1000~-168~ | General Pump [27] - CWP-1 : Motor: Efficiency | % | 96.4354 | 96.3844
93¦~27~7~3~1000~-168~ | General Pump [27] - CWP-1 : Motor: Electrical loss | kW | 33.442 | 30.9769
89¦~27~3~5~1000~-168~ | General Pump [27] - CWP-1 : Motor: Nameplate motor shaft power | kW | 936.344 | 854.6267
82¦71¦~35~10~3~~-168~ | General Pump [35] - BFP-C : Mode |  | TD | TD
82¦71¦~35~10~7~~-168~ | General Pump [35] - BFP-C : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~35~10~6~~-168~ | General Pump [35] - BFP-C : Pump head | m | 0 | 0
83¦93¦~35~3~15~~-168~ | General Pump [35] - BFP-C : Pressure rise before control valve | bar | 0 | 0
83¦93¦~35~3~18~~-168~ | General Pump [35] - BFP-C : Pressure rise after valve pressure drop | bar | 0 | 0
83¦93¦~35~3~16~~-168~ | General Pump [35] - BFP-C : Pressure drop across valve | bar | 0 | 0
83¦93¦~35~3~12~~-168~ | General Pump [35] - BFP-C : Apparent isentropic efficiency | % | 50.0001 | 50.0001
83¦93¦~35~3~13~~-168~ | General Pump [35] - BFP-C : Shaft work per station | kW | 0 | 0
82¦71¦~35~10~1~~-168~ | General Pump [35] - BFP-C : Hydraulic work per station | kW | 0 | 0
82¦71¦~35~10~2~~-168~ | General Pump [35] - BFP-C : Electricity consumption per station | kW | 0 | 0
83¦93¦~35~3~5~~-168~ | General Pump [35] - BFP-C : Suction flow | t/h | 2.9419e-07 | 2.9419e-07
83¦93¦~35~3~27~~-168~ | General Pump [35] - BFP-C : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~28~~-168~ | General Pump [35] - BFP-C : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~4~~-168~ | General Pump [35] - BFP-C : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~35~3~8~~-168~ | General Pump [35] - BFP-C : Discharge flow | t/h | 0 | 0
83¦93¦~35~3~29~~-168~ | General Pump [35] - BFP-C : Discharge pressure | bar | 3.4473 | 3.4473
83¦93¦~35~3~6~~-168~ | General Pump [35] - BFP-C : Discharge temperature | C | 138.3288 | 138.3288
83¦93¦~35~3~7~~-168~ | General Pump [35] - BFP-C : Discharge enthalpy | kJ/kg | 582.0298 | 582.0298
82¦71¦~35~6~1~1000~-168~ | General Pump [35] - BFP-C : Motor: Mode |  | Design | Design
91¦~35~1~7~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate power | kW | 1 | 1
91¦~35~1~19~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate efficiency | % | 96.4478 | 96.397
91¦~35~1~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate / Design point load |  | 1.75 | 1.75
76¦~35~2~8~1000~-168~ | General Pump [35] - BFP-C : Motor: Number of operating units |  | 1 | 1
93¦~35~7~2~1000~-168~ | General Pump [35] - BFP-C : Motor: Electricity consumption | kW | 0 | 0
93¦~35~7~6~1000~-168~ | General Pump [35] - BFP-C : Motor: Shaft power | kW | 0 | 0
93¦~35~7~4~1000~-168~ | General Pump [35] - BFP-C : Motor: Efficiency | % | 99.9 | 99.9
93¦~35~7~3~1000~-168~ | General Pump [35] - BFP-C : Motor: Electrical loss | kW | 0 | 0
89¦~35~3~5~1000~-168~ | General Pump [35] - BFP-C : Motor: Nameplate motor shaft power | kW | 0 | 0
82¦71¦~45~10~3~~-168~ | General Pump [45] - CP : Mode |  | TD | TD
82¦71¦~45~10~7~~-168~ | General Pump [45] - CP : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~45~10~6~~-168~ | General Pump [45] - CP : Pump head | m | 71.2929 | 71.293
83¦93¦~45~3~15~~-168~ | General Pump [45] - CP : Pressure rise before control valve | bar | 6.9218 | 6.9218
83¦93¦~45~3~18~~-168~ | General Pump [45] - CP : Pressure rise after valve pressure drop | bar | 6.9218 | 6.9218
83¦93¦~45~3~16~~-168~ | General Pump [45] - CP : Pressure drop across valve | bar | 0 | 0
83¦93¦~45~3~12~~-168~ | General Pump [45] - CP : Apparent isentropic efficiency | % | 75.0006 | 75.0007
83¦93¦~45~3~13~~-168~ | General Pump [45] - CP : Shaft work per station | kW | 95.7684 | 87.2599
82¦71¦~45~10~1~~-168~ | General Pump [45] - CP : Hydraulic work per station | kW | 92.8953 | 84.6421
82¦71¦~45~10~2~~-168~ | General Pump [45] - CP : Electricity consumption per station | kW | 101.2423 | 92.3548
83¦93¦~45~3~5~~-168~ | General Pump [45] - CP : Suction flow | t/h | 358.765 | 326.891
83¦93¦~45~3~27~~-168~ | General Pump [45] - CP : Suction pressure | bar | 0.45741 | 0.45741
83¦93¦~45~3~28~~-168~ | General Pump [45] - CP : Suction temperature | C | 45.423 | 45.4273
83¦93¦~45~3~4~~-168~ | General Pump [45] - CP : Suction enthalpy | kJ/kg | 190.1834 | 190.2018
83¦93¦~45~3~8~~-168~ | General Pump [45] - CP : Discharge flow | t/h | 358.765 | 326.891
83¦93¦~45~3~29~~-168~ | General Pump [45] - CP : Discharge pressure | bar | 7.3792 | 7.3792
83¦93¦~45~3~6~~-168~ | General Pump [45] - CP : Discharge temperature | C | 45.5004 | 45.5048
83¦93¦~45~3~7~~-168~ | General Pump [45] - CP : Discharge enthalpy | kJ/kg | 191.1155 | 191.1339
82¦71¦~45~6~1~1000~-168~ | General Pump [45] - CP : Motor: Mode |  | Design | Design
91¦~45~1~7~1000~-168~ | General Pump [45] - CP : Motor: Nameplate power | kW | 104.7795 | 95.5815
91¦~45~1~19~1000~-168~ | General Pump [45] - CP : Motor: Nameplate efficiency | % | 94.6121 | 94.5026
91¦~45~1~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate / Design point load |  | 1.0349 | 1.0349
76¦~45~2~8~1000~-168~ | General Pump [45] - CP : Motor: Number of operating units |  | 1 | 1
93¦~45~7~2~1000~-168~ | General Pump [45] - CP : Motor: Electricity consumption | kW | 101.2423 | 92.3548
93¦~45~7~6~1000~-168~ | General Pump [45] - CP : Motor: Shaft power | kW | 95.7684 | 87.2599
93¦~45~7~4~1000~-168~ | General Pump [45] - CP : Motor: Efficiency | % | 94.5932 | 94.4834
93¦~45~7~3~1000~-168~ | General Pump [45] - CP : Motor: Electrical loss | kW | 5.4739 | 5.0948
89¦~45~3~5~1000~-168~ | General Pump [45] - CP : Motor: Nameplate motor shaft power | kW | 99.1143 | 90.3086
82¦71¦~50~10~3~~-168~ | General Pump [50] - BFP-B : Mode |  | TD | TD
82¦71¦~50~10~7~~-168~ | General Pump [50] - BFP-B : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~50~10~6~~-168~ | General Pump [50] - BFP-B : Pump head | m | 1284.6265 | 1242.9407
83¦93¦~50~3~15~~-168~ | General Pump [50] - BFP-B : Pressure rise before control valve | bar | 116.8622 | 113.0701
83¦93¦~50~3~18~~-168~ | General Pump [50] - BFP-B : Pressure rise after valve pressure drop | bar | 116.8622 | 113.0701
83¦93¦~50~3~16~~-168~ | General Pump [50] - BFP-B : Pressure drop across valve | bar | 0 | 0
83¦93¦~50~3~12~~-168~ | General Pump [50] - BFP-B : Apparent isentropic efficiency | % | 50 | 49.9999
83¦93¦~50~3~13~~-168~ | General Pump [50] - BFP-B : Shaft work per station | kW | 1476.1187 | 1301.9116
82¦71¦~50~10~1~~-168~ | General Pump [50] - BFP-B : Hydraulic work per station | kW | 1431.8351 | 1262.8544
82¦71¦~50~10~2~~-168~ | General Pump [50] - BFP-B : Electricity consumption per station | kW | 1527.5677 | 1348.0876
83¦93¦~50~3~5~~-168~ | General Pump [50] - BFP-B : Suction flow | t/h | 204.5898 | 186.4964
83¦93¦~50~3~27~~-168~ | General Pump [50] - BFP-B : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~50~3~28~~-168~ | General Pump [50] - BFP-B : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~50~3~4~~-168~ | General Pump [50] - BFP-B : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~50~3~8~~-168~ | General Pump [50] - BFP-B : Discharge flow | t/h | 204.5898 | 186.4964
83¦93¦~50~3~29~~-168~ | General Pump [50] - BFP-B : Discharge pressure | bar | 120.3095 | 116.5174
83¦93¦~50~3~6~~-168~ | General Pump [50] - BFP-B : Discharge temperature | C | 142.4535 | 142.3198
83¦93¦~50~3~7~~-168~ | General Pump [50] - BFP-B : Discharge enthalpy | kJ/kg | 607.2243 | 606.4067
82¦71¦~50~6~1~1000~-168~ | General Pump [50] - BFP-B : Motor: Mode |  | Design | Design
91¦~50~1~7~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate power | kW | 2123.1482 | 1873.6909
91¦~50~1~19~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate efficiency | % | 96.8267 | 96.7728
91¦~50~1~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~50~2~8~1000~-168~ | General Pump [50] - BFP-B : Motor: Number of operating units |  | 1 | 1
93¦~50~7~2~1000~-168~ | General Pump [50] - BFP-B : Motor: Electricity consumption | kW | 1527.5677 | 1348.0876
93¦~50~7~6~1000~-168~ | General Pump [50] - BFP-B : Motor: Shaft power | kW | 1476.1187 | 1301.9116
93¦~50~7~4~1000~-168~ | General Pump [50] - BFP-B : Motor: Efficiency | % | 96.632 | 96.5747
93¦~50~7~3~1000~-168~ | General Pump [50] - BFP-B : Motor: Electrical loss | kW | 51.4491 | 46.176
89¦~50~3~5~1000~-168~ | General Pump [50] - BFP-B : Motor: Nameplate motor shaft power | kW | 2051.6396 | 1809.5115
82¦71¦~59~10~3~~-168~ | General Pump [59] - BFP-A : Mode |  | TD | TD
82¦71¦~59~10~7~~-168~ | General Pump [59] - BFP-A : Multi-pump utilization label |  | 1 installed / 1 running | 1 installed / 1 running
82¦71¦~59~10~6~~-168~ | General Pump [59] - BFP-A : Pump head | m | 1284.6265 | 1242.9407
83¦93¦~59~3~15~~-168~ | General Pump [59] - BFP-A : Pressure rise before control valve | bar | 116.8622 | 113.0701
83¦93¦~59~3~18~~-168~ | General Pump [59] - BFP-A : Pressure rise after valve pressure drop | bar | 116.8622 | 113.0701
83¦93¦~59~3~16~~-168~ | General Pump [59] - BFP-A : Pressure drop across valve | bar | 0 | 0
83¦93¦~59~3~12~~-168~ | General Pump [59] - BFP-A : Apparent isentropic efficiency | % | 50 | 49.9999
83¦93¦~59~3~13~~-168~ | General Pump [59] - BFP-A : Shaft work per station | kW | 1476.1188 | 1301.9117
82¦71¦~59~10~1~~-168~ | General Pump [59] - BFP-A : Hydraulic work per station | kW | 1431.8352 | 1262.8545
82¦71¦~59~10~2~~-168~ | General Pump [59] - BFP-A : Electricity consumption per station | kW | 1527.5679 | 1348.0878
83¦93¦~59~3~5~~-168~ | General Pump [59] - BFP-A : Suction flow | t/h | 204.5898 | 186.4964
83¦93¦~59~3~27~~-168~ | General Pump [59] - BFP-A : Suction pressure | bar | 3.4473 | 3.4473
83¦93¦~59~3~28~~-168~ | General Pump [59] - BFP-A : Suction temperature | C | 138.3288 | 138.3288
83¦93¦~59~3~4~~-168~ | General Pump [59] - BFP-A : Suction enthalpy | kJ/kg | 582.0298 | 582.0298
83¦93¦~59~3~8~~-168~ | General Pump [59] - BFP-A : Discharge flow | t/h | 204.5898 | 186.4964
83¦93¦~59~3~29~~-168~ | General Pump [59] - BFP-A : Discharge pressure | bar | 120.3095 | 116.5174
83¦93¦~59~3~6~~-168~ | General Pump [59] - BFP-A : Discharge temperature | C | 142.4535 | 142.3198
83¦93¦~59~3~7~~-168~ | General Pump [59] - BFP-A : Discharge enthalpy | kJ/kg | 607.2243 | 606.4067
82¦71¦~59~6~1~1000~-168~ | General Pump [59] - BFP-A : Motor: Mode |  | Design | Design
91¦~59~1~7~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate power | kW | 2123.1484 | 1873.691
91¦~59~1~19~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate efficiency | % | 96.8267 | 96.7728
91¦~59~1~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate / Design point load |  | 1.3899 | 1.3899
76¦~59~2~8~1000~-168~ | General Pump [59] - BFP-A : Motor: Number of operating units |  | 1 | 1
93¦~59~7~2~1000~-168~ | General Pump [59] - BFP-A : Motor: Electricity consumption | kW | 1527.5679 | 1348.0878
93¦~59~7~6~1000~-168~ | General Pump [59] - BFP-A : Motor: Shaft power | kW | 1476.1188 | 1301.9117
93¦~59~7~4~1000~-168~ | General Pump [59] - BFP-A : Motor: Efficiency | % | 96.632 | 96.5747
93¦~59~7~3~1000~-168~ | General Pump [59] - BFP-A : Motor: Electrical loss | kW | 51.4491 | 46.176
89¦~59~3~5~1000~-168~ | General Pump [59] - BFP-A : Motor: Nameplate motor shaft power | kW | 2051.6399 | 1809.5115
93¦~44~3~1~~-46~ | Makeup / Blowdown [44] : Makeup flow | t/h | 1.1103 | 0.96474
93¦~44~3~3~~-46~ | Makeup / Blowdown [44] : Makeup temperature | C | 15 | 15
93¦~44~3~2~~-46~ | Makeup / Blowdown [44] : Makeup enthalpy | kJ/kg | 63.079 | 63.079
93¦~44~3~4~~-46~ | Makeup / Blowdown [44] : Blowdown flow | t/h | 0 | 0
93¦~44~3~6~~-46~ | Makeup / Blowdown [44] : Blowdown temperature | C | 45.5173 | 45.5173
93¦~44~3~5~~-46~ | Makeup / Blowdown [44] : Blowdown enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~11~~-46~ | Makeup / Blowdown [44] : Inlet pressure | bar | 0.45741 | 0.45741
93¦~44~3~12~~-46~ | Makeup / Blowdown [44] : Inlet flow | t/h | 357.6548 | 325.9262
93¦~44~3~14~~-46~ | Makeup / Blowdown [44] : Inlet temperature | C | 45.5173 | 45.5173
93¦~44~3~13~~-46~ | Makeup / Blowdown [44] : Inlet enthalpy | kJ/kg | 190.578 | 190.578
93¦~44~3~22~~-46~ | Makeup / Blowdown [44] : Outlet flow | t/h | 358.765 | 326.891
93¦~44~3~24~~-46~ | Makeup / Blowdown [44] : Outlet temperature | C | 45.423 | 45.4273
93¦~44~3~23~~-46~ | Makeup / Blowdown [44] : Outlet enthalpy | kJ/kg | 190.1834 | 190.2018
91¦~5~1~1~~-6~ | Mixer [5] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~5~1~3~~-6~ | Mixer [5] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~5~3~1~~-6~ | Mixer [5] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~5~3~3~~-6~ | Mixer [5] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
91¦~60~1~1~~-6~ | Mixer [60] : Desired mass flow fraction into 1st clockwise node |  | 0.1 | 0.1
91¦~60~1~3~~-6~ | Mixer [60] : Desired mass flow fraction into 3rd clockwise node |  | 0.9 | 0.9
93¦~60~3~1~~-6~ | Mixer [60] : Actual mass flow fraction of 1st clockwise inlet |  | 0.1 | 0.1
93¦~60~3~3~~-6~ | Mixer [60] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.9 | 0.9
91¦~62~1~1~~-6~ | Mixer [62] : Desired mass flow fraction into 1st clockwise node |  | 0.09 | 0.09
91¦~62~1~2~~-6~ | Mixer [62] : Desired mass flow fraction into 2nd clockwise node |  | 0.91 | 0.91
93¦~62~3~1~~-6~ | Mixer [62] : Actual mass flow fraction of 1st clockwise inlet |  | 0.09 | 0.09
93¦~62~3~2~~-6~ | Mixer [62] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.91 | 0.91
91¦~64~1~1~~-6~ | Mixer [64] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~64~1~2~~-6~ | Mixer [64] : Desired mass flow fraction into 2nd clockwise node |  | 0.5 | 0.5
93¦~64~3~1~~-6~ | Mixer [64] : Actual mass flow fraction of 1st clockwise inlet |  | 0.0068469 | 0.0068618
93¦~64~3~2~~-6~ | Mixer [64] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.99315 | 0.99314
91¦~66~1~1~~-6~ | Mixer [66] : Desired mass flow fraction into 1st clockwise node |  | 0.33333 | 0.33333
91¦~66~1~2~~-6~ | Mixer [66] : Desired mass flow fraction into 2nd clockwise node |  | 0.33333 | 0.33333
91¦~66~1~3~~-6~ | Mixer [66] : Desired mass flow fraction into 3rd clockwise node |  | 0.33333 | 0.33333
93¦~66~3~1~~-6~ | Mixer [66] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~66~3~2~~-6~ | Mixer [66] : Actual mass flow fraction of 2nd clockwise inlet |  | 0.5 | 0.5
93¦~66~3~3~~-6~ | Mixer [66] : Actual mass flow fraction of 3rd clockwise inlet |  | 7.1897e-10 | 7.8873e-10
91¦~86~1~1~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~86~1~3~~-6~ | Gas/Air Mixer [86] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~86~3~1~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~3~~-6~ | Gas/Air Mixer [86] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~41~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~86~3~43~~-6~ | Gas/Air Mixer [86] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~86~3~31~~-6~ | Gas/Air Mixer [86] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~86~3~32~~-6~ | Gas/Air Mixer [86] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~86~3~33~~-6~ | Gas/Air Mixer [86] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~86~3~34~~-6~ | Gas/Air Mixer [86] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~86~3~35~~-6~ | Gas/Air Mixer [86] : Exit gas SO2 mole percent | % | 0 | 0
93¦~86~3~36~~-6~ | Gas/Air Mixer [86] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
91¦~87~1~1~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 1st clockwise node |  | 0.5 | 0.5
91¦~87~1~3~~-6~ | Gas/Air Mixer [87] : Desired mass flow fraction into 3rd clockwise node |  | 0.5 | 0.5
93¦~87~3~1~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~3~~-6~ | Gas/Air Mixer [87] : Actual mass flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~41~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 1st clockwise inlet |  | 0.5 | 0.5
93¦~87~3~43~~-6~ | Gas/Air Mixer [87] : Actual mole flow fraction of 3rd clockwise inlet |  | 0.5 | 0.5
93¦~87~3~31~~-6~ | Gas/Air Mixer [87] : Exit gas N2 mole percent | % | 75.8741 | 75.7646
93¦~87~3~32~~-6~ | Gas/Air Mixer [87] : Exit gas O2 mole percent | % | 20.3577 | 20.3283
93¦~87~3~33~~-6~ | Gas/Air Mixer [87] : Exit gas CO2 mole percent | % | 0.029447 | 0.029404
93¦~87~3~34~~-6~ | Gas/Air Mixer [87] : Exit gas H2O mole percent | % | 2.825 | 2.9652
93¦~87~3~35~~-6~ | Gas/Air Mixer [87] : Exit gas SO2 mole percent | % | 0 | 0
93¦~87~3~36~~-6~ | Gas/Air Mixer [87] : Exit gas Ar mole percent | % | 0.91378 | 0.91246
~14~10~1~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Mode |  | TD | TD
~14~3~125~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Total heat transfered away from external gases | kW | 22628.5273 | 18775.0137
~14~3~120~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on SA side | kW | 11082.3271 | 9195.168
~14~3~121~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfered away from external gases on PA side | kW | 11546.2012 | 9579.8457
~14~3~122~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on SA side | kW | 11027.1914 | 9149.4199
~14~3~123~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat transfer to internal gases on PA side | kW | 11488.7578 | 9532.1846
~14~3~124~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Heat loss from heater | kW | 112.5767 | 93.4073
~14~3~53~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : External pressure drop | millibar | 12.4533 | 12.4533
~14~3~83~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on SA side | millibar | 12.4533 | 12.4533
~14~3~103~~-162~ | Boiler Assembly [1]: Parallel Tubular Air Heaters [14] : Internal pressure drop on PA side | millibar | 12.4533 | 12.4533
~1~6~5~~-107~ | Pipe (PCE) [1] : Mode |  | TD | TD
~1~6~1~~-107~ | Pipe (PCE) [1] : Pressure drop from inlet to exit | bar | 0.06297 | 0.061192
~1~6~2~~-107~ | Pipe (PCE) [1] : Pressure drop as percent of exit pressure | % | 1 | 1
~1~6~4~~-107~ | Pipe (PCE) [1] : Heat loss | kW | 0.3899 | 0.35713
~4~6~5~~-107~ | Pipe (PCE) [4] : Mode |  | TD | TD
~4~6~1~~-107~ | Pipe (PCE) [4] : Pressure drop from inlet to exit | bar | 1.5561 | 1.5066
~4~6~2~~-107~ | Pipe (PCE) [4] : Pressure drop as percent of exit pressure | % | 1.8 | 1.8
~4~6~4~~-107~ | Pipe (PCE) [4] : Heat loss | kW | 0 | 0
~53~6~5~~-107~ | Pipe (PCE) [53] : Mode |  | TD | TD
~53~6~1~~-107~ | Pipe (PCE) [53] : Pressure drop from inlet to exit | bar | 0.54275 | 0.52742
~53~6~2~~-107~ | Pipe (PCE) [53] : Pressure drop as percent of exit pressure | % | 2 | 2
~53~6~4~~-107~ | Pipe (PCE) [53] : Heat loss | kW | 5.0507 | 4.6074
~54~6~5~~-107~ | Pipe (PCE) [54] : Mode |  | TD | TD
~54~6~1~~-107~ | Pipe (PCE) [54] : Pressure drop from inlet to exit | bar | 0.36765 | 0.35213
~54~6~2~~-107~ | Pipe (PCE) [54] : Pressure drop as percent of exit pressure | % | 2 | 2
~54~6~4~~-107~ | Pipe (PCE) [54] : Heat loss | kW | 8.5197 | 7.8016
~55~6~5~~-107~ | Pipe (PCE) [55] : Mode |  | TD | TD
~55~6~1~~-107~ | Pipe (PCE) [55] : Pressure drop from inlet to exit | bar | 0.10784 | 0.10479
~55~6~2~~-107~ | Pipe (PCE) [55] : Pressure drop as percent of exit pressure | % | 2 | 2
~55~6~4~~-107~ | Pipe (PCE) [55] : Heat loss | kW | 5.3827 | 5.0435
~56~6~5~~-107~ | Pipe (PCE) [56] : Mode |  | TD | TD
~56~6~1~~-107~ | Pipe (PCE) [56] : Pressure drop from inlet to exit | bar | 0.042745 | 0.041538
~56~6~2~~-107~ | Pipe (PCE) [56] : Pressure drop as percent of exit pressure | % | 2 | 2
~56~6~4~~-107~ | Pipe (PCE) [56] : Heat loss | kW | 2.6357 | 2.3795
~57~6~5~~-107~ | Pipe (PCE) [57] : Mode |  | TD | TD
~57~6~1~~-107~ | Pipe (PCE) [57] : Pressure drop from inlet to exit | bar | 0.026274 | 0.025533
~57~6~2~~-107~ | Pipe (PCE) [57] : Pressure drop as percent of exit pressure | % | 2 | 2
~57~6~4~~-107~ | Pipe (PCE) [57] : Heat loss | kW | 5.3243 | 4.8118
~58~6~5~~-107~ | Pipe (PCE) [58] : Mode |  | TD | TD
~58~6~1~~-107~ | Pipe (PCE) [58] : Pressure drop from inlet to exit | bar | 0.0078431 | 0.0076216
~58~6~2~~-107~ | Pipe (PCE) [58] : Pressure drop as percent of exit pressure | % | 2 | 2
~58~6~4~~-107~ | Pipe (PCE) [58] : Heat loss | kW | 4.2495 | 3.7665
~77~6~5~~-107~ | Pipe (PCE) [77] : Mode |  | TD | TD
~77~6~1~~-107~ | Pipe (PCE) [77] : Pressure drop from inlet to exit | bar | 1.183 | 1.1454
~77~6~2~~-107~ | Pipe (PCE) [77] : Pressure drop as percent of exit pressure | % | 1 | 1
~77~6~4~~-107~ | Pipe (PCE) [77] : Heat loss | kW | 971.685 | 886.3712
~79~6~5~~-107~ | Pipe (PCE) [79] : Mode |  | TD | TD
~79~6~1~~-107~ | Pipe (PCE) [79] : Pressure drop from inlet to exit | bar | 0 | 0
~79~6~2~~-107~ | Pipe (PCE) [79] : Pressure drop as percent of exit pressure | % | 0 | 0
~79~6~4~~-107~ | Pipe (PCE) [79] : Heat loss | kW | 0 | 0
91¦~63~1~13~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell pressure | bar | 0.175 | 0.175
91¦~63~1~71~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Saturation temperature | C | 57.2007 | 57.2007
89¦~63~3~7~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer | kW | 393.3015 | 358.5564
91¦~63~1~101~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Feedwater temperature rise (overall) | C | 0.95284 | 0.95335
82¦71¦~63~5~2~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Terminal difference | C | 10.7474 | 10.7425
91¦~63~1~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total heat transfer area | m^2 | 1870.6956 | 1870.6956
91¦~63~1~82~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Nameplate steam pressure | bar | 0 | 0
89¦~63~3~52~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell length | m | 0 | 0
89¦~63~3~53~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Shell inner diameter | m | 0 | 0
89¦~63~3~56~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall length | m | 0 | 0
89¦~63~3~27~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Overall outer diameter | m | 0 | 0
89¦~63~3~45~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total dry weight | kg | 0 | 0
89¦~63~3~57~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total operating (wet) weight | kg | 0 | 0
82¦71¦~63~5~5~~-127~ | Shell-Tube Water Heater (PCE) [63] - GC : Total estimated installed cost | USD | 0 | 0
91¦~15~1~1~~-7~ | Splitter [15] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~15~1~3~~-7~ | Splitter [15] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~15~3~1~~-7~ | Splitter [15] : Actual flow fraction of 1st clockwise outlet |  | 0.050126 | 0.049461
93¦~15~3~3~~-7~ | Splitter [15] : Actual flow fraction of 3rd clockwise outlet |  | 0.94987 | 0.95054
91¦~26~1~1~~-7~ | Splitter [26] - k : Desired flow fraction of 1st clockwise node |  | 0.1 | 0.1
91¦~26~1~2~~-7~ | Splitter [26] - k : Desired flow fraction of 2nd clockwise node |  | 0.89904 | 0.89904
91¦~26~1~3~~-7~ | Splitter [26] - k : Desired flow fraction of 3rd clockwise node |  | 0.00096306 | 0.00096306
93¦~26~3~1~~-7~ | Splitter [26] - k : Actual flow fraction of 1st clockwise outlet |  | 0.00038207 | 0.00038391
93¦~26~3~2~~-7~ | Splitter [26] - k : Actual flow fraction of 2nd clockwise outlet |  | 0.99855 | 0.99855
93¦~26~3~3~~-7~ | Splitter [26] - k : Actual flow fraction of 3rd clockwise outlet |  | 0.0010696 | 0.0010696
91¦~28~1~1~~-7~ | Splitter [28] : Desired flow fraction of 1st clockwise node |  | 0.97 | 0.97
91¦~28~1~2~~-7~ | Splitter [28] : Desired flow fraction of 2nd clockwise node |  | 0.03 | 0.03
93¦~28~3~1~~-7~ | Splitter [28] : Actual flow fraction of 1st clockwise outlet |  | 0.95535 | 0.95533
93¦~28~3~2~~-7~ | Splitter [28] : Actual flow fraction of 2nd clockwise outlet |  | 0.04465 | 0.044674
91¦~29~1~1~~-7~ | Splitter [29] : Desired flow fraction of 1st clockwise node |  | 0.92 | 0.92
91¦~29~1~2~~-7~ | Splitter [29] : Desired flow fraction of 2nd clockwise node |  | 0.08 | 0.08
93¦~29~3~1~~-7~ | Splitter [29] : Actual flow fraction of 1st clockwise outlet |  | 0.92116 | 0.92082
93¦~29~3~2~~-7~ | Splitter [29] : Actual flow fraction of 2nd clockwise outlet |  | 0.078837 | 0.079183
91¦~30~1~1~~-7~ | Splitter [30] : Desired flow fraction of 1st clockwise node |  | 0.989 | 0.989
91¦~30~1~2~~-7~ | Splitter [30] : Desired flow fraction of 2nd clockwise node |  | 0.011 | 0.011
93¦~30~3~1~~-7~ | Splitter [30] : Actual flow fraction of 1st clockwise outlet |  | 0.99608 | 0.99606
93¦~30~3~2~~-7~ | Splitter [30] : Actual flow fraction of 2nd clockwise outlet |  | 0.0039167 | 0.0039365
91¦~33~1~1~~-7~ | Splitter [33] : Desired flow fraction of 1st clockwise node |  | 0.954 | 0.954
91¦~33~1~2~~-7~ | Splitter [33] : Desired flow fraction of 2nd clockwise node |  | 0.046 | 0.046
93¦~33~3~1~~-7~ | Splitter [33] : Actual flow fraction of 1st clockwise outlet |  | 0.94572 | 0.94419
93¦~33~3~2~~-7~ | Splitter [33] : Actual flow fraction of 2nd clockwise outlet |  | 0.054284 | 0.055812
91¦~34~1~1~~-7~ | Splitter [34] : Desired flow fraction of 1st clockwise node |  | 0.873 | 0.873
91¦~34~1~2~~-7~ | Splitter [34] : Desired flow fraction of 2nd clockwise node |  | 0.1 | 0.1
91¦~34~1~3~~-7~ | Splitter [34] : Desired flow fraction of 3rd clockwise node |  | 0.027 | 0.027
93¦~34~3~1~~-7~ | Splitter [34] : Actual flow fraction of 1st clockwise outlet |  | 0.96781 | 0.96814
93¦~34~3~2~~-7~ | Splitter [34] : Actual flow fraction of 2nd clockwise outlet |  | 0.0040784 | 0.0039729
93¦~34~3~3~~-7~ | Splitter [34] : Actual flow fraction of 3rd clockwise outlet |  | 0.028107 | 0.027889
91¦~47~1~1~~-7~ | Splitter [47] : Desired flow fraction of 1st clockwise node |  | 0.942 | 0.942
91¦~47~1~2~~-7~ | Splitter [47] : Desired flow fraction of 2nd clockwise node |  | 0.058 | 0.058
93¦~47~3~1~~-7~ | Splitter [47] : Actual flow fraction of 1st clockwise outlet |  | 0.94133 | 0.94175
93¦~47~3~2~~-7~ | Splitter [47] : Actual flow fraction of 2nd clockwise outlet |  | 0.058665 | 0.058251
91¦~49~1~1~~-7~ | Splitter [49] : Desired flow fraction of 1st clockwise node |  | 0.9393 | 0.9393
91¦~49~1~2~~-7~ | Splitter [49] : Desired flow fraction of 2nd clockwise node |  | 0.0607 | 0.0607
93¦~49~3~1~~-7~ | Splitter [49] : Actual flow fraction of 1st clockwise outlet |  | 0.95474 | 0.95594
93¦~49~3~2~~-7~ | Splitter [49] : Actual flow fraction of 2nd clockwise outlet |  | 0.045264 | 0.044059
91¦~61~1~1~~-7~ | Splitter [61] : Desired flow fraction of 1st clockwise node |  | 0.33333 | 0.33333
91¦~61~1~2~~-7~ | Splitter [61] : Desired flow fraction of 2nd clockwise node |  | 0.33333 | 0.33333
91¦~61~1~3~~-7~ | Splitter [61] : Desired flow fraction of 3rd clockwise node |  | 0.33333 | 0.33333
93¦~61~3~1~~-7~ | Splitter [61] : Actual flow fraction of 1st clockwise outlet |  | 7.1897e-10 | 7.8873e-10
93¦~61~3~2~~-7~ | Splitter [61] : Actual flow fraction of 2nd clockwise outlet |  | 0.5 | 0.5
93¦~61~3~3~~-7~ | Splitter [61] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
91¦~67~1~1~~-7~ | Splitter [67] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~67~1~3~~-7~ | Splitter [67] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~67~3~1~~-7~ | Splitter [67] : Actual flow fraction of 1st clockwise outlet |  | 0.50013 | 0.50086
93¦~67~3~3~~-7~ | Splitter [67] : Actual flow fraction of 3rd clockwise outlet |  | 0.49987 | 0.49914
91¦~76~1~1~~-7~ | Splitter [76] : Desired flow fraction of 1st clockwise node |  | 0.5 | 0.5
91¦~76~1~3~~-7~ | Splitter [76] : Desired flow fraction of 3rd clockwise node |  | 0.5 | 0.5
93¦~76~3~1~~-7~ | Splitter [76] : Actual flow fraction of 1st clockwise outlet |  | 0.5 | 0.5
93¦~76~3~3~~-7~ | Splitter [76] : Actual flow fraction of 3rd clockwise outlet |  | 0.5 | 0.5
82¦71¦~43~6~2~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Mode |  | TD | TD
93¦~43~4~11~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exit temperature | C | 148.239 | 94.4053
93¦~43~4~48~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Water dew point temperature | C | 57.0002 | 55.1079
93¦~43~4~47~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Sulfur dew point temperature | C | 146.9678 | 146.0616
93¦~43~4~65~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO2 emission | tonne/day | 2525.6865 | 2199.6116
93¦~43~4~16~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas O2 mol% | % | 2.9438 | 3.541
93¦~43~4~17~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas CO2 mol% | % | 13.2498 | 13.9605
93¦~43~4~18~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas H2O mol% | % | 17.1003 | 15.6285
82¦71¦~43~6~3~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas N2 mol% | % | 65.91 | 66.0719
82¦71¦~43~6~5~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas Ar mol% | % | 0.79282 | 0.79472
93¦~43~4~36~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 mol% | % | 0.0031714 | 0.0033418
93¦~43~4~43~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (energy basis) | ng/J | 29.829 | 29.8297
93¦~43~4~44~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (volume basis, @ 6% O2, dry) | mg/Nm^3 | 93.8988 | 100.9782
93¦~43~4~45~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas SO2 content (ppmv, @ 6% O2, dry) |  | 32.8529 | 35.3298
93¦~43~4~40~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust flow | t/h | 0.0097615 | 0.007906
93¦~43~4~41~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (energy basis) | ng/J | 7.9416 | 7.385
93¦~43~4~42~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Exhaust gas dust load (volume basis) | mg/Nm^3 | 24.9994 | 24.9994
93¦~43~4~46~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Plume visibility index |  | 0 | 0
93¦~43~4~64~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : HCL mass flow in exit gas | kg/hr | 0 | 0
93¦~43~4~60~~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Hg mass flow in exit gas | kg/hr | 0 | 0
91¦~43~1~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Reference O2 content | % | 6 | 6
90¦~43~4~2~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : Actual O2 content in exit gas | % | 2.9438 | 3.541
90¦~43~4~4~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : H2O content in exit gas | % | 17.1003 | 15.6285
93¦~43~2~6~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~10~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, wet basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~13~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, actual O2% (ppmv) |  | 0 | 0
93¦~43~2~16~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx volume concentration in exit gas, dry basis, ref. O2% (ppmv) |  | 0 | 0
93¦~43~2~20~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : NOx mass concentration in exit gas, wet basis, actual O2% (ppm) |  | 0 | 0
93¦~43~2~7~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~11~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~14~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~17~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~21~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : CO mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
93¦~43~2~8~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass flow in exit gas | kg/hr | 0 | 0
93¦~43~2~12~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, wet basis, actual O2% (ppmv) | ppmv | 0 | 0
93¦~43~2~15~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, actual O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~18~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC volume concentration in exit gas, dry basis, ref. O2% (ppmv) | ppmvd | 0 | 0
93¦~43~2~22~100~-121~ | Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack : UHC mass concentration in exit gas, wet basis, actual O2% (ppm) | ppm | 0 | 0
~38~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Mode |  | TD | TD
~38~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet mass flow | t/h | 408.2104 | 372.1087
~38~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet pressure | bar | 96.1447 | 93.0932
~38~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet enthalpy | kJ/kg | 3209.927 | 3215.0935
~38~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam inlet temperature | C | 436.0032 | 436.0036
~38~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit mass flow | t/h | 408.2104 | 372.1087
~38~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit pressure | bar | 88.2061 | 85.4066
~38~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit temperature | C | 537.2 | 536.16
~38~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam exit enthalpy | kJ/kg | 3482.1716 | 3482.5215
~38~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas mass flow | t/h | 516.8243 | 431.4653
~38~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Flyash mass flow | t/h | 4.4783 | 3.9456
~38~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas inlet temperature | C | 894 | 894
~38~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas exit temperature | C | 731.6876 | 718.207
~38~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat transfer to steam | kW | 30870.7617 | 27642.7109
~38~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Heat loss | kW | 0 | 0
~38~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Radiant heat influx | kW | 0 | 0
~38~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~38~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Steam side pressure drop | bar | 7.9386 | 7.6866
~41~10~1~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Mode |  | TD | TD
~41~1~35~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet mass flow | t/h | 387.7 | 353.66
~41~1~36~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet pressure | bar | 106.4033 | 103.0262
~41~1~38~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet enthalpy | kJ/kg | 2851.1492 | 2865.3564
~41~1~37~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam inlet temperature | C | 338.9836 | 339.0041
~41~3~12~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit mass flow | t/h | 387.7 | 353.66
~41~3~13~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit pressure | bar | 98.0676 | 94.9551
~41~3~14~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit temperature | C | 434.1 | 434.1
~41~3~15~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam exit enthalpy | kJ/kg | 3201.3213 | 3206.6785
~41~1~24~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas mass flow | t/h | 516.8243 | 431.4653
~41~1~105~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Flyash mass flow | t/h | 4.4783 | 3.9456
~41~1~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas inlet temperature | C | 731.6875 | 718.228
~41~3~3~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas exit temperature | C | 524.1159 | 494.2181
~41~3~19~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat transfer to steam | kW | 37712.1797 | 33531.6289
~41~3~26~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Heat loss | kW | 282.8414 | 251.4872
~41~1~16~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Radiant heat influx | kW | 0 | 0
~41~3~29~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Gas side pressure drop | millibar | 2.4907 | 2.4907
~41~3~28~~-115~ | Boiler Assembly [1]: Superheater (PCE) [41] - LTSH : Steam side pressure drop | bar | 8.3357 | 8.0712
~13~5~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure control mode |  | VWO | VWO
~13~5~2~~-32~ | Boiler Assembly [1]: Valve [13] : Valve current status |  | Wide open | Wide open
~13~3~1~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop @ VWO | bar | 0 | 0
~13~3~10~~-32~ | Boiler Assembly [1]: Valve [13] : Pressure drop | bar | 0 | 0
~13~3~3~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet pressure | bar | 118.2992 | 114.5446
~13~3~4~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet temperature | C | 226.1392 | 226.1398
~13~3~5~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet enthalpy | kJ/kg | 974.4664 | 974.3673
~13~3~6~~-32~ | Boiler Assembly [1]: Valve [13] : Inlet mass flow | t/h | 388.6693 | 354.5441
~13~3~7~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet pressure | bar | 118.2992 | 114.5446
~13~3~8~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet temperature | C | 226.1392 | 226.1398
~13~3~9~~-32~ | Boiler Assembly [1]: Valve [13] : Outlet enthalpy | kJ/kg | 974.4664 | 974.3673
~31~5~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure control mode |  | Delta P | Delta P
~31~5~2~~-32~ | Boiler Assembly [1]: Valve [31] : Valve current status |  | Partially open | Partially open
~31~3~1~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop @ VWO | bar | 0 | 0
~31~3~10~~-32~ | Boiler Assembly [1]: Valve [31] : Pressure drop | bar | 0.20001 | 0.19999
~31~3~3~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet pressure | bar | 88.2061 | 85.4066
~31~3~4~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet temperature | C | 537.2003 | 536.1599
~31~3~5~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet enthalpy | kJ/kg | 3482.1716 | 3482.5215
~31~3~6~~-32~ | Boiler Assembly [1]: Valve [31] : Inlet mass flow | t/h | 408.2104 | 372.1087
~31~3~7~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet pressure | bar | 88.0061 | 85.2066
~31~3~8~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet temperature | C | 537.116 | 536.0752
~31~3~9~~-32~ | Boiler Assembly [1]: Valve [31] : Outlet enthalpy | kJ/kg | 3482.1716 | 3482.5215
~69~5~1~~-32~ | Valve [69] : Pressure control mode |  | Closed | Closed
~69~5~2~~-32~ | Valve [69] : Valve current status |  | Closed | Closed
~69~3~1~~-32~ | Valve [69] : Pressure drop @ VWO | bar | 0 | 0
~69~3~10~~-32~ | Valve [69] : Pressure drop | bar | 0 | 0
~69~3~3~~-32~ | Valve [69] : Inlet pressure | bar | 120.3095 | 116.5174
~69~3~4~~-32~ | Valve [69] : Inlet temperature | C | 152.1979 | 152.2534
~69~3~5~~-32~ | Valve [69] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~69~3~6~~-32~ | Valve [69] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~69~3~7~~-32~ | Valve [69] : Outlet pressure | bar | 120.3095 | 116.5174
~69~3~8~~-32~ | Valve [69] : Outlet temperature | C | 152.1979 | 152.2534
~69~3~9~~-32~ | Valve [69] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~70~5~1~~-32~ | Valve [70] : Pressure control mode |  | Down set point | Down set point
~70~5~2~~-32~ | Valve [70] : Valve current status |  | Partially open | Partially open
~70~3~1~~-32~ | Valve [70] : Pressure drop @ VWO | bar | 0 | 0
~70~3~10~~-32~ | Valve [70] : Pressure drop | bar | 0 | 0
~70~3~3~~-32~ | Valve [70] : Inlet pressure | bar | 120.3095 | 116.5174
~70~3~4~~-32~ | Valve [70] : Inlet temperature | C | 158.077 | 157.9403
~70~3~5~~-32~ | Valve [70] : Inlet enthalpy | kJ/kg | 673.9965 | 673.179
~70~3~6~~-32~ | Valve [70] : Inlet mass flow | t/h | 204.5898 | 186.4964
~70~3~7~~-32~ | Valve [70] : Outlet pressure | bar | 120.3095 | 116.5174
~70~3~8~~-32~ | Valve [70] : Outlet temperature | C | 158.077 | 157.9403
~70~3~9~~-32~ | Valve [70] : Outlet enthalpy | kJ/kg | 673.9965 | 673.179
~71~5~1~~-32~ | Valve [71] : Pressure control mode |  | Down set point | Down set point
~71~5~2~~-32~ | Valve [71] : Valve current status |  | Partially open | Partially open
~71~3~1~~-32~ | Valve [71] : Pressure drop @ VWO | bar | 0 | 0
~71~3~10~~-32~ | Valve [71] : Pressure drop | bar | 0 | 0
~71~3~3~~-32~ | Valve [71] : Inlet pressure | bar | 120.3095 | 116.5174
~71~3~4~~-32~ | Valve [71] : Inlet temperature | C | 158.077 | 157.9403
~71~3~5~~-32~ | Valve [71] : Inlet enthalpy | kJ/kg | 673.9965 | 673.179
~71~3~6~~-32~ | Valve [71] : Inlet mass flow | t/h | 204.5898 | 186.4964
~71~3~7~~-32~ | Valve [71] : Outlet pressure | bar | 120.3095 | 116.5174
~71~3~8~~-32~ | Valve [71] : Outlet temperature | C | 158.077 | 157.9403
~71~3~9~~-32~ | Valve [71] : Outlet enthalpy | kJ/kg | 673.9965 | 673.179
~73~5~1~~-32~ | Valve [73] : Pressure control mode |  | Up set point | Up set point
~73~5~2~~-32~ | Valve [73] : Valve current status |  | Partially open | Partially open
~73~3~1~~-32~ | Valve [73] : Pressure drop @ VWO | bar | 0 | 0
~73~3~10~~-32~ | Valve [73] : Pressure drop | bar | 0 | 0
~73~3~3~~-32~ | Valve [73] : Inlet pressure | bar | 3.4473 | 3.4473
~73~3~4~~-32~ | Valve [73] : Inlet temperature | C | 138.3289 | 138.3289
~73~3~5~~-32~ | Valve [73] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~73~3~6~~-32~ | Valve [73] : Inlet mass flow | t/h | 204.5898 | 186.4964
~73~3~7~~-32~ | Valve [73] : Outlet pressure | bar | 3.4473 | 3.4473
~73~3~8~~-32~ | Valve [73] : Outlet temperature | C | 138.3289 | 138.3289
~73~3~9~~-32~ | Valve [73] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~5~1~~-32~ | Valve [74] : Pressure control mode |  | Closed | Closed
~74~5~2~~-32~ | Valve [74] : Valve current status |  | Partially open | Partially open
~74~3~1~~-32~ | Valve [74] : Pressure drop @ VWO | bar | 0 | 0
~74~3~10~~-32~ | Valve [74] : Pressure drop | bar | 0 | 0
~74~3~3~~-32~ | Valve [74] : Inlet pressure | bar | 3.4473 | 3.4473
~74~3~4~~-32~ | Valve [74] : Inlet temperature | C | 138.3289 | 138.3289
~74~3~5~~-32~ | Valve [74] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~74~3~6~~-32~ | Valve [74] : Inlet mass flow | t/h | 2.9419e-07 | 2.9419e-07
~74~3~7~~-32~ | Valve [74] : Outlet pressure | bar | 3.4473 | 3.4473
~74~3~8~~-32~ | Valve [74] : Outlet temperature | C | 138.3289 | 138.3289
~74~3~9~~-32~ | Valve [74] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~5~1~~-32~ | Valve [75] : Pressure control mode |  | Up set point | Up set point
~75~5~2~~-32~ | Valve [75] : Valve current status |  | Partially open | Partially open
~75~3~1~~-32~ | Valve [75] : Pressure drop @ VWO | bar | 0 | 0
~75~3~10~~-32~ | Valve [75] : Pressure drop | bar | 0 | 0
~75~3~3~~-32~ | Valve [75] : Inlet pressure | bar | 3.4473 | 3.4473
~75~3~4~~-32~ | Valve [75] : Inlet temperature | C | 138.3289 | 138.3289
~75~3~5~~-32~ | Valve [75] : Inlet enthalpy | kJ/kg | 648.8021 | 648.8021
~75~3~6~~-32~ | Valve [75] : Inlet mass flow | t/h | 204.5898 | 186.4964
~75~3~7~~-32~ | Valve [75] : Outlet pressure | bar | 3.4473 | 3.4473
~75~3~8~~-32~ | Valve [75] : Outlet temperature | C | 138.3289 | 138.3289
~75~3~9~~-32~ | Valve [75] : Outlet enthalpy | kJ/kg | 648.8021 | 648.8021
93¦~51~3~1~~-14~ | Water Sink [51] - Outfall : Pressure | bar | 2.75 | 2.75
93¦~51~3~2~~-14~ | Water Sink [51] - Outfall : Temperature | C | 39.3118 | 37.3932
93¦~51~3~3~~-14~ | Water Sink [51] - Outfall : Enthalpy | kJ/kg | 164.8358 | 156.815
93¦~51~3~4~~-14~ | Water Sink [51] - Outfall : Mass flow | t/h | 15118.5244 | 13806.7119
93¦~3~3~1~~-9~ | Water Source [3] - Intake : Pressure | bar | 1.0135 | 1.0135
93¦~3~3~2~~-9~ | Water Source [3] - Intake : Temperature | C | 29.2416 | 27.3223
93¦~3~3~3~~-9~ | Water Source [3] - Intake : Enthalpy | kJ/kg | 122.5732 | 114.5466
93¦~3~3~4~~-9~ | Water Source [3] - Intake : Mass flow | t/h | 15118.5244 | 13806.7119
~40~10~1~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Mode |  | TD | TD
~40~3~27~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser pressure | bar | 0.0985 | 0.0985
~40~3~26~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Saturation temperature | C | 45.5122 | 45.5122
~40~3~21~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Condenser heat rejection (per unit) | kW | 175732.4844 | 160509
~40~3~23~~-104~ | Water-cooled Condenser (PCE) [40] - COND : Cooling water-side pressure drop | bar | 0.34473 | 0.34473
86¦87¦68¦86¦86¦~16~4~31~~-4100~ | ST Assembly [1]: Current generator power | kW | 110027.0938 | 99960.1641
86¦87¦68¦86¦86¦~16~4~4~~-4100~ | ST Assembly [1]: Current generator efficiency | % | 98.6043 | 98.5882
86¦87¦68¦86¦86¦~16~4~6~~-4100~ | ST Assembly [1]: Current ST lube oil pump auxiliary | kW | 173.2927 | 157.4372
86¦87¦68¦86¦86¦~16~4~7~~-4100~ | ST Assembly [1]: Current ST misc auxiliary | kW | 57.7642 | 52.4791
86¦87¦68¦86¦86¦~16~3~24~~-4100~ | ST Assembly [1]: Nameplate capacity | MVA | 128.365 | 116.6202
86¦87¦68¦86¦86¦~16~1~19~~-4100~ | ST Assembly [1]: Design point generator power factor |  | 0.9 | 0.9
86¦87¦68¦86¦86¦~16~1~21~~-4100~ | ST Assembly [1]: Design point generator efficiency | % | 98.6233 | 98.6074
86¦87¦68¦86¦86¦~16~3~25~~-4100~ | ST Assembly [1]: Nameplate throttle pressure | bar | 90.7725 | 87.885
86¦87¦68¦86¦86¦~16~3~26~~-4100~ | ST Assembly [1]: Nameplate throttle temperature | C | 536.4592 | 535.4362
86¦87¦68¦86¦86¦~16~3~27~~-4100~ | ST Assembly [1]: Nameplate throttle mass flow | t/h | 407.6178 | 371.5678
86¦87¦68¦86¦86¦~16~2~22~~-4100~ | ST Assembly [1]: Number of LPT exhaust annuli |  | 1 | 1
86¦87¦68¦86¦86¦~16~3~28~~-4100~ | ST Assembly [1]: Number of extraction/admission ports |  | 7 | 7
86¦87¦68¦86¦86¦~16~3~29~~-4100~ | ST Assembly [1]: Number of auto extraction/admission ports |  | 0 | 0
82¦71¦~16~6~1~2000~-4100~ | ST Assembly [1]: Generator mode |  | Design | Design
91¦~16~1~7~2000~-4100~ | ST Assembly [1]: Generator nameplate power | kW | 115528.4453 | 104958.1641
91¦~16~1~19~2000~-4100~ | ST Assembly [1]: Generator nameplate efficiency | % | 98.6233 | 98.6074
91¦~16~1~5~2000~-4100~ | ST Assembly [1]: Generator nameplate / design point load |  | 1.05 | 1.05
76¦~16~2~8~2000~-4100~ | ST Assembly [1]: Generator number of operating units |  | 1 | 1
93¦~16~7~2~2000~-4100~ | ST Assembly [1]: Generator power output | kW | 110027.0938 | 99960.1641
93¦~16~7~6~2000~-4100~ | ST Assembly [1]: Generator shaft power | kW | 111584.4922 | 101391.5938
93¦~16~7~4~2000~-4100~ | ST Assembly [1]: Generator generator efficiency | % | 98.6043 | 98.5882
93¦~16~7~3~2000~-4100~ | ST Assembly [1]: Generator total loss | kW | 1557.3973 | 1431.4281
93¦~16~7~28~2000~-4100~ | ST Assembly [1]: Generator electrical & windage loss | kW | 1366.5381 | 1256.0345
93¦~16~7~29~2000~-4100~ | ST Assembly [1]: Generator mechanical loss | kW | 190.8593 | 175.3936
86¦87¦68¦86¦86¦~16~3~30~~-4100~ | ST Assembly [1]: Steam turbine length | m | 11.0305 | 10.7083
86¦87¦68¦86¦86¦~16~3~31~~-4100~ | ST Assembly [1]: Steam turbine width | m | 5.1286 | 4.9922
86¦87¦68¦86¦86¦~16~3~32~~-4100~ | ST Assembly [1]: Steam turbine weight | kg | 185334.25 | 172800.8438
86¦87¦68¦86¦86¦~16~3~34~~-4100~ | ST Assembly [1]: Generator length | m | 10.2414 | 10.0051
86¦87¦68¦86¦86¦~16~3~35~~-4100~ | ST Assembly [1]: Generator width | m | 3.5074 | 3.4608
86¦87¦68¦86¦86¦~16~3~36~~-4100~ | ST Assembly [1]: Generator weight | kg | 170233.7812 | 159013.1562
86¦87¦68¦86¦86¦~16~3~37~~-4100~ | ST Assembly [1]: Overall steam turbine and generator length | m | 21.2719 | 20.7134
86¦87¦68¦86¦86¦~16~3~38~~-4100~ | ST Assembly [1]: Overall steam turbine and generator width | m | 5.1286 | 4.9922
86¦87¦68¦86¦86¦~16~3~39~~-4100~ | ST Assembly [1]: Overall steam turbine and generator weight | kg | 355568.0312 | 331814
86¦87¦68¦86¦86¦~16~3~40~~-4100~ | ST Assembly [1]: Foundation length | m | 23.8759 | 23.2688
86¦87¦68¦86¦86¦~16~3~41~~-4100~ | ST Assembly [1]: Foundation width | m | 6.1544 | 5.9906
86¦87¦68¦86¦86¦~16~3~6~~-4100~ | ST Assembly [1]: Steam turbine package reference cost | USD | 20509736 | 19411402
86¦87¦68¦86¦86¦~16~10~1~~-4100~ | ST Assembly [1]: Total estimated installed cost | USD | 24926490 | 23589240
82¦71¦~16~10~3~~-11~ | ST Assembly [1]: ST Group [16] : Mode |  | Design | Design
82¦71¦~16~10~4~~-11~ | ST Assembly [1]: ST Group [16] : Type of inlet control |  | Sliding | Sliding
93¦~16~3~29~~-11~ | ST Assembly [1]: ST Group [16] : Steam supply pressure | bar | 86.45 | 83.7
93¦~16~3~11~~-11~ | ST Assembly [1]: ST Group [16] : Inlet pressure | bar | 86.45 | 83.7
93¦~16~3~12~~-11~ | ST Assembly [1]: ST Group [16] : Inlet temperature | C | 536.4592 | 535.4362
93¦~16~3~14~~-11~ | ST Assembly [1]: ST Group [16] : Inlet flow | t/h | 407.6178 | 371.5678
93¦~16~3~13~~-11~ | ST Assembly [1]: ST Group [16] : Inlet enthalpy | kJ/kg | 3482.1716 | 3482.5215
93¦~16~3~16~~-11~ | ST Assembly [1]: ST Group [16] : Expansion massflow | t/h | 407.239 | 371.2879
93¦~16~3~4~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial pressure | bar | 86.45 | 83.7
93¦~16~3~15~~-11~ | ST Assembly [1]: ST Group [16] : Expansion initial enthalpy | kJ/kg | 3482.1716 | 3482.5215
93¦~16~3~6~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end pressure (before Exhaust Loss) | bar | 27.68 | 26.8987
93¦~16~3~25~~-11~ | ST Assembly [1]: ST Group [16] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3213.314 | 3214.521
93¦~16~3~21~~-11~ | ST Assembly [1]: ST Group [16] : Outlet pressure | bar | 27.68 | 26.8987
93¦~16~3~22~~-11~ | ST Assembly [1]: ST Group [16] : Outlet temperature | C | 390.2057 | 390.1317
93¦~16~3~24~~-11~ | ST Assembly [1]: ST Group [16] : Outlet flow | t/h | 407.239 | 371.2879
93¦~16~3~23~~-11~ | ST Assembly [1]: ST Group [16] : Outlet enthalpy | kJ/kg | 3213.314 | 3214.521
72¦79¦93¦~16~7~15~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust volume flow | m^3/s | 12.0183 | 11.2877
72¦79¦93¦~16~7~18~~-11~ | ST Assembly [1]: ST Group [16] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~16~7~17~~-11~ | ST Assembly [1]: ST Group [16] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~16~3~7~~-11~ | ST Assembly [1]: ST Group [16] : Actual flow function | m^2 | 0.011633 | 0.010957
93¦~16~3~10~~-11~ | ST Assembly [1]: ST Group [16] : Actual pressure ratio (blading) |  | 3.1232 | 3.1117
93¦~16~3~3~~-11~ | ST Assembly [1]: ST Group [16] : Dry step efficiency | % | 73.4972 | 73.4479
93¦~16~3~1~~-11~ | ST Assembly [1]: ST Group [16] : Group overall efficiency | % | 75.6653 | 75.6098
93¦~16~3~30~~-11~ | ST Assembly [1]: ST Group [16] : Group blading efficiency | % | 75.6653 | 75.6098
93¦~16~3~50~~-11~ | ST Assembly [1]: ST Group [16] : Expansion power | kW | 30414.1699 | 27640.7949
93¦~16~3~8~~-11~ | ST Assembly [1]: ST Group [16] : Shaft power | kW | 30338.1348 | 27571.6953
93¦~16~3~9~~-11~ | ST Assembly [1]: ST Group [16] : Mechanical loss | kW | 76.0354 | 69.1019
82¦71¦~17~10~3~~-11~ | ST Assembly [1]: ST Group [17] : Mode |  | Design | Design
82¦71¦~17~10~4~~-11~ | ST Assembly [1]: ST Group [17] : Type of inlet control |  | Sliding | Sliding
93¦~17~3~29~~-11~ | ST Assembly [1]: ST Group [17] : Steam supply pressure | bar | 27.68 | 26.8987
93¦~17~3~11~~-11~ | ST Assembly [1]: ST Group [17] : Inlet pressure | bar | 27.68 | 26.8987
93¦~17~3~12~~-11~ | ST Assembly [1]: ST Group [17] : Inlet temperature | C | 390.2057 | 390.1317
93¦~17~3~14~~-11~ | ST Assembly [1]: ST Group [17] : Inlet flow | t/h | 389.0559 | 354.7009
93¦~17~3~13~~-11~ | ST Assembly [1]: ST Group [17] : Inlet enthalpy | kJ/kg | 3213.314 | 3214.521
93¦~17~3~16~~-11~ | ST Assembly [1]: ST Group [17] : Expansion massflow | t/h | 389.0559 | 354.7009
93¦~17~3~4~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial pressure | bar | 27.68 | 26.8987
93¦~17~3~15~~-11~ | ST Assembly [1]: ST Group [17] : Expansion initial enthalpy | kJ/kg | 3213.314 | 3214.521
93¦~17~3~6~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end pressure (before Exhaust Loss) | bar | 18.75 | 17.9587
93¦~17~3~25~~-11~ | ST Assembly [1]: ST Group [17] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 3127.1702 | 3125.2595
93¦~17~3~21~~-11~ | ST Assembly [1]: ST Group [17] : Outlet pressure | bar | 18.75 | 17.9587
93¦~17~3~22~~-11~ | ST Assembly [1]: ST Group [17] : Outlet temperature | C | 344.0994 | 342.4655
93¦~17~3~24~~-11~ | ST Assembly [1]: ST Group [17] : Outlet flow | t/h | 389.0559 | 354.7009
93¦~17~3~23~~-11~ | ST Assembly [1]: ST Group [17] : Outlet enthalpy | kJ/kg | 3127.1702 | 3125.2595
72¦79¦93¦~17~7~15~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust volume flow | m^3/s | 15.8415 | 15.0575
72¦79¦93¦~17~7~18~~-11~ | ST Assembly [1]: ST Group [17] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~17~7~17~~-11~ | ST Assembly [1]: ST Group [17] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~17~3~7~~-11~ | ST Assembly [1]: ST Group [17] : Actual flow function | m^2 | 0.031705 | 0.029761
93¦~17~3~10~~-11~ | ST Assembly [1]: ST Group [17] : Actual pressure ratio (blading) |  | 1.4763 | 1.4978
93¦~17~3~3~~-11~ | ST Assembly [1]: ST Group [17] : Dry step efficiency | % | 78.1537 | 78.1059
93¦~17~3~1~~-11~ | ST Assembly [1]: ST Group [17] : Group overall efficiency | % | 78.5327 | 78.5001
93¦~17~3~30~~-11~ | ST Assembly [1]: ST Group [17] : Group blading efficiency | % | 78.5327 | 78.5001
93¦~17~3~50~~-11~ | ST Assembly [1]: ST Group [17] : Expansion power | kW | 9309.7842 | 8794.8838
93¦~17~3~8~~-11~ | ST Assembly [1]: ST Group [17] : Shaft power | kW | 9286.5107 | 8772.8965
93¦~17~3~9~~-11~ | ST Assembly [1]: ST Group [17] : Mechanical loss | kW | 23.2744 | 21.9872
82¦71¦~18~10~3~~-11~ | ST Assembly [1]: ST Group [18] : Mode |  | Design | Design
82¦71¦~18~10~4~~-11~ | ST Assembly [1]: ST Group [18] : Type of inlet control |  | Sliding | Sliding
93¦~18~3~29~~-11~ | ST Assembly [1]: ST Group [18] : Steam supply pressure | bar | 18.75 | 17.9587
93¦~18~3~11~~-11~ | ST Assembly [1]: ST Group [18] : Inlet pressure | bar | 18.75 | 17.9587
93¦~18~3~12~~-11~ | ST Assembly [1]: ST Group [18] : Inlet temperature | C | 344.0994 | 342.4655
93¦~18~3~14~~-11~ | ST Assembly [1]: ST Group [18] : Inlet flow | t/h | 358.384 | 326.6145
93¦~18~3~13~~-11~ | ST Assembly [1]: ST Group [18] : Inlet enthalpy | kJ/kg | 3127.1702 | 3125.2595
93¦~18~3~16~~-11~ | ST Assembly [1]: ST Group [18] : Expansion massflow | t/h | 358.384 | 326.6145
93¦~18~3~4~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial pressure | bar | 18.75 | 17.9587
93¦~18~3~15~~-11~ | ST Assembly [1]: ST Group [18] : Expansion initial enthalpy | kJ/kg | 3127.1702 | 3125.2595
93¦~18~3~6~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end pressure (before Exhaust Loss) | bar | 6.36 | 6.1804
93¦~18~3~25~~-11~ | ST Assembly [1]: ST Group [18] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2905.8972 | 2907.1526
93¦~18~3~21~~-11~ | ST Assembly [1]: ST Group [18] : Outlet pressure | bar | 6.36 | 6.1804
93¦~18~3~22~~-11~ | ST Assembly [1]: ST Group [18] : Outlet temperature | C | 226.2648 | 226.4971
93¦~18~3~24~~-11~ | ST Assembly [1]: ST Group [18] : Outlet flow | t/h | 358.384 | 326.6145
93¦~18~3~23~~-11~ | ST Assembly [1]: ST Group [18] : Outlet enthalpy | kJ/kg | 2905.8972 | 2907.1526
72¦79¦93¦~18~7~15~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust volume flow | m^3/s | 35.0919 | 32.9548
72¦79¦93¦~18~7~18~~-11~ | ST Assembly [1]: ST Group [18] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~18~7~17~~-11~ | ST Assembly [1]: ST Group [18] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~18~3~7~~-11~ | ST Assembly [1]: ST Group [18] : Actual flow function | m^2 | 0.041681 | 0.039632
93¦~18~3~10~~-11~ | ST Assembly [1]: ST Group [18] : Actual pressure ratio (blading) |  | 2.9481 | 2.9057
93¦~18~3~3~~-11~ | ST Assembly [1]: ST Group [18] : Dry step efficiency | % | 82.7075 | 82.6348
93¦~18~3~1~~-11~ | ST Assembly [1]: ST Group [18] : Group overall efficiency | % | 84.0439 | 83.9584
93¦~18~3~30~~-11~ | ST Assembly [1]: ST Group [18] : Group blading efficiency | % | 84.0439 | 83.9584
93¦~18~3~50~~-11~ | ST Assembly [1]: ST Group [18] : Expansion power | kW | 22028.3203 | 19788.3203
93¦~18~3~8~~-11~ | ST Assembly [1]: ST Group [18] : Shaft power | kW | 21973.248 | 19738.8516
93¦~18~3~9~~-11~ | ST Assembly [1]: ST Group [18] : Mechanical loss | kW | 55.0707 | 49.4708
82¦71¦~19~10~3~~-11~ | ST Assembly [1]: ST Group [19] : Mode |  | Design | Design
82¦71¦~19~10~4~~-11~ | ST Assembly [1]: ST Group [19] : Type of inlet control |  | Sliding | Sliding
93¦~19~3~29~~-11~ | ST Assembly [1]: ST Group [19] : Steam supply pressure | bar | 6.36 | 6.1804
93¦~19~3~11~~-11~ | ST Assembly [1]: ST Group [19] : Inlet pressure | bar | 6.36 | 6.1804
93¦~19~3~12~~-11~ | ST Assembly [1]: ST Group [19] : Inlet temperature | C | 226.2648 | 226.4971
93¦~19~3~14~~-11~ | ST Assembly [1]: ST Group [19] : Inlet flow | t/h | 356.9803 | 325.3288
93¦~19~3~13~~-11~ | ST Assembly [1]: ST Group [19] : Inlet enthalpy | kJ/kg | 2905.8972 | 2907.1526
93¦~19~3~16~~-11~ | ST Assembly [1]: ST Group [19] : Expansion massflow | t/h | 356.9803 | 325.3288
93¦~19~3~4~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial pressure | bar | 6.36 | 6.1804
93¦~19~3~15~~-11~ | ST Assembly [1]: ST Group [19] : Expansion initial enthalpy | kJ/kg | 2905.8972 | 2907.1526
93¦~19~3~6~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end pressure (before Exhaust Loss) | bar | 5.5 | 5.3442
93¦~19~3~25~~-11~ | ST Assembly [1]: ST Group [19] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2879.03 | 2880.2673
93¦~19~3~21~~-11~ | ST Assembly [1]: ST Group [19] : Outlet pressure | bar | 5.5 | 5.3442
93¦~19~3~22~~-11~ | ST Assembly [1]: ST Group [19] : Outlet temperature | C | 211.9436 | 212.1814
93¦~19~3~24~~-11~ | ST Assembly [1]: ST Group [19] : Outlet flow | t/h | 356.9803 | 325.3288
93¦~19~3~23~~-11~ | ST Assembly [1]: ST Group [19] : Outlet enthalpy | kJ/kg | 2879.03 | 2880.2673
72¦79¦93¦~19~7~15~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust volume flow | m^3/s | 39.2905 | 36.9004
72¦79¦93¦~19~7~18~~-11~ | ST Assembly [1]: ST Group [19] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~19~7~17~~-11~ | ST Assembly [1]: ST Group [19] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~19~3~7~~-11~ | ST Assembly [1]: ST Group [19] : Actual flow function | m^2 | 0.11055 | 0.10374
93¦~19~3~10~~-11~ | ST Assembly [1]: ST Group [19] : Actual pressure ratio (blading) |  | 1.1564 | 1.1565
93¦~19~3~3~~-11~ | ST Assembly [1]: ST Group [19] : Dry step efficiency | % | 83.8913 | 83.7892
93¦~19~3~1~~-11~ | ST Assembly [1]: ST Group [19] : Group overall efficiency | % | 83.8911 | 83.7896
93¦~19~3~30~~-11~ | ST Assembly [1]: ST Group [19] : Group blading efficiency | % | 83.8911 | 83.7896
93¦~19~3~50~~-11~ | ST Assembly [1]: ST Group [19] : Expansion power | kW | 2664.2161 | 2429.6365
93¦~19~3~8~~-11~ | ST Assembly [1]: ST Group [19] : Shaft power | kW | 2657.5557 | 2423.5625
93¦~19~3~9~~-11~ | ST Assembly [1]: ST Group [19] : Mechanical loss | kW | 6.6605 | 6.0741
82¦71¦~20~10~3~~-11~ | ST Assembly [1]: ST Group [20] : Mode |  | Design | Design
82¦71¦~20~10~4~~-11~ | ST Assembly [1]: ST Group [20] : Type of inlet control |  | Sliding | Sliding
93¦~20~3~29~~-11~ | ST Assembly [1]: ST Group [20] : Steam supply pressure | bar | 5.5 | 5.3442
93¦~20~3~11~~-11~ | ST Assembly [1]: ST Group [20] : Inlet pressure | bar | 5.5 | 5.3442
93¦~20~3~12~~-11~ | ST Assembly [1]: ST Group [20] : Inlet temperature | C | 211.9436 | 212.1814
93¦~20~3~14~~-11~ | ST Assembly [1]: ST Group [20] : Inlet flow | t/h | 337.602 | 307.1717
93¦~20~3~13~~-11~ | ST Assembly [1]: ST Group [20] : Inlet enthalpy | kJ/kg | 2879.03 | 2880.2673
93¦~20~3~16~~-11~ | ST Assembly [1]: ST Group [20] : Expansion massflow | t/h | 337.602 | 307.1717
93¦~20~3~4~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial pressure | bar | 5.5 | 5.3442
93¦~20~3~15~~-11~ | ST Assembly [1]: ST Group [20] : Expansion initial enthalpy | kJ/kg | 2879.03 | 2880.2673
93¦~20~3~6~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end pressure (before Exhaust Loss) | bar | 2.18 | 2.1184
93¦~20~3~25~~-11~ | ST Assembly [1]: ST Group [20] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2721.9922 | 2723.0752
93¦~20~3~21~~-11~ | ST Assembly [1]: ST Group [20] : Outlet pressure | bar | 2.18 | 2.1184
93¦~20~3~22~~-11~ | ST Assembly [1]: ST Group [20] : Outlet temperature | C | 128.3819 | 128.5931
93¦~20~3~24~~-11~ | ST Assembly [1]: ST Group [20] : Outlet flow | t/h | 337.602 | 307.1717
93¦~20~3~23~~-11~ | ST Assembly [1]: ST Group [20] : Outlet enthalpy | kJ/kg | 2721.9922 | 2723.0752
72¦79¦93¦~20~7~15~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust volume flow | m^3/s | 77.8079 | 72.9485
72¦79¦93¦~20~7~18~~-11~ | ST Assembly [1]: ST Group [20] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~20~7~17~~-11~ | ST Assembly [1]: ST Group [20] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~20~3~7~~-11~ | ST Assembly [1]: ST Group [20] : Actual flow function | m^2 | 0.11919 | 0.11168
93¦~20~3~10~~-11~ | ST Assembly [1]: ST Group [20] : Actual pressure ratio (blading) |  | 2.5229 | 2.5227
93¦~20~3~3~~-11~ | ST Assembly [1]: ST Group [20] : Dry step efficiency | % | 85.7638 | 85.7396
93¦~20~3~1~~-11~ | ST Assembly [1]: ST Group [20] : Group overall efficiency | % | 86.6021 | 86.5964
93¦~20~3~30~~-11~ | ST Assembly [1]: ST Group [20] : Group blading efficiency | % | 86.6021 | 86.5964
93¦~20~3~50~~-11~ | ST Assembly [1]: ST Group [20] : Expansion power | kW | 14726.9775 | 13412.7168
93¦~20~3~8~~-11~ | ST Assembly [1]: ST Group [20] : Shaft power | kW | 14690.1602 | 13379.1855
93¦~20~3~9~~-11~ | ST Assembly [1]: ST Group [20] : Mechanical loss | kW | 36.8174 | 33.5318
82¦71¦~36~10~3~~-11~ | ST Assembly [1]: ST Group [36] : Mode |  | Design | Design
82¦71¦~36~10~4~~-11~ | ST Assembly [1]: ST Group [36] : Type of inlet control |  | Sliding | Sliding
93¦~36~3~29~~-11~ | ST Assembly [1]: ST Group [36] : Steam supply pressure | bar | 2.18 | 2.1184
93¦~36~3~11~~-11~ | ST Assembly [1]: ST Group [36] : Inlet pressure | bar | 2.18 | 2.1184
93¦~36~3~12~~-11~ | ST Assembly [1]: ST Group [36] : Inlet temperature | C | 128.3819 | 128.5931
93¦~36~3~14~~-11~ | ST Assembly [1]: ST Group [36] : Inlet flow | t/h | 326.7362 | 297.3847
93¦~36~3~13~~-11~ | ST Assembly [1]: ST Group [36] : Inlet enthalpy | kJ/kg | 2721.9922 | 2723.0752
93¦~36~3~16~~-11~ | ST Assembly [1]: ST Group [36] : Expansion massflow | t/h | 326.7362 | 297.3847
93¦~36~3~4~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial pressure | bar | 2.18 | 2.1184
93¦~36~3~15~~-11~ | ST Assembly [1]: ST Group [36] : Expansion initial enthalpy | kJ/kg | 2721.9922 | 2723.0752
93¦~36~3~6~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end pressure (before Exhaust Loss) | bar | 1.34 | 1.3022
93¦~36~3~25~~-11~ | ST Assembly [1]: ST Group [36] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2648.6372 | 2650.0066
93¦~36~3~21~~-11~ | ST Assembly [1]: ST Group [36] : Outlet pressure | bar | 1.34 | 1.3022
93¦~36~3~22~~-11~ | ST Assembly [1]: ST Group [36] : Outlet temperature | C | 107.9986 | 107.1588
93¦~36~3~24~~-11~ | ST Assembly [1]: ST Group [36] : Outlet flow | t/h | 326.7362 | 297.3847
93¦~36~3~23~~-11~ | ST Assembly [1]: ST Group [36] : Outlet enthalpy | kJ/kg | 2648.6372 | 2650.0066
72¦79¦93¦~36~7~15~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust volume flow | m^3/s | 114.8681 | 107.5173
72¦79¦93¦~36~7~18~~-11~ | ST Assembly [1]: ST Group [36] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~36~7~17~~-11~ | ST Assembly [1]: ST Group [36] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~36~3~7~~-11~ | ST Assembly [1]: ST Group [36] : Actual flow function | m^2 | 0.26514 | 0.2485
93¦~36~3~10~~-11~ | ST Assembly [1]: ST Group [36] : Actual pressure ratio (blading) |  | 1.6269 | 1.6268
93¦~36~3~3~~-11~ | ST Assembly [1]: ST Group [36] : Dry step efficiency | % | 86.6278 | 86.3211
93¦~36~3~1~~-11~ | ST Assembly [1]: ST Group [36] : Group overall efficiency | % | 86.628 | 86.3209
93¦~36~3~30~~-11~ | ST Assembly [1]: ST Group [36] : Group blading efficiency | % | 86.628 | 86.3209
93¦~36~3~50~~-11~ | ST Assembly [1]: ST Group [36] : Expansion power | kW | 6657.7983 | 6036.0474
93¦~36~3~8~~-11~ | ST Assembly [1]: ST Group [36] : Shaft power | kW | 6641.1538 | 6020.9575
93¦~36~3~9~~-11~ | ST Assembly [1]: ST Group [36] : Mechanical loss | kW | 16.6445 | 15.0901
82¦71¦~37~10~3~~-11~ | ST Assembly [1]: ST Group [37] : Mode |  | Design | Design
82¦71¦~37~10~4~~-11~ | ST Assembly [1]: ST Group [37] : Type of inlet control |  | Sliding | Sliding
93¦~37~3~29~~-11~ | ST Assembly [1]: ST Group [37] : Steam supply pressure | bar | 1.34 | 1.3022
93¦~37~3~11~~-11~ | ST Assembly [1]: ST Group [37] : Inlet pressure | bar | 1.34 | 1.3022
93¦~37~3~12~~-11~ | ST Assembly [1]: ST Group [37] : Inlet temperature | C | 107.9986 | 107.1588
93¦~37~3~14~~-11~ | ST Assembly [1]: ST Group [37] : Inlet flow | t/h | 307.5682 | 280.0619
93¦~37~3~13~~-11~ | ST Assembly [1]: ST Group [37] : Inlet enthalpy | kJ/kg | 2648.6372 | 2650.0066
93¦~37~3~16~~-11~ | ST Assembly [1]: ST Group [37] : Expansion massflow | t/h | 307.5682 | 280.0619
93¦~37~3~4~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial pressure | bar | 1.34 | 1.3022
93¦~37~3~15~~-11~ | ST Assembly [1]: ST Group [37] : Expansion initial enthalpy | kJ/kg | 2648.6372 | 2650.0066
93¦~37~3~6~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end pressure (before Exhaust Loss) | bar | 0.4 | 0.3887
93¦~37~3~25~~-11~ | ST Assembly [1]: ST Group [37] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2484.623 | 2486.1553
93¦~37~3~21~~-11~ | ST Assembly [1]: ST Group [37] : Outlet pressure | bar | 0.4 | 0.3887
93¦~37~3~22~~-11~ | ST Assembly [1]: ST Group [37] : Outlet temperature | C | 75.8568 | 75.1698
93¦~37~3~24~~-11~ | ST Assembly [1]: ST Group [37] : Outlet flow | t/h | 307.5682 | 280.0619
93¦~37~3~23~~-11~ | ST Assembly [1]: ST Group [37] : Outlet enthalpy | kJ/kg | 2484.623 | 2486.1553
72¦79¦93¦~37~7~15~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust volume flow | m^3/s | 318.8601 | 298.6268
72¦79¦93¦~37~7~18~~-11~ | ST Assembly [1]: ST Group [37] : Exhaust loss | kJ/kg | 0 | 0
72¦79¦93¦~37~7~17~~-11~ | ST Assembly [1]: ST Group [37] : Dry exhaust loss | kJ/kg | 0 | 0
93¦~37~3~7~~-11~ | ST Assembly [1]: ST Group [37] : Actual flow function | m^2 | 0.3897 | 0.36526
93¦~37~3~10~~-11~ | ST Assembly [1]: ST Group [37] : Actual pressure ratio (blading) |  | 3.35 | 3.3501
93¦~37~3~3~~-11~ | ST Assembly [1]: ST Group [37] : Dry step efficiency | % | 88.0421 | 87.8888
93¦~37~3~1~~-11~ | ST Assembly [1]: ST Group [37] : Group overall efficiency | % | 85.8082 | 85.7703
93¦~37~3~30~~-11~ | ST Assembly [1]: ST Group [37] : Group blading efficiency | % | 85.8082 | 85.7703
93¦~37~3~50~~-11~ | ST Assembly [1]: ST Group [37] : Expansion power | kW | 14012.8779 | 12747.0039
93¦~37~3~8~~-11~ | ST Assembly [1]: ST Group [37] : Shaft power | kW | 13977.8457 | 12715.1357
93¦~37~3~9~~-11~ | ST Assembly [1]: ST Group [37] : Mechanical loss | kW | 35.0322 | 31.8675
82¦71¦~39~10~3~~-11~ | ST Assembly [1]: ST Group [39] : Mode |  | Design | Design
82¦71¦~39~10~4~~-11~ | ST Assembly [1]: ST Group [39] : Type of inlet control |  | Sliding | Sliding
93¦~39~3~29~~-11~ | ST Assembly [1]: ST Group [39] : Steam supply pressure | bar | 0.4 | 0.3887
93¦~39~3~11~~-11~ | ST Assembly [1]: ST Group [39] : Inlet pressure | bar | 0.4 | 0.3887
93¦~39~3~12~~-11~ | ST Assembly [1]: ST Group [39] : Inlet temperature | C | 75.8568 | 75.1698
93¦~39~3~14~~-11~ | ST Assembly [1]: ST Group [39] : Inlet flow | t/h | 293.6464 | 267.7225
93¦~39~3~13~~-11~ | ST Assembly [1]: ST Group [39] : Inlet enthalpy | kJ/kg | 2484.623 | 2486.1553
93¦~39~3~16~~-11~ | ST Assembly [1]: ST Group [39] : Expansion massflow | t/h | 293.6464 | 267.7225
93¦~39~3~4~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial pressure | bar | 0.4 | 0.3887
93¦~39~3~15~~-11~ | ST Assembly [1]: ST Group [39] : Expansion initial enthalpy | kJ/kg | 2484.623 | 2486.1553
93¦~39~3~6~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end pressure (before Exhaust Loss) | bar | 0.0985 | 0.0985
93¦~39~3~25~~-11~ | ST Assembly [1]: ST Group [39] : Expansion end enthalpy (before Exhaust Loss) | kJ/kg | 2325.2444 | 2329.9683
93¦~39~3~21~~-11~ | ST Assembly [1]: ST Group [39] : Outlet pressure | bar | 0.0985 | 0.0985
93¦~39~3~22~~-11~ | ST Assembly [1]: ST Group [39] : Outlet temperature | C | 45.5122 | 45.5122
93¦~39~3~24~~-11~ | ST Assembly [1]: ST Group [39] : Outlet flow | t/h | 293.8842 | 267.9219
93¦~39~3~23~~-11~ | ST Assembly [1]: ST Group [39] : Outlet enthalpy | kJ/kg | 2337.2493 | 2341.3037
72¦79¦76¦~39~6~2~~-11~ | ST Assembly [1]: ST Group [39] : Number of exhaust ends |  | 1 | 1
72¦79¦93¦~39~7~15~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust volume flow per end | m^3/s | 1082.817 | 989.4077
72¦79¦91¦~39~5~3~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus area | m^2 | 5.9214 | 5.5755
72¦79¦93¦~39~7~16~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust annulus velocity | m/s | 182.864 | 177.4572
72¦79¦91¦~39~5~1~~-11~ | ST Assembly [1]: ST Group [39] : Last stage pitch diameter | mm | 2429.6218 | 2371.8689
72¦79¦91¦~39~5~2~~-11~ | ST Assembly [1]: ST Group [39] : Last stage blade length | mm | 775.7797 | 748.2404
72¦79¦93¦~39~7~18~~-11~ | ST Assembly [1]: ST Group [39] : Exhaust loss | kJ/kg | 11.6521 | 11.0139
72¦79¦93¦~39~7~17~~-11~ | ST Assembly [1]: ST Group [39] : Dry exhaust loss | kJ/kg | 16.1448 | 15.2057
93¦~39~3~7~~-11~ | ST Assembly [1]: ST Group [39] : Actual flow function | m^2 | 1.1407 | 1.0706
93¦~39~3~10~~-11~ | ST Assembly [1]: ST Group [39] : Actual pressure ratio (blading) |  | 4.0609 | 3.9462
93¦~39~3~3~~-11~ | ST Assembly [1]: ST Group [39] : Dry step efficiency | % | 88.0245 | 87.8671
93¦~39~3~1~~-11~ | ST Assembly [1]: ST Group [39] : Group overall efficiency | % | 76.0904 | 76.2584
93¦~39~3~30~~-11~ | ST Assembly [1]: ST Group [39] : Group blading efficiency | % | 82.0921 | 82.0439
93¦~39~3~50~~-11~ | ST Assembly [1]: ST Group [39] : Expansion power | kW | 12050.0088 | 10796.3066
93¦~39~3~8~~-11~ | ST Assembly [1]: ST Group [39] : Shaft power | kW | 12019.8828 | 10769.3164
93¦~39~3~9~~-11~ | ST Assembly [1]: ST Group [39] : Mechanical loss | kW | 30.125 | 26.9907
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~3~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (source) | bar | 86.45 | 83.7
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~5~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Pressure (sink) | bar | 2.18 | 2.1184
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (source) | C | 536.4592 | 535.4362
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Temperature (sink) | C | 497.5313 | 497.6638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 1 to LP section inlet: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~3~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (source) | bar | 2.18 | 2.1184
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~5~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (source) | C | 497.5313 | 497.6638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Temperature (sink) | C | 497.0556 | 497.2196
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: Valve Stem leak 2 to SSR: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~1~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~3~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (source) | bar | 86.45 | 83.7
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~5~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Pressure (sink) | bar | 2.18 | 2.1184
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (source) | C | 536.4592 | 535.4362
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~4~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Temperature (sink) | C | 497.5313 | 497.6638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~4~2~-4100~ | ST Assembly [1]: HPT HP leak 1 to LP section inlet: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~1~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Leakage flow C-factor | m^2 | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~3~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (source) | bar | 2.18 | 2.1184
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Pressure (sink) | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~1~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (source) | C | 497.5313 | 497.6638
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~10~2~5~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Temperature (sink) | C | 497.0556 | 497.2196
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: HPT HP leak 2 to SSR: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦~16~4~8~~-4100~ | ST Assembly [1]: SSR pressure | bar | 1.241 | 1.241
86¦87¦68¦86¦86¦~16~4~9~~-4100~ | ST Assembly [1]: SSR temperature | C | 148.8893 | 148.8893
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~1~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~2~2~-4100~ | ST Assembly [1]: SSR leakage in (Valve Stem leak 2): Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~1~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Mass flow | t/h | 0 | 0
86¦87¦68¦86¦86¦98¦86¦79¦78¦~16~3~5~2~-4100~ | ST Assembly [1]: SSR leakage in (HPT HP leak 2): Enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦~16~4~17~~-4100~ | ST Assembly [1]: SSR make-up steam mass flow | t/h | 0.37875 | 0.27995
86¦87¦68¦86¦86¦~16~4~18~~-4100~ | ST Assembly [1]: SSR make-up steam enthalpy | kJ/kg | 3482.1716 | 3482.5215
86¦87¦68¦86¦86¦~16~4~15~~-4100~ | ST Assembly [1]: SSR desuperheating water mass flow | t/h | 0.099178 | 0.073344
86¦87¦68¦86¦86¦~16~4~16~~-4100~ | ST Assembly [1]: SSR desuperheating water enthalpy | kJ/kg | 62.798 | 62.798
86¦87¦68¦86¦86¦~16~10~2~~-4100~ | ST Assembly [1]: Sealing steam to LPT exhaust: Mass flow | t/h | 0.23779 | 0.19943
86¦87¦68¦86¦86¦~16~10~3~~-4100~ | ST Assembly [1]: Sealing steam packing exhaust (destination Discharged): Mass flow | t/h | 0.24014 | 0.15387
86¦87¦68¦86¦86¦~16~4~14~~-4100~ | ST Assembly [1]: SSR excess sealing steam (destination LPT exhaust): Mass flow | t/h | 0 | 0
93¦~7~3~112~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (LHV) | % | 92.5832 | 95.3551
93¦~7~3~111~~-4200~ | Boiler Assembly [1]: Boiler fuel efficiency (HHV) | % | 83.8211 | 87.7283
93¦~7~3~102~~-4200~ | Boiler Assembly [1]: Fuel input (LHV) | MW | 309.1231 | 273.6078
93¦~7~3~103~~-4200~ | Boiler Assembly [1]: Fuel input (HHV) | MW | 341.4366 | 297.3943
93¦~7~3~105~~-4200~ | Boiler Assembly [1]: Fuel massflow | t/h | 73.3954 | 63.928
93¦~7~3~101~~-4200~ | Boiler Assembly [1]: Total heat transfer to water and steam | kW | 286195.9062 | 260898.9062
93¦~7~3~155~~-4200~ | Boiler Assembly [1]: HP steam pressure | bar | 88.0061 | 85.2066
93¦~7~3~156~~-4200~ | Boiler Assembly [1]: HP steam temperature | C | 537.116 | 536.0752
93¦~7~3~157~~-4200~ | Boiler Assembly [1]: HP steam massflow | t/h | 408.2104 | 372.1087
93¦~7~3~158~~-4200~ | Boiler Assembly [1]: HP steam enthalpy | kJ/kg | 3482.1716 | 3482.5215
93¦~7~3~151~~-4200~ | Boiler Assembly [1]: Water pressure | bar | 118.2992 | 114.5446
93¦~7~3~152~~-4200~ | Boiler Assembly [1]: Water temperature | C | 226.1392 | 226.1398
93¦~7~3~153~~-4200~ | Boiler Assembly [1]: Water massflow | t/h | 388.6693 | 354.5441
93¦~7~3~154~~-4200~ | Boiler Assembly [1]: Water enthalpy | kJ/kg | 974.4664 | 974.3673
~1~2~0~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Pressure | bar | 0.9749 | 0.9749
~1~2~1~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Temperature | C | 143.6583 | 90.6411
~1~2~2~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mass flow | t/h | 516.8241 | 431.4364
~1~2~22~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash flow | t/h | 4.4783 | 3.9456
~1~2~16~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Fly ash enthalpy | kJ/kg | 97.8019 | 51.6679
~1~2~18~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Relative humidity | % | 4.1638 | 21.2106
~1~2~20~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Entropy | kJ/kg-C | 0.66494 | 0.51218
~1~2~3~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Enthalpy | kJ/kg | 130.111 | 70.8569
~1~2~19~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Molecular weight | M.W. | 28.6375 | 28.9224
~1~2~4~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO2 mass flow | t/h | 105.237 | 91.6505
~1~2~5~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Volume flow | m^3/s | 178.2093 | 128.5644
~1~2~101~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Density | kg/m^3 | 0.80558 | 0.93217
~1~2~6~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of N2 | % | 65.91 | 66.0719
~1~2~7~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of O2 | % | 2.9438 | 3.541
~1~2~8~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~2~9~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O | % | 17.1003 | 15.6285
~1~2~10~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of H2O liquid | % | 0 | 0
~1~2~11~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of Ar | % | 0.79282 | 0.79472
~1~2~12~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~2~14~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~2~23~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: HCl mass flow | kg/hr | 0 | 0
~1~2~24~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: NOx mass flow | kg/hr | 0 | 0
~1~2~25~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: CO mass flow | kg/hr | 0 | 0
~1~2~26~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: UHC mass flow | kg/hr | 0 | 0
~1~2~29~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Hg mass flow | kg/hr | 0 | 0
~1~2~32~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Dry Oxygen | % | 3.5511 | 4.197
~1~2~31~~-5001~ | 2 - Flue gas outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Inlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~4~0~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Pressure | bar | 1.0944 | 1.0944
~1~4~1~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Temperature | C | 40.6977 | 38.4551
~1~4~2~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mass flow | t/h | 109.9377 | 91.1703
~1~4~22~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~4~16~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~4~18~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Relative humidity | % | 40.3933 | 47.801
~1~4~20~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~4~3~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~4~19~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~4~4~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~4~5~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Volume flow | m^3/s | 25.4101 | 20.9331
~1~4~101~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Density | kg/m^3 | 1.2018 | 1.2098
~1~4~6~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~4~7~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~4~8~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~4~9~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~4~10~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~4~11~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~4~12~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~4~14~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~4~23~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~4~24~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~4~25~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~4~26~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~4~29~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~4~32~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~4~31~~-5001~ | 4 - Outlet of Boiler Assembly [1]: Fan [72] - PA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~7~0~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~7~1~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~7~2~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mass flow | t/h | 114.4249 | 94.8916
~1~7~22~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash flow | t/h | 0 | 0
~1~7~16~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~7~18~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~7~20~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~7~3~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~7~19~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~7~4~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~7~5~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Volume flow | m^3/s | 27.8128 | 22.9125
~1~7~101~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~7~6~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~7~7~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~7~8~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~7~9~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~7~10~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~7~11~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~7~12~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~7~14~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~7~23~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~7~24~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~7~25~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~7~26~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~7~29~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~7~32~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~7~31~~-5001~ | 7 - Outlet of Gas/Air Source [8] - PA #1 -> Inlet of Boiler Assembly [1]: Fan [9] - SA Fan #1: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~1~8~0~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Pressure | bar | 1.1794 | 1.1794
~1~8~1~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Temperature | C | 49.0609 | 46.7577
~1~8~2~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mass flow | t/h | 114.4249 | 94.8916
~1~8~22~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash flow | t/h | 0 | 0
~1~8~16~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~8~18~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Relative humidity | % | 28.3036 | 33.3628
~1~8~20~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~8~3~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~8~19~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~8~4~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~8~5~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Volume flow | m^3/s | 25.1944 | 20.7552
~1~8~101~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Density | kg/m^3 | 1.2616 | 1.27
~1~8~6~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~8~7~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~8~8~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~8~9~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~8~10~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of H2O liquid | % | 0 | 0
~1~8~11~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~8~12~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Mole percent of SO2 | % | 0 | 0
~1~8~14~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~8~23~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: HCl mass flow | kg/hr | 0 | 0
~1~8~24~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: NOx mass flow | kg/hr | 0 | 0
~1~8~25~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: CO mass flow | kg/hr | 0 | 0
~1~8~26~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: UHC mass flow | kg/hr | 0 | 0
~1~8~29~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Hg mass flow | kg/hr | 0 | 0
~1~8~32~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~8~31~~-5001~ | 8 - Outlet of Boiler Assembly [1]: Fan [9] - SA Fan #1 -> Inlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~1~13~0~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 0.98736 | 0.98736
~1~13~1~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 281.8529 | 231.14
~1~13~2~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 516.8241 | 431.4364
~1~13~22~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 4.4783 | 3.9456
~1~13~16~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 233.9566 | 181.5628
~1~13~18~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 0 | 0.54021
~1~13~20~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.98512 | 0.86955
~1~13~3~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 286.5504 | 226.3291
~1~13~19~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~13~4~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 105.237 | 91.6505
~1~13~5~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 234.3001 | 175.9674
~1~13~101~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 0.61273 | 0.68106
~1~13~6~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 65.91 | 66.0719
~1~13~7~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 2.9438 | 3.541
~1~13~8~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~13~9~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~13~10~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~13~11~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~13~12~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~13~14~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~13~23~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~13~24~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~13~25~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~13~26~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~13~29~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~13~32~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 3.5511 | 4.197
~1~13~31~~-5001~ | 13 - Gas outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Flue gas inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~14~0~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 0.99235 | 0.99234
~1~14~1~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 731.6876 | 718.2131
~1~14~2~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 516.8241 | 431.4364
~1~14~22~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash flow | t/h | 4.4783 | 3.9456
~1~14~16~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Fly ash enthalpy | kJ/kg | 770.9417 | 754.0746
~1~14~18~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Relative humidity | % | 0 | 0
~1~14~20~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 1.7073 | 1.677
~1~14~3~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 838.0667 | 813.4511
~1~14~19~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~14~4~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO2 mass flow | t/h | 105.237 | 91.6505
~1~14~5~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Volume flow | m^3/s | 422.0713 | 344.1893
~1~14~101~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 0.34014 | 0.34819
~1~14~6~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~14~7~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~14~8~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~14~9~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~14~10~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of H2O liquid | % | 0 | 0
~1~14~11~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~14~12~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~14~14~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~14~23~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: HCl mass flow | kg/hr | 0 | 0
~1~14~24~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: NOx mass flow | kg/hr | 0 | 0
~1~14~25~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: CO mass flow | kg/hr | 0 | 0
~1~14~26~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: UHC mass flow | kg/hr | 0 | 0
~1~14~29~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Hg mass flow | kg/hr | 0 | 0
~1~14~32~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dry Oxygen | % | 3.5511 | 4.197
~1~14~31~~-5001~ | 14 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~15~0~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 0.98985 | 0.98985
~1~15~1~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 524.1159 | 494.2415
~1~15~2~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 516.8241 | 431.4364
~1~15~22~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash flow | t/h | 4.4783 | 3.9456
~1~15~16~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Fly ash enthalpy | kJ/kg | 512.7029 | 476.4297
~1~15~18~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Relative humidity | % | 0 | 0
~1~15~20~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 1.4158 | 1.3588
~1~15~3~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 575.6496 | 534.1673
~1~15~19~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Molecular weight | M.W. | 28.6375 | 28.9224
~1~15~4~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO2 mass flow | t/h | 105.237 | 91.6505
~1~15~5~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Volume flow | m^3/s | 335.7263 | 267.1
~1~15~101~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 0.42762 | 0.44868
~1~15~6~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of N2 | % | 65.91 | 66.0719
~1~15~7~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of O2 | % | 2.9438 | 3.541
~1~15~8~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~15~9~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O | % | 17.1003 | 15.6285
~1~15~10~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of H2O liquid | % | 0 | 0
~1~15~11~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of Ar | % | 0.79282 | 0.79472
~1~15~12~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~15~14~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~15~23~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: HCl mass flow | kg/hr | 0 | 0
~1~15~24~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: NOx mass flow | kg/hr | 0 | 0
~1~15~25~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: CO mass flow | kg/hr | 0 | 0
~1~15~26~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: UHC mass flow | kg/hr | 0 | 0
~1~15~29~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Hg mass flow | kg/hr | 0 | 0
~1~15~32~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dry Oxygen | % | 3.5511 | 4.197
~1~15~31~~-5001~ | 15 - Gas outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Gas inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~16~0~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.162 | 1.162
~1~16~1~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 223.0611 | 220.7578
~1~16~2~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 228.8499 | 189.7832
~1~16~22~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~16~16~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~16~18~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.1335 | 0.14639
~1~16~20~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68255 | 0.67936
~1~16~3~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 204.3276 | 202.0738
~1~16~19~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~16~4~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.10349 | 0.085747
~1~16~5~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 78.7649 | 65.0507
~1~16~101~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.80708 | 0.81041
~1~16~6~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~16~7~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~16~8~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~16~9~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~16~10~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~16~11~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~16~12~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~16~14~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~16~23~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~16~24~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~16~25~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~16~26~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~16~29~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~16~32~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~16~31~~-5001~ | 16 - Primary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Primary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 178998.5312 | 148521.4688
~1~52~0~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.1744 | 1.1744
~1~52~1~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 48.0609 | 45.7577
~1~52~2~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 228.8499 | 189.7832
~1~52~22~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~52~16~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~52~18~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 29.6329 | 34.9587
~1~52~20~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~52~3~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~52~19~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~52~4~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.10349 | 0.085747
~1~52~5~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 50.4456 | 41.5564
~1~52~101~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2602 | 1.2686
~1~52~6~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~52~7~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~52~8~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~52~9~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~52~10~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~52~11~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~52~12~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~52~14~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~52~23~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~52~24~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~52~25~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~52~26~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~52~29~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~52~32~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~52~31~~-5001~ | 52 - Outlet of Gas/Air Mixer [87] -> Primary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 178998.5312 | 148521.4688
~1~55~0~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 0.99484 | 0.99484
~1~55~1~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 893.9999 | 893.9999
~1~55~2~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 516.8241 | 431.4364
~1~55~22~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash flow | t/h | 4.4783 | 3.9456
~1~55~16~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Fly ash enthalpy | kJ/kg | 971.1801 | 971.1801
~1~55~18~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Relative humidity | % | 0 | 0
~1~55~20~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 1.9033 | 1.8886
~1~55~3~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 1051.3622 | 1042.0958
~1~55~19~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Molecular weight | M.W. | 28.6375 | 28.9224
~1~55~4~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO2 mass flow | t/h | 105.237 | 91.6505
~1~55~5~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Volume flow | m^3/s | 489.0205 | 404.2051
~1~55~101~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 0.29357 | 0.29649
~1~55~6~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of N2 | % | 65.91 | 66.0719
~1~55~7~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of O2 | % | 2.9438 | 3.541
~1~55~8~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~55~9~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O | % | 17.1003 | 15.6285
~1~55~10~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of H2O liquid | % | 0 | 0
~1~55~11~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of Ar | % | 0.79282 | 0.79472
~1~55~12~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~55~14~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Sulfur trioxide SO3 | ppmv | 0.15857 | 0.16709
~1~55~23~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: HCl mass flow | kg/hr | 0 | 0
~1~55~24~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: NOx mass flow | kg/hr | 0 | 0
~1~55~25~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: CO mass flow | kg/hr | 0 | 0
~1~55~26~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: UHC mass flow | kg/hr | 0 | 0
~1~55~29~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Hg mass flow | kg/hr | 0 | 0
~1~55~32~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dry Oxygen | % | 3.5511 | 4.197
~1~55~31~~-5001~ | 55 - Flue gas of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Gas inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~77~0~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0769 | 1.0769
~1~77~1~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 214.6979 | 212.4552
~1~77~2~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 219.8754 | 182.3407
~1~77~22~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash flow | t/h | 0 | 0
~1~77~16~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~77~18~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Relative humidity | % | 0.14532 | 0.15941
~1~77~20~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 0.68683 | 0.6837
~1~77~3~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 195.5857 | 193.392
~1~77~19~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~77~4~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO2 mass flow | t/h | 0.099433 | 0.082384
~1~77~5~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Volume flow | m^3/s | 80.2754 | 66.3012
~1~77~101~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 0.76084 | 0.76394
~1~77~6~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~77~7~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~77~8~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~77~9~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O | % | 2.825 | 2.9652
~1~77~10~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of H2O liquid | % | 0 | 0
~1~77~11~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~77~12~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mole percent of SO2 | % | 0 | 0
~1~77~14~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~77~23~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HCl mass flow | kg/hr | 0 | 0
~1~77~24~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: NOx mass flow | kg/hr | 0 | 0
~1~77~25~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: CO mass flow | kg/hr | 0 | 0
~1~77~26~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: UHC mass flow | kg/hr | 0 | 0
~1~77~29~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Hg mass flow | kg/hr | 0 | 0
~1~77~32~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dry Oxygen | % | 20.9495 | 20.9495
~1~77~31~~-5001~ | 77 - Secondary air outlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14] -> Secondary air inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Normal volume flow | Nm^3/hr | 171978.9844 | 142697.0938
~1~89~0~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Pressure | bar | 1.0894 | 1.0894
~1~89~1~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Temperature | C | 39.6977 | 37.4551
~1~89~2~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mass flow | t/h | 219.8754 | 182.3407
~1~89~22~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash flow | t/h | 0 | 0
~1~89~16~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~89~18~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Relative humidity | % | 42.4078 | 50.229
~1~89~20~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~89~3~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~89~19~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~89~4~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO2 mass flow | t/h | 0.099433 | 0.082384
~1~89~5~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Volume flow | m^3/s | 50.8902 | 41.9227
~1~89~101~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Density | kg/m^3 | 1.2002 | 1.2082
~1~89~6~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~89~7~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~89~8~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~89~9~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O | % | 2.825 | 2.9652
~1~89~10~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of H2O liquid | % | 0 | 0
~1~89~11~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~89~12~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Mole percent of SO2 | % | 0 | 0
~1~89~14~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~89~23~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: HCl mass flow | kg/hr | 0 | 0
~1~89~24~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: NOx mass flow | kg/hr | 0 | 0
~1~89~25~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: CO mass flow | kg/hr | 0 | 0
~1~89~26~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: UHC mass flow | kg/hr | 0 | 0
~1~89~29~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Hg mass flow | kg/hr | 0 | 0
~1~89~32~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Dry Oxygen | % | 20.9495 | 20.9495
~1~89~31~~-5001~ | 89 - Outlet of Gas/Air Mixer [86] -> Secondary air inlet of Boiler Assembly [1]: Parallel Tubular Air Heaters [14]: Normal volume flow | Nm^3/hr | 171978.9844 | 142697.0938
~1~93~0~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Pressure | bar | 0.9668 | 0.96679
~1~93~1~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Temperature | C | 142.4583 | 89.4411
~1~93~2~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mass flow | t/h | 516.8241 | 431.4364
~1~93~22~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash flow | t/h | 0.0097615 | 0.007906
~1~93~16~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Fly ash enthalpy | kJ/kg | 96.7169 | 50.6677
~1~93~18~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Relative humidity | % | 4.2694 | 22.0152
~1~93~20~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Entropy | kJ/kg-C | 0.66416 | 0.51099
~1~93~3~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Enthalpy | kJ/kg | 128.7773 | 69.5524
~1~93~19~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Molecular weight | M.W. | 28.6375 | 28.9224
~1~93~4~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO2 mass flow | t/h | 105.237 | 91.6505
~1~93~5~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Volume flow | m^3/s | 179.1852 | 129.2141
~1~93~101~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Density | kg/m^3 | 0.8012 | 0.92748
~1~93~6~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of N2 | % | 65.91 | 66.0719
~1~93~7~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of O2 | % | 2.9438 | 3.541
~1~93~8~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~93~9~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O | % | 17.1003 | 15.6285
~1~93~10~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of H2O liquid | % | 0 | 0
~1~93~11~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of Ar | % | 0.79282 | 0.79472
~1~93~12~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~93~14~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~93~23~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: HCl mass flow | kg/hr | 0 | 0
~1~93~24~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: NOx mass flow | kg/hr | 0 | 0
~1~93~25~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: CO mass flow | kg/hr | 0 | 0
~1~93~26~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: UHC mass flow | kg/hr | 0 | 0
~1~93~29~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Hg mass flow | kg/hr | 0 | 0
~1~93~32~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Dry Oxygen | % | 3.5511 | 4.197
~1~93~31~~-5001~ | 93 - Outlet of Boiler Assembly [1]: Electrostatic Precipitator [12] - ESP -> Inlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~94~0~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Pressure | bar | 0.96181 | 0.96181
~1~94~1~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Temperature | C | 141.2583 | 88.2411
~1~94~2~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mass flow | t/h | 516.8241 | 431.4364
~1~94~22~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash flow | t/h | 0.0097615 | 0.007906
~1~94~16~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Fly ash enthalpy | kJ/kg | 95.6338 | 49.6694
~1~94~18~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Relative humidity | % | 4.3926 | 22.931
~1~94~20~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Entropy | kJ/kg-C | 0.66245 | 0.50888
~1~94~3~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Enthalpy | kJ/kg | 127.444 | 68.2483
~1~94~19~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Molecular weight | M.W. | 28.6375 | 28.9224
~1~94~4~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO2 mass flow | t/h | 105.237 | 91.6505
~1~94~5~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Volume flow | m^3/s | 179.594 | 129.454
~1~94~101~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Density | kg/m^3 | 0.79937 | 0.92576
~1~94~6~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of N2 | % | 65.91 | 66.0719
~1~94~7~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of O2 | % | 2.9438 | 3.541
~1~94~8~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~94~9~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O | % | 17.1003 | 15.6285
~1~94~10~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of H2O liquid | % | 0 | 0
~1~94~11~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of Ar | % | 0.79282 | 0.79472
~1~94~12~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~94~14~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~94~23~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: HCl mass flow | kg/hr | 0 | 0
~1~94~24~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: NOx mass flow | kg/hr | 0 | 0
~1~94~25~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: CO mass flow | kg/hr | 0 | 0
~1~94~26~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: UHC mass flow | kg/hr | 0 | 0
~1~94~29~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Hg mass flow | kg/hr | 0 | 0
~1~94~32~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Dry Oxygen | % | 3.5511 | 4.197
~1~94~31~~-5001~ | 94 - Outlet of Boiler Assembly [1]: Duct - Classic [48] - Flue Gas Duct Out -> Inlet of Boiler Assembly [1]: Fan [52]: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~95~0~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Pressure | bar | 1.0124 | 1.0124
~1~95~1~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Temperature | C | 148.239 | 94.4053
~1~95~2~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mass flow | t/h | 516.8241 | 431.4364
~1~95~22~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash flow | t/h | 0.0097615 | 0.007906
~1~95~16~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Fly ash enthalpy | kJ/kg | 101.9602 | 54.8184
~1~95~18~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Relative humidity | % | 3.8139 | 19.1343
~1~95~20~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Entropy | kJ/kg-C | 0.66614 | 0.51253
~1~95~3~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Enthalpy | kJ/kg | 135.2057 | 74.9507
~1~95~19~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Molecular weight | M.W. | 28.6375 | 28.9224
~1~95~4~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO2 mass flow | t/h | 105.237 | 91.6505
~1~95~5~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Volume flow | m^3/s | 173.4936 | 125.0828
~1~95~101~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Density | kg/m^3 | 0.82748 | 0.95811
~1~95~6~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of N2 | % | 65.91 | 66.0719
~1~95~7~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of O2 | % | 2.9438 | 3.541
~1~95~8~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of CO2 | % | 13.2498 | 13.9605
~1~95~9~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O | % | 17.1003 | 15.6285
~1~95~10~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of H2O liquid | % | 0 | 0
~1~95~11~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of Ar | % | 0.79282 | 0.79472
~1~95~12~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Mole percent of SO2 | % | 0.0031714 | 0.0033418
~1~95~14~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Sulfur trioxide SO3 | ppmv | 15 | 15
~1~95~23~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: HCl mass flow | kg/hr | 0 | 0
~1~95~24~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: NOx mass flow | kg/hr | 0 | 0
~1~95~25~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: CO mass flow | kg/hr | 0 | 0
~1~95~26~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: UHC mass flow | kg/hr | 0 | 0
~1~95~29~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Hg mass flow | kg/hr | 0 | 0
~1~95~32~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Dry Oxygen | % | 3.5511 | 4.197
~1~95~31~~-5001~ | 95 - Outlet of Boiler Assembly [1]: Fan [52] -> Inlet of Boiler Assembly [1]: Concrete Stack [43] - Concrete Stack: Normal volume flow | Nm^3/hr | 404524.75 | 334363.9375
~1~106~0~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~106~1~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~106~2~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mass flow | t/h | 114.4249 | 94.8916
~1~106~22~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash flow | t/h | 0 | 0
~1~106~16~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~106~18~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~106~20~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~106~3~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~106~19~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~106~4~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~106~5~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Volume flow | m^3/s | 27.8128 | 22.9125
~1~106~101~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~106~6~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~106~7~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~106~8~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~106~9~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~106~10~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~106~11~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~106~12~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~106~14~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~106~23~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~106~24~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~106~25~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~106~26~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~106~29~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~106~32~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~106~31~~-5001~ | 106 - Outlet of Gas/Air Source [80] - PA #2 -> Inlet of Boiler Assembly [1]: Fan [81] - SA Fan #2: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~1~107~0~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Pressure | bar | 1.1794 | 1.1794
~1~107~1~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Temperature | C | 49.0609 | 46.7577
~1~107~2~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mass flow | t/h | 114.4249 | 94.8916
~1~107~22~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~107~16~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~107~18~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Relative humidity | % | 28.3036 | 33.3628
~1~107~20~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Entropy | kJ/kg-C | 0.23262 | 0.22661
~1~107~3~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Enthalpy | kJ/kg | 24.6265 | 22.285
~1~107~19~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~107~4~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~107~5~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Volume flow | m^3/s | 25.1944 | 20.7552
~1~107~101~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Density | kg/m^3 | 1.2616 | 1.27
~1~107~6~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~107~7~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~107~8~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~107~9~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~107~10~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~107~11~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~107~12~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~107~14~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~107~23~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~107~24~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~107~25~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~107~26~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~107~29~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~107~32~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~107~31~~-5001~ | 107 - Outlet of Fan [81] - SA Fan #2 -> Inlet of Duct - Classic [82] - PA Duct In #2: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~1~108~0~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Pressure | bar | 1.0944 | 1.0944
~1~108~1~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Temperature | C | 40.6977 | 38.4551
~1~108~2~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mass flow | t/h | 109.9377 | 91.1703
~1~108~22~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash flow | t/h | 0 | 0
~1~108~16~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~108~18~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Relative humidity | % | 40.3933 | 47.801
~1~108~20~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Entropy | kJ/kg-C | 0.22741 | 0.2214
~1~108~3~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Enthalpy | kJ/kg | 16.0649 | 13.7797
~1~108~19~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~108~4~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~108~5~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Volume flow | m^3/s | 25.4101 | 20.9331
~1~108~101~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Density | kg/m^3 | 1.2018 | 1.2098
~1~108~6~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~108~7~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~108~8~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~108~9~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~108~10~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of H2O liquid | % | 0 | 0
~1~108~11~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~108~12~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Mole percent of SO2 | % | 0 | 0
~1~108~14~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~108~23~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: HCl mass flow | kg/hr | 0 | 0
~1~108~24~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: NOx mass flow | kg/hr | 0 | 0
~1~108~25~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: CO mass flow | kg/hr | 0 | 0
~1~108~26~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: UHC mass flow | kg/hr | 0 | 0
~1~108~29~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Hg mass flow | kg/hr | 0 | 0
~1~108~32~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~108~31~~-5001~ | 108 - Outlet of Fan [85] - PA Fan #2 -> Inlet of Duct - Classic [83] - SA Duct In #2: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~109~0~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Pressure | bar | 1.0124 | 1.0124
~1~109~1~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Temperature | C | 32.1803 | 30.0002
~1~109~2~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mass flow | t/h | 109.9377 | 91.1703
~1~109~22~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash flow | t/h | 0 | 0
~1~109~16~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Fly ash enthalpy | kJ/kg | 0 | 0
~1~109~18~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Relative humidity | % | 59.5589 | 70.7771
~1~109~20~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~109~3~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~109~19~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Molecular weight | M.W. | 28.6575 | 28.6422
~1~109~4~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~109~5~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Volume flow | m^3/s | 26.7221 | 22.014
~1~109~101~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Density | kg/m^3 | 1.1428 | 1.1504
~1~109~6~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of N2 | % | 75.8741 | 75.7646
~1~109~7~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of O2 | % | 20.3577 | 20.3283
~1~109~8~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~109~9~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O | % | 2.825 | 2.9652
~1~109~10~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of H2O liquid | % | 0 | 0
~1~109~11~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of Ar | % | 0.91378 | 0.91246
~1~109~12~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Mole percent of SO2 | % | 0 | 0
~1~109~14~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~109~23~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: HCl mass flow | kg/hr | 0 | 0
~1~109~24~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: NOx mass flow | kg/hr | 0 | 0
~1~109~25~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: CO mass flow | kg/hr | 0 | 0
~1~109~26~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: UHC mass flow | kg/hr | 0 | 0
~1~109~29~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Hg mass flow | kg/hr | 0 | 0
~1~109~32~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Dry Oxygen | % | 20.9495 | 20.9495
~1~109~31~~-5001~ | 109 - Outlet of Gas/Air Source [11] - SA #1 -> Inlet of Boiler Assembly [1]: Fan [72] - PA Fan #1: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~111~0~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Pressure | bar | 1.0124 | 1.0124
~1~111~1~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Temperature | C | 32.1803 | 30.0002
~1~111~2~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mass flow | t/h | 109.9377 | 91.1703
~1~111~22~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash flow | t/h | 0 | 0
~1~111~16~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Fly ash enthalpy | kJ/kg | 0 | 0
~1~111~18~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Relative humidity | % | 59.5589 | 70.7771
~1~111~20~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Entropy | kJ/kg-C | 0.22184 | 0.21582
~1~111~3~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Enthalpy | kJ/kg | 7.3473 | 5.1202
~1~111~19~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Molecular weight | M.W. | 28.6575 | 28.6422
~1~111~4~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~111~5~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Volume flow | m^3/s | 26.7221 | 22.014
~1~111~101~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Density | kg/m^3 | 1.1428 | 1.1504
~1~111~6~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of N2 | % | 75.8741 | 75.7646
~1~111~7~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of O2 | % | 20.3577 | 20.3283
~1~111~8~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~111~9~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O | % | 2.825 | 2.9652
~1~111~10~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of H2O liquid | % | 0 | 0
~1~111~11~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of Ar | % | 0.91378 | 0.91246
~1~111~12~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Mole percent of SO2 | % | 0 | 0
~1~111~14~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~111~23~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: HCl mass flow | kg/hr | 0 | 0
~1~111~24~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: NOx mass flow | kg/hr | 0 | 0
~1~111~25~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: CO mass flow | kg/hr | 0 | 0
~1~111~26~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: UHC mass flow | kg/hr | 0 | 0
~1~111~29~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Hg mass flow | kg/hr | 0 | 0
~1~111~32~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Dry Oxygen | % | 20.9495 | 20.9495
~1~111~31~~-5001~ | 111 - Outlet of Gas/Air Source [84] - SA #2 -> Inlet of Fan [85] - PA Fan #2: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~113~0~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~113~1~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~113~2~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mass flow | t/h | 109.9377 | 91.1703
~1~113~22~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~113~16~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~113~18~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~113~20~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~113~3~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~113~19~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~113~4~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~113~5~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Volume flow | m^3/s | 25.4451 | 20.9614
~1~113~101~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~113~6~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~113~7~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~113~8~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~113~9~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~113~10~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~113~11~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~113~12~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~113~14~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~113~23~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~113~24~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~113~25~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~113~26~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~113~29~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~113~32~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~113~31~~-5001~ | 113 - Outlet of Boiler Assembly [1]: Duct - Classic [2] - SA Duct In #1 -> Inlet 3 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~114~0~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Pressure | bar | 1.0894 | 1.0894
~1~114~1~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Temperature | C | 39.6977 | 37.4551
~1~114~2~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mass flow | t/h | 109.9377 | 91.1703
~1~114~22~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash flow | t/h | 0 | 0
~1~114~16~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~114~18~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Relative humidity | % | 42.4078 | 50.229
~1~114~20~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Entropy | kJ/kg-C | 0.22547 | 0.21943
~1~114~3~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Enthalpy | kJ/kg | 15.0413 | 12.7554
~1~114~19~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~114~4~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO2 mass flow | t/h | 0.049716 | 0.041192
~1~114~5~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Volume flow | m^3/s | 25.4451 | 20.9614
~1~114~101~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Density | kg/m^3 | 1.2002 | 1.2082
~1~114~6~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~114~7~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~114~8~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~114~9~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O | % | 2.825 | 2.9652
~1~114~10~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of H2O liquid | % | 0 | 0
~1~114~11~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~114~12~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Mole percent of SO2 | % | 0 | 0
~1~114~14~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~114~23~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: HCl mass flow | kg/hr | 0 | 0
~1~114~24~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: NOx mass flow | kg/hr | 0 | 0
~1~114~25~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: CO mass flow | kg/hr | 0 | 0
~1~114~26~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: UHC mass flow | kg/hr | 0 | 0
~1~114~29~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Hg mass flow | kg/hr | 0 | 0
~1~114~32~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Dry Oxygen | % | 20.9495 | 20.9495
~1~114~31~~-5001~ | 114 - Outlet of Duct - Classic [83] - SA Duct In #2 -> Inlet 1 of Gas/Air Mixer [86]: Normal volume flow | Nm^3/hr | 85989.4922 | 71348.5469
~1~115~0~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~115~1~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~115~2~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mass flow | t/h | 114.4249 | 94.8916
~1~115~22~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~115~16~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~115~18~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~115~20~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~115~3~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~115~19~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~115~4~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~115~5~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Volume flow | m^3/s | 25.2228 | 20.7782
~1~115~101~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~115~6~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~115~7~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~115~8~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~115~9~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~115~10~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~115~11~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~115~12~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~115~14~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~115~23~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~115~24~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~115~25~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~115~26~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~115~29~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~115~32~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~115~31~~-5001~ | 115 - Outlet of Boiler Assembly [1]: Duct - Classic [65] - PA Duct In #1 -> Inlet 1 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~1~116~0~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Pressure | bar | 1.1744 | 1.1744
~1~116~1~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Temperature | C | 48.0609 | 45.7577
~1~116~2~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mass flow | t/h | 114.4249 | 94.8916
~1~116~22~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash flow | t/h | 0 | 0
~1~116~16~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Fly ash enthalpy | kJ/kg | 0 | 0
~1~116~18~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Relative humidity | % | 29.6329 | 34.9587
~1~116~20~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Entropy | kJ/kg-C | 0.23067 | 0.22463
~1~116~3~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Enthalpy | kJ/kg | 23.6026 | 21.2604
~1~116~19~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Molecular weight | M.W. | 28.6575 | 28.6422
~1~116~4~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO2 mass flow | t/h | 0.051746 | 0.042873
~1~116~5~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Volume flow | m^3/s | 25.2228 | 20.7782
~1~116~101~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Density | kg/m^3 | 1.2602 | 1.2686
~1~116~6~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of N2 | % | 75.8741 | 75.7646
~1~116~7~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of O2 | % | 20.3577 | 20.3283
~1~116~8~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of CO2 | % | 0.029447 | 0.029404
~1~116~9~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O | % | 2.825 | 2.9652
~1~116~10~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of H2O liquid | % | 0 | 0
~1~116~11~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of Ar | % | 0.91378 | 0.91246
~1~116~12~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Mole percent of SO2 | % | 0 | 0
~1~116~14~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Sulfur trioxide SO3 | ppmv | 0 | 0
~1~116~23~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: HCl mass flow | kg/hr | 0 | 0
~1~116~24~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: NOx mass flow | kg/hr | 0 | 0
~1~116~25~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: CO mass flow | kg/hr | 0 | 0
~1~116~26~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: UHC mass flow | kg/hr | 0 | 0
~1~116~29~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Hg mass flow | kg/hr | 0 | 0
~1~116~32~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Dry Oxygen | % | 20.9495 | 20.9495
~1~116~31~~-5001~ | 116 - Outlet of Duct - Classic [82] - PA Duct In #2 -> Inlet 3 of Gas/Air Mixer [87]: Normal volume flow | Nm^3/hr | 89499.2656 | 74260.7344
~2~1~0~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Pressure | bar | 6.297 | 6.1192
~2~1~1~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Temperature | C | 252.8501 | 253.113
~2~1~2~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 1.5596 | 1.4286
~2~1~20~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 7.171 | 7.1862
~2~1~4~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 2962.6248 | 2963.7893
~2~1~3~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | 415.1362 | 416.301
~2~1~5~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Steam quality |  | 1.0983 | 1.0993
~2~1~10~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 2.6517 | 2.5737
~2~1~11~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 2.1192 | 2.1141
~2~1~12~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.039327 | 0.039324
~2~1~13~~-5001~ | 1 - Outlet of Mixer [60] -> Heating stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 1.8259e-05 | 1.8273e-05
~2~3~0~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Pressure | bar | 6.36 | 6.1804
~2~3~1~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Temperature | C | 226.2648 | 226.4971
~2~3~2~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Mass flow | t/h | 1.4037 | 1.2857
~2~3~20~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Entropy | kJ/kg-C | 7.0559 | 7.0713
~2~3~4~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy | kJ/kg | 2905.8972 | 2907.1526
~2~3~3~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Enthalpy H* | kJ/kg | 358.4086 | 359.6642
~2~3~5~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Steam quality |  | 1.0708 | 1.0719
~2~3~10~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Density | kg/m^3 | 2.8369 | 2.7531
~2~3~11~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Specific heat | kJ/kg-C | 2.1638 | 2.1565
~2~3~12~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Thermal conductivity | W/m-C | 0.03687 | 0.036852
~2~3~13~~-5001~ | 3 - Outlet 2 of Splitter [30] -> Inlet of Pipe (PCE) [1]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7154e-05
~2~5~0~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Pressure | bar | 96.1447 | 93.0932
~2~5~1~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Temperature | C | 436.0033 | 436.0036
~2~5~2~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Mass flow | t/h | 408.2104 | 372.1087
~2~5~20~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Entropy | kJ/kg-C | 6.3927 | 6.4132
~2~5~4~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy | kJ/kg | 3209.927 | 3215.0935
~2~5~3~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Enthalpy H* | kJ/kg | 662.4385 | 667.6049
~2~5~5~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Steam quality |  | 1.356 | 1.351
~2~5~10~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Density | kg/m^3 | 33.0945 | 31.9029
~2~5~11~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Specific heat | kJ/kg-C | 2.7502 | 2.7202
~2~5~12~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Thermal conductivity | W/m-C | 0.068933 | 0.068504
~2~5~13~~-5001~ | 5 - Steam outlet of Boiler Assembly [1]: Desuperheater [68] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH: Dynamic viscosity | kg/m-s | 2.6095e-05 | 2.6081e-05
~2~6~0~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Pressure | bar | 1.0135 | 1.0135
~2~6~1~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Temperature | C | 29.2416 | 27.3223
~2~6~2~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Mass flow | t/h | 7559.2622 | 6903.356
~2~6~20~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~6~4~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~6~3~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~6~5~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Steam quality |  | -0.13137 | -0.13493
~2~6~10~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Density | kg/m^3 | 995.916 | 996.4656
~2~6~11~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~6~12~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~6~13~~-5001~ | 6 - Outlet 3 of Splitter [76] -> Suction of General Pump [27] - CWP-1: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~10~0~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 108.5314 | 105.0868
~2~10~1~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 303.015 | 301.2661
~2~10~2~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 388.6693 | 354.5441
~2~10~20~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 3.2745 | 3.2587
~2~10~4~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 1359.2158 | 1349.636
~2~10~3~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | -1188.2727 | -1197.8524
~2~10~5~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | -0.067129 | -0.062193
~2~10~10~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 710.3107 | 713.5569
~2~10~11~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 5.7521 | 5.7091
~2~10~12~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.54437 | 0.54713
~2~10~13~~-5001~ | 10 - Water outlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO -> Feedwater of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 8.5499e-05 | 8.6084e-05
~2~11~0~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~11~1~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~11~2~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Mass flow | t/h | 7559.2622 | 6903.356
~2~11~20~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~11~4~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~11~3~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~11~5~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~11~10~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~11~11~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~11~12~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~11~13~~-5001~ | 11 - Discharge of General Pump [27] - CWP-1 -> Inlet 1 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~12~0~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Pressure | bar | 3.0947 | 3.0947
~2~12~1~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Temperature | C | 29.2957 | 27.3762
~2~12~2~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Mass flow | t/h | 7559.2622 | 6903.356
~2~12~20~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~12~4~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy | kJ/kg | 122.9913 | 114.9646
~2~12~3~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5239
~2~12~5~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Steam quality |  | -0.20507 | -0.20878
~2~12~10~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Density | kg/m^3 | 995.9927 | 996.5438
~2~12~11~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~12~12~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~12~13~~-5001~ | 12 - Discharge of General Pump [6] - CWP-2 -> Inlet 3 of Mixer [5]: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~17~0~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Pressure | bar | 118.2992 | 114.5446
~2~17~1~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Temperature | C | 226.1392 | 226.1398
~2~17~2~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Mass flow | t/h | 388.6693 | 354.5441
~2~17~20~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Entropy | kJ/kg-C | 2.5571 | 2.5578
~2~17~4~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy | kJ/kg | 974.4664 | 974.3673
~2~17~3~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Enthalpy H* | kJ/kg | -1573.0221 | -1573.1212
~2~17~5~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Steam quality |  | -0.42326 | -0.40283
~2~17~10~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Density | kg/m^3 | 840.5917 | 840.2652
~2~17~11~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Specific heat | kJ/kg-C | 4.5809 | 4.5837
~2~17~12~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Thermal conductivity | W/m-C | 0.65273 | 0.65235
~2~17~13~~-5001~ | 17 - Outlet of Pipe (PCE) [77] -> Inlet of Boiler Assembly [1]: Valve [13]: Dynamic viscosity | kg/m-s | 0.0001199 | 0.0001198
~2~18~0~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Pressure | bar | 3.4473 | 3.4473
~2~18~1~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Temperature | C | 138.3289 | 138.3289
~2~18~2~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Mass flow | t/h | 409.1796 | 372.9929
~2~18~20~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~18~4~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~18~3~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~18~5~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Steam quality |  | 0.031068 | 0.031068
~2~18~10~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Density | kg/m^3 | 56.9378 | 56.9378
~2~18~11~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~18~12~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~18~13~~-5001~ | 18 - Feedwater outlet of Deaerator [25] - DAER -> Inlet of Splitter [61]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~19~0~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Pressure | bar | 88.0061 | 85.2066
~2~19~1~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Temperature | C | 537.116 | 536.0752
~2~19~2~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Mass flow | t/h | 408.2104 | 372.1087
~2~19~20~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Entropy | kJ/kg-C | 6.7896 | 6.8041
~2~19~4~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~19~3~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~19~5~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Steam quality |  | 1.5289 | 1.5194
~2~19~10~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Density | kg/m^3 | 24.9721 | 24.1678
~2~19~11~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Specific heat | kJ/kg-C | 2.4395 | 2.4296
~2~19~12~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Thermal conductivity | W/m-C | 0.078328 | 0.077955
~2~19~13~~-5001~ | 19 - Outlet of Boiler Assembly [1]: Valve [31] -> Inlet of Pipe (PCE) [4]: Dynamic viscosity | kg/m-s | 3.0414e-05 | 3.0354e-05
~2~20~0~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 120.3095 | 116.5174
~2~20~1~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 158.077 | 157.9403
~2~20~2~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 388.6693 | 354.5441
~2~20~20~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~20~4~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 673.9968 | 673.1791
~2~20~3~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1873.4917 | -1874.3093
~2~20~5~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.68654 | -0.66124
~2~20~10~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 915.9666 | 915.8819
~2~20~11~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~20~12~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~20~13~~-5001~ | 20 - Outlet 3 of Splitter [15] -> Feedwater inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~21~0~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Pressure | bar | 2.18 | 2.1184
~2~21~1~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Temperature | C | 128.3819 | 128.5931
~2~21~2~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Mass flow | t/h | 1.3769 | 1.2204
~2~21~20~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Entropy | kJ/kg-C | 7.1277 | 7.1433
~2~21~4~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy | kJ/kg | 2721.9922 | 2723.0752
~2~21~3~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Enthalpy H* | kJ/kg | 174.5037 | 175.5865
~2~21~5~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Steam quality |  | 1.0054 | 1.0065
~2~21~10~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Density | kg/m^3 | 1.2053 | 1.1697
~2~21~11~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Specific heat | kJ/kg-C | 2.1223 | 2.1151
~2~21~12~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Thermal conductivity | W/m-C | 0.027674 | 0.027644
~2~21~13~~-5001~ | 21 - Outlet 2 of Splitter [34] -> Inlet 1 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.33e-05
~2~22~0~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Pressure | bar | 27.68 | 26.8987
~2~22~1~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Temperature | C | 390.2057 | 390.1317
~2~22~2~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Mass flow | t/h | 407.239 | 371.2879
~2~22~20~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Entropy | kJ/kg-C | 6.9316 | 6.9461
~2~22~4~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy | kJ/kg | 3213.314 | 3214.521
~2~22~3~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Enthalpy H* | kJ/kg | 665.8253 | 667.0323
~2~22~5~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Steam quality |  | 1.226 | 1.2259
~2~22~10~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Density | kg/m^3 | 9.4125 | 9.137
~2~22~11~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Specific heat | kJ/kg-C | 2.2522 | 2.2456
~2~22~12~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Thermal conductivity | W/m-C | 0.056038 | 0.055949
~2~22~13~~-5001~ | 22 - Outlet of ST Assembly [1]: ST Group [16] -> Inlet of Splitter [28]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3978e-05
~2~23~0~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Pressure | bar | 27.68 | 26.8987
~2~23~1~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Temperature | C | 390.2057 | 390.1317
~2~23~2~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Mass flow | t/h | 389.0559 | 354.7009
~2~23~20~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Entropy | kJ/kg-C | 6.9316 | 6.9461
~2~23~4~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy | kJ/kg | 3213.314 | 3214.521
~2~23~3~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Enthalpy H* | kJ/kg | 665.8253 | 667.0323
~2~23~5~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Steam quality |  | 1.226 | 1.2259
~2~23~10~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Density | kg/m^3 | 9.4125 | 9.137
~2~23~11~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Specific heat | kJ/kg-C | 2.2522 | 2.2456
~2~23~12~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Thermal conductivity | W/m-C | 0.056038 | 0.055949
~2~23~13~~-5001~ | 23 - Outlet 1 of Splitter [28] -> Inlet of ST Assembly [1]: ST Group [17]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3978e-05
~2~24~0~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Pressure | bar | 27.68 | 26.8987
~2~24~1~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Temperature | C | 390.2057 | 390.1317
~2~24~2~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Mass flow | t/h | 18.1831 | 16.587
~2~24~20~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Entropy | kJ/kg-C | 6.9316 | 6.9461
~2~24~4~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy | kJ/kg | 3213.314 | 3214.521
~2~24~3~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Enthalpy H* | kJ/kg | 665.8253 | 667.0323
~2~24~5~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Steam quality |  | 1.226 | 1.2259
~2~24~10~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Density | kg/m^3 | 9.4125 | 9.137
~2~24~11~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Specific heat | kJ/kg-C | 2.2522 | 2.2456
~2~24~12~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Thermal conductivity | W/m-C | 0.056038 | 0.055949
~2~24~13~~-5001~ | 24 - Outlet 2 of Splitter [28] -> Inlet of Pipe (PCE) [53]: Dynamic viscosity | kg/m-s | 2.3979e-05 | 2.3978e-05
~2~25~0~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Pressure | bar | 18.75 | 17.9587
~2~25~1~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Temperature | C | 344.0994 | 342.4655
~2~25~2~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Mass flow | t/h | 389.0559 | 354.7009
~2~25~20~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Entropy | kJ/kg-C | 6.9701 | 6.9862
~2~25~4~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy | kJ/kg | 3127.1702 | 3125.2595
~2~25~3~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Enthalpy H* | kJ/kg | 579.6817 | 577.7709
~2~25~5~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Steam quality |  | 1.1735 | 1.1723
~2~25~10~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Density | kg/m^3 | 6.822 | 6.5435
~2~25~11~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Specific heat | kJ/kg-C | 2.2172 | 2.2096
~2~25~12~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Thermal conductivity | W/m-C | 0.050151 | 0.049888
~2~25~13~~-5001~ | 25 - Outlet of ST Assembly [1]: ST Group [17] -> Inlet of Splitter [29]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.1962e-05
~2~26~0~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Pressure | bar | 18.75 | 17.9587
~2~26~1~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Temperature | C | 344.0994 | 342.4655
~2~26~2~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Mass flow | t/h | 30.6719 | 28.0864
~2~26~20~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Entropy | kJ/kg-C | 6.9701 | 6.9862
~2~26~4~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy | kJ/kg | 3127.1702 | 3125.2595
~2~26~3~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Enthalpy H* | kJ/kg | 579.6817 | 577.7709
~2~26~5~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Steam quality |  | 1.1735 | 1.1723
~2~26~10~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Density | kg/m^3 | 6.822 | 6.5435
~2~26~11~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Specific heat | kJ/kg-C | 2.2172 | 2.2096
~2~26~12~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Thermal conductivity | W/m-C | 0.050151 | 0.049888
~2~26~13~~-5001~ | 26 - Outlet 2 of Splitter [29] -> Inlet of Pipe (PCE) [54]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.1962e-05
~2~27~0~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Pressure | bar | 18.75 | 17.9587
~2~27~1~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Temperature | C | 344.0994 | 342.4655
~2~27~2~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Mass flow | t/h | 358.384 | 326.6145
~2~27~20~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Entropy | kJ/kg-C | 6.9701 | 6.9862
~2~27~4~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy | kJ/kg | 3127.1702 | 3125.2595
~2~27~3~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Enthalpy H* | kJ/kg | 579.6817 | 577.7709
~2~27~5~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Steam quality |  | 1.1735 | 1.1723
~2~27~10~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Density | kg/m^3 | 6.822 | 6.5435
~2~27~11~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Specific heat | kJ/kg-C | 2.2172 | 2.2096
~2~27~12~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Thermal conductivity | W/m-C | 0.050151 | 0.049888
~2~27~13~~-5001~ | 27 - Outlet 1 of Splitter [29] -> Inlet of ST Assembly [1]: ST Group [18]: Dynamic viscosity | kg/m-s | 2.2027e-05 | 2.1962e-05
~2~28~0~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Pressure | bar | 1.0135 | 1.0135
~2~28~1~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Temperature | C | 29.2416 | 27.3223
~2~28~2~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Mass flow | t/h | 7559.2622 | 6903.356
~2~28~20~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~28~4~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~28~3~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~28~5~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Steam quality |  | -0.13137 | -0.13493
~2~28~10~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Density | kg/m^3 | 995.916 | 996.4656
~2~28~11~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~28~12~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~28~13~~-5001~ | 28 - Outlet 1 of Splitter [76] -> Suction of General Pump [6] - CWP-2: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~29~0~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Pressure | bar | 6.297 | 6.1192
~2~29~1~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Temperature | C | 225.6743 | 225.9089
~2~29~2~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Mass flow | t/h | 1.4037 | 1.2857
~2~29~20~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Entropy | kJ/kg-C | 7.0583 | 7.0737
~2~29~4~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy | kJ/kg | 2904.8972 | 2906.1528
~2~29~3~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Enthalpy H* | kJ/kg | 357.4087 | 358.6642
~2~29~5~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Steam quality |  | 1.0705 | 1.0716
~2~29~10~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Density | kg/m^3 | 2.8117 | 2.7286
~2~29~11~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Specific heat | kJ/kg-C | 2.1626 | 2.1554
~2~29~12~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Thermal conductivity | W/m-C | 0.036804 | 0.036787
~2~29~13~~-5001~ | 29 - Outlet of Pipe (PCE) [1] -> Inlet 3 of Mixer [60]: Dynamic viscosity | kg/m-s | 1.7117e-05 | 1.7131e-05
~2~30~0~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Pressure | bar | 6.36 | 6.1804
~2~30~1~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Temperature | C | 226.2648 | 226.4971
~2~30~2~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Mass flow | t/h | 356.9803 | 325.3288
~2~30~20~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Entropy | kJ/kg-C | 7.0559 | 7.0713
~2~30~4~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy | kJ/kg | 2905.8972 | 2907.1526
~2~30~3~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Enthalpy H* | kJ/kg | 358.4086 | 359.6642
~2~30~5~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Steam quality |  | 1.0708 | 1.0719
~2~30~10~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Density | kg/m^3 | 2.8369 | 2.7531
~2~30~11~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Specific heat | kJ/kg-C | 2.1638 | 2.1565
~2~30~12~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Thermal conductivity | W/m-C | 0.03687 | 0.036852
~2~30~13~~-5001~ | 30 - Outlet 1 of Splitter [30] -> Inlet of ST Assembly [1]: ST Group [19]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7154e-05
~2~31~0~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Pressure | bar | 3.4473 | 3.4473
~2~31~1~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Temperature | C | 138.3289 | 138.3289
~2~31~2~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Mass flow | t/h | 204.5898 | 186.4964
~2~31~20~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~31~4~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~31~3~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~31~5~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Steam quality |  | 0.031068 | 0.031068
~2~31~10~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Density | kg/m^3 | 56.9378 | 56.9378
~2~31~11~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~31~12~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~31~13~~-5001~ | 31 - Outlet of Valve [75] -> Suction of General Pump [59] - BFP-A: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~32~0~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Pressure | bar | 6.297 | 6.1192
~2~32~1~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Temperature | C | 499.6052 | 499.6784
~2~32~2~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Mass flow | t/h | 0.15596 | 0.14286
~2~32~20~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Entropy | kJ/kg-C | 7.9802 | 7.9938
~2~32~4~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~32~3~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~32~5~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Steam quality |  | 1.3481 | 1.3483
~2~32~10~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Density | kg/m^3 | 1.7742 | 1.7237
~2~32~11~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Specific heat | kJ/kg-C | 2.1496 | 2.1491
~2~32~12~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Thermal conductivity | W/m-C | 0.067265 | 0.067262
~2~32~13~~-5001~ | 32 - Outlet 1 of Splitter [26] - k -> Inlet 1 of Mixer [60]: Dynamic viscosity | kg/m-s | 2.8572e-05 | 2.8575e-05
~2~33~0~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 1.3137 | 1.2767
~2~33~1~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 78.9798 | 78.295
~2~33~2~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 48.0353 | 44.0466
~2~33~20~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 1.0632 | 1.055
~2~33~4~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 330.7401 | 327.8648
~2~33~3~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2216.7485 | -2219.6238
~2~33~5~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.053513 | -0.053163
~2~33~10~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 972.4866 | 972.9072
~2~33~11~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1953 | 4.1948
~2~33~12~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.66687 | 0.6664
~2~33~13~~-5001~ | 33 - Drain outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Water/steam addition to shell of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00035937 | 0.00036248
~2~34~0~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 6.5519 | 6.5519
~2~34~1~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 73.3808 | 72.696
~2~34~2~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 358.765 | 326.891
~2~34~20~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 0.99568 | 0.98739
~2~34~4~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 307.6902 | 304.8211
~2~34~3~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2239.7983 | -2242.6675
~2~34~5~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.18218 | -0.18356
~2~34~10~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 976.0994 | 976.5015
~2~34~11~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.1903 | 4.1899
~2~34~12~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.6631 | 0.66258
~2~34~13~~-5001~ | 34 - Feedwater outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Feedwater inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00038637 | 0.00038989
~2~35~0~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Pressure | bar | 3.4473 | 3.4473
~2~35~1~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Temperature | C | 138.3289 | 138.3289
~2~35~2~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~35~20~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~35~4~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~35~3~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~35~5~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Steam quality |  | 0.031068 | 0.031068
~2~35~10~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Density | kg/m^3 | 56.9378 | 56.9378
~2~35~11~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~35~12~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~35~13~~-5001~ | 35 - Outlet of Valve [74] -> Suction of General Pump [35] - BFP-C: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~36~0~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Pressure | bar | 16.894 | 16.894
~2~36~1~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Temperature | C | 164.6357 | 164.499
~2~36~2~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Mass flow | t/h | 48.855 | 44.6733
~2~36~20~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.9877 | 1.9864
~2~36~4~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 696.2256 | 695.6312
~2~36~3~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1851.2629 | -1851.8573
~2~36~5~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Steam quality |  | -0.09059 | -0.090899
~2~36~10~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Density | kg/m^3 | 903.515 | 903.6523
~2~36~11~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3491 | 4.3486
~2~36~12~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68174 | 0.68178
~2~36~13~~-5001~ | 36 - Drain outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Secondary stream inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00016472 | 0.00016487
~2~37~0~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Pressure | bar | 5.5 | 5.3442
~2~37~1~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Temperature | C | 211.9436 | 212.1814
~2~37~2~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Mass flow | t/h | 356.9803 | 325.3288
~2~37~20~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Entropy | kJ/kg-C | 7.0665 | 7.082
~2~37~4~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy | kJ/kg | 2879.03 | 2880.2673
~2~37~3~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Enthalpy H* | kJ/kg | 331.5415 | 332.7789
~2~37~5~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Steam quality |  | 1.0604 | 1.0615
~2~37~10~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Density | kg/m^3 | 2.5238 | 2.449
~2~37~11~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Specific heat | kJ/kg-C | 2.1585 | 2.1512
~2~37~12~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Thermal conductivity | W/m-C | 0.035418 | 0.035401
~2~37~13~~-5001~ | 37 - Outlet of ST Assembly [1]: ST Group [19] -> Inlet of Splitter [33]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6574e-05
~2~38~0~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Pressure | bar | 5.5 | 5.3442
~2~38~1~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Temperature | C | 211.9436 | 212.1814
~2~38~2~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Mass flow | t/h | 19.3783 | 18.1571
~2~38~20~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Entropy | kJ/kg-C | 7.0665 | 7.082
~2~38~4~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy | kJ/kg | 2879.03 | 2880.2673
~2~38~3~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Enthalpy H* | kJ/kg | 331.5415 | 332.7789
~2~38~5~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Steam quality |  | 1.0604 | 1.0615
~2~38~10~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Density | kg/m^3 | 2.5238 | 2.449
~2~38~11~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Specific heat | kJ/kg-C | 2.1585 | 2.1512
~2~38~12~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Thermal conductivity | W/m-C | 0.035418 | 0.035401
~2~38~13~~-5001~ | 38 - Outlet 2 of Splitter [33] -> Inlet of Pipe (PCE) [55]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6574e-05
~2~39~0~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Pressure | bar | 5.5 | 5.3442
~2~39~1~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Temperature | C | 211.9436 | 212.1814
~2~39~2~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Mass flow | t/h | 337.602 | 307.1717
~2~39~20~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Entropy | kJ/kg-C | 7.0665 | 7.082
~2~39~4~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy | kJ/kg | 2879.03 | 2880.2673
~2~39~3~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Enthalpy H* | kJ/kg | 331.5415 | 332.7789
~2~39~5~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Steam quality |  | 1.0604 | 1.0615
~2~39~10~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Density | kg/m^3 | 2.5238 | 2.449
~2~39~11~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Specific heat | kJ/kg-C | 2.1585 | 2.1512
~2~39~12~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Thermal conductivity | W/m-C | 0.035418 | 0.035401
~2~39~13~~-5001~ | 39 - Outlet 1 of Splitter [33] -> Inlet of ST Assembly [1]: ST Group [20]: Dynamic viscosity | kg/m-s | 1.6561e-05 | 1.6574e-05
~2~40~0~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Pressure | bar | 2.18 | 2.1184
~2~40~1~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Temperature | C | 128.3819 | 128.5931
~2~40~2~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Mass flow | t/h | 337.602 | 307.1717
~2~40~20~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Entropy | kJ/kg-C | 7.1277 | 7.1433
~2~40~4~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy | kJ/kg | 2721.9922 | 2723.0752
~2~40~3~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Enthalpy H* | kJ/kg | 174.5037 | 175.5865
~2~40~5~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Steam quality |  | 1.0054 | 1.0065
~2~40~10~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Density | kg/m^3 | 1.2053 | 1.1697
~2~40~11~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Specific heat | kJ/kg-C | 2.1223 | 2.1151
~2~40~12~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Thermal conductivity | W/m-C | 0.027674 | 0.027644
~2~40~13~~-5001~ | 40 - Outlet of ST Assembly [1]: ST Group [20] -> Inlet of Splitter [34]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.33e-05
~2~41~0~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Pressure | bar | 2.18 | 2.1184
~2~41~1~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Temperature | C | 128.3819 | 128.5931
~2~41~2~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Mass flow | t/h | 9.4889 | 8.5666
~2~41~20~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Entropy | kJ/kg-C | 7.1277 | 7.1433
~2~41~4~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy | kJ/kg | 2721.9922 | 2723.0752
~2~41~3~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Enthalpy H* | kJ/kg | 174.5037 | 175.5865
~2~41~5~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Steam quality |  | 1.0054 | 1.0065
~2~41~10~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Density | kg/m^3 | 1.2053 | 1.1697
~2~41~11~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Specific heat | kJ/kg-C | 2.1223 | 2.1151
~2~41~12~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Thermal conductivity | W/m-C | 0.027674 | 0.027644
~2~41~13~~-5001~ | 41 - Outlet 3 of Splitter [34] -> Inlet of Pipe (PCE) [56]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.33e-05
~2~42~0~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 2.1373 | 2.0769
~2~42~1~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 111.026 | 110.1885
~2~42~2~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 28.8672 | 26.7237
~2~42~20~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 1.4299 | 1.4207
~2~42~4~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 465.7306 | 462.1843
~2~42~3~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | -2081.7578 | -2085.3042
~2~42~5~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | -0.021831 | -0.021649
~2~42~10~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 950.2326 | 950.8726
~2~42~11~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2299 | 4.2286
~2~42~12~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.68216 | 0.68192
~2~42~13~~-5001~ | 42 - Drain outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Water/steam addition to shell of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 0.00025247 | 0.00025453
~2~43~0~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 6.1382 | 6.1382
~2~43~1~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 105.4201 | 104.583
~2~43~2~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 358.765 | 326.891
~2~43~20~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.3675 | 1.3581
~2~43~4~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 442.3387 | 438.8056
~2~43~3~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2105.1499 | -2108.6829
~2~43~5~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.11141 | -0.11311
~2~43~10~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 954.6662 | 955.2871
~2~43~11~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2211 | 4.22
~2~43~12~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68065 | 0.68035
~2~43~13~~-5001~ | 43 - Feedwater outlet of Feedwater Heater (PCE) [22] - LPH-6 -> Feedwater inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00026696 | 0.00026924
~2~44~0~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Pressure | bar | 5.3108 | 5.3108
~2~44~1~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Temperature | C | 150.0223 | 150.0223
~2~44~2~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Mass flow | t/h | 358.765 | 326.891
~2~44~20~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Entropy | kJ/kg-C | 1.8421 | 1.8421
~2~44~4~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy | kJ/kg | 632.2855 | 632.2855
~2~44~3~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Enthalpy H* | kJ/kg | -1915.203 | -1915.203
~2~44~5~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Steam quality |  | -0.0084685 | -0.0084685
~2~44~10~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Density | kg/m^3 | 917.0516 | 917.0516
~2~44~11~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Specific heat | kJ/kg-C | 4.3096 | 4.3096
~2~44~12~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Thermal conductivity | W/m-C | 0.68443 | 0.68443
~2~44~13~~-5001~ | 44 - Feedwater outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Feedwater inlet of Deaerator [25] - DAER: Dynamic viscosity | kg/m-s | 0.00018197 | 0.00018197
~2~45~0~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Pressure | bar | 3.4473 | 3.4473
~2~45~1~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Temperature | C | 138.3289 | 138.3289
~2~45~2~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Mass flow | t/h | 204.5898 | 186.4964
~2~45~20~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~45~4~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~45~3~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~45~5~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Steam quality |  | 0.031068 | 0.031068
~2~45~10~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Density | kg/m^3 | 56.9378 | 56.9378
~2~45~11~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~45~12~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~45~13~~-5001~ | 45 - Outlet of Valve [73] -> Suction of General Pump [50] - BFP-B: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~46~0~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Pressure | bar | 0.45741 | 0.45741
~2~46~1~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Temperature | C | 45.423 | 45.4273
~2~46~2~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Mass flow | t/h | 358.765 | 326.891
~2~46~20~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Entropy | kJ/kg-C | 0.64416 | 0.64422
~2~46~4~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy | kJ/kg | 190.1835 | 190.2019
~2~46~3~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Enthalpy H* | kJ/kg | -2357.3052 | -2357.2866
~2~46~5~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Steam quality |  | -0.061053 | -0.061045
~2~46~10~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Density | kg/m^3 | 990.0591 | 990.0573
~2~46~11~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~46~12~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Thermal conductivity | W/m-C | 0.63578 | 0.63579
~2~46~13~~-5001~ | 46 - Outlet of Makeup / Blowdown [44] -> Suction of General Pump [45] - CP: Dynamic viscosity | kg/m-s | 0.00059101 | 0.00059096
~2~47~0~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 7.3792 | 7.3792
~2~47~1~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 45.5004 | 45.5048
~2~47~2~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 358.765 | 326.891
~2~47~20~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 0.64488 | 0.64494
~2~47~4~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 191.1157 | 191.134
~2~47~3~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | -2356.3728 | -2356.3545
~2~47~5~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | -0.25036 | -0.25036
~2~47~10~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 990.3279 | 990.326
~2~47~11~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 4.178 | 4.178
~2~47~12~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.63623 | 0.63624
~2~47~13~~-5001~ | 47 - Discharge of General Pump [45] - CP -> Feedwater inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 0.00059029 | 0.00059024
~2~48~0~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.3922 | 5.2395
~2~48~1~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 211.2392 | 211.4829
~2~48~2~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 19.3783 | 18.1571
~2~48~20~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 7.0734 | 7.0888
~2~48~4~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 2878.03 | 2879.2676
~2~48~3~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | 330.5416 | 331.7789
~2~48~5~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | 1.0603 | 1.0614
~2~48~10~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 2.4769 | 2.4035
~2~48~11~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 2.1553 | 2.148
~2~48~12~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.035331 | 0.035315
~2~48~13~~-5001~ | 48 - Outlet of Pipe (PCE) [55] -> Heating steam inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 1.6534e-05 | 1.6548e-05
~2~49~0~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 5.3922 | 5.2395
~2~49~1~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 125.9456 | 125.0304
~2~49~2~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 19.3783 | 18.1571
~2~49~20~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 1.5913 | 1.5816
~2~49~4~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 529.2431 | 525.3402
~2~49~3~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | -2018.2455 | -2022.1483
~2~49~5~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | -0.058768 | -0.058271
~2~49~10~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 938.4268 | 939.181
~2~49~11~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 4.2543 | 4.2526
~2~49~12~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.68518 | 0.68507
~2~49~13~~-5001~ | 49 - Drain outlet of Feedwater Heater (PCE) [24] - LPH-4 -> Water/steam addition to shell of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 0.00022034 | 0.00022209
~2~50~0~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Pressure | bar | 5.7245 | 5.7245
~2~50~1~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Temperature | C | 120.3328 | 119.4181
~2~50~2~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Mass flow | t/h | 358.765 | 326.891
~2~50~20~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Entropy | kJ/kg-C | 1.5311 | 1.5212
~2~50~4~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy | kJ/kg | 505.418 | 501.537
~2~50~3~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Enthalpy H* | kJ/kg | -2042.0706 | -2045.9515
~2~50~5~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Steam quality |  | -0.075135 | -0.076991
~2~50~10~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Density | kg/m^3 | 943.059 | 943.798
~2~50~11~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Specific heat | kJ/kg-C | 4.244 | 4.2424
~2~50~12~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Thermal conductivity | W/m-C | 0.68444 | 0.68428
~2~50~13~~-5001~ | 50 - Feedwater outlet of Feedwater Heater (PCE) [23] - LPH-5 -> Feedwater inlet of Feedwater Heater (PCE) [24] - LPH-4: Dynamic viscosity | kg/m-s | 0.00023155 | 0.00023347
~2~51~0~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 25.0205 | 25.0205
~2~51~1~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 211.2493 | 211.2491
~2~51~2~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 18.1831 | 16.587
~2~51~20~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 2.4355 | 2.4355
~2~51~4~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 903.6204 | 903.6192
~2~51~3~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | -1643.8682 | -1643.8694
~2~51~5~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | -0.031831 | -0.031832
~2~51~10~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 851.6813 | 851.6815
~2~51~11~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 4.5541 | 4.5541
~2~51~12~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.65634 | 0.65634
~2~51~13~~-5001~ | 51 - Drain outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Water/steam addition to shell of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 0.00012632 | 0.00012632
~2~53~0~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Pressure | bar | 2.18 | 2.1184
~2~53~1~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Temperature | C | 128.3819 | 128.5931
~2~53~2~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Mass flow | t/h | 326.7362 | 297.3847
~2~53~20~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Entropy | kJ/kg-C | 7.1277 | 7.1433
~2~53~4~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy | kJ/kg | 2721.9922 | 2723.0752
~2~53~3~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Enthalpy H* | kJ/kg | 174.5037 | 175.5865
~2~53~5~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Steam quality |  | 1.0054 | 1.0065
~2~53~10~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Density | kg/m^3 | 1.2053 | 1.1697
~2~53~11~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Specific heat | kJ/kg-C | 2.1223 | 2.1151
~2~53~12~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Thermal conductivity | W/m-C | 0.027674 | 0.027644
~2~53~13~~-5001~ | 53 - Outlet 1 of Splitter [34] -> Inlet of ST Assembly [1]: ST Group [36]: Dynamic viscosity | kg/m-s | 1.3288e-05 | 1.33e-05
~2~54~0~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Pressure | bar | 108.5314 | 105.0868
~2~54~1~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Temperature | C | 317.0735 | 314.6631
~2~54~2~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Mass flow | t/h | 387.7 | 353.66
~2~54~20~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Entropy | kJ/kg-C | 5.5635 | 5.5845
~2~54~4~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy | kJ/kg | 2709.3022 | 2715.9788
~2~54~3~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Enthalpy H* | kJ/kg | 161.8137 | 168.4903
~2~54~5~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Steam quality |  | 1 | 1
~2~54~10~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Density | kg/m^3 | 61.459 | 58.9913
~2~54~11~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Specific heat | kJ/kg-C | 7.3549 | 7.0935
~2~54~12~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Thermal conductivity | W/m-C | 0.083797 | 0.081808
~2~54~13~~-5001~ | 54 - Saturated steam outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Inlet of Pipe (PCE) [79]: Dynamic viscosity | kg/m-s | 2.071e-05 | 2.056e-05
~2~56~0~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Pressure | bar | 1.34 | 1.3022
~2~56~1~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Temperature | C | 107.9986 | 107.1588
~2~56~2~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Mass flow | t/h | 326.7362 | 297.3847
~2~56~20~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Entropy | kJ/kg-C | 7.1574 | 7.1737
~2~56~4~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy | kJ/kg | 2648.6372 | 2650.0066
~2~56~3~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Enthalpy H* | kJ/kg | 101.1488 | 102.5181
~2~56~5~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Steam quality |  | 0.98238 | 0.98359
~2~56~10~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Density | kg/m^3 | 0.79011 | 0.7683
~2~56~11~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Specific heat | kJ/kg-C | 4.2257 | 4.2245
~2~56~12~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Thermal conductivity | W/m-C | 0.025652 | 0.025562
~2~56~13~~-5001~ | 56 - Outlet of ST Assembly [1]: ST Group [36] -> Inlet of Splitter [47]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2527e-05
~2~57~0~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Pressure | bar | 1.34 | 1.3022
~2~57~1~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Temperature | C | 107.9986 | 107.1588
~2~57~2~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Mass flow | t/h | 19.168 | 17.3229
~2~57~20~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Entropy | kJ/kg-C | 7.1574 | 7.1737
~2~57~4~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy | kJ/kg | 2648.6372 | 2650.0066
~2~57~3~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Enthalpy H* | kJ/kg | 101.1488 | 102.5181
~2~57~5~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Steam quality |  | 0.98238 | 0.98359
~2~57~10~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Density | kg/m^3 | 0.79011 | 0.7683
~2~57~11~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Specific heat | kJ/kg-C | 4.2257 | 4.2245
~2~57~12~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Thermal conductivity | W/m-C | 0.025652 | 0.025562
~2~57~13~~-5001~ | 57 - Outlet 2 of Splitter [47] -> Inlet of Pipe (PCE) [57]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2527e-05
~2~58~0~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Pressure | bar | 1.34 | 1.3022
~2~58~1~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Temperature | C | 107.9986 | 107.1588
~2~58~2~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Mass flow | t/h | 307.5682 | 280.0619
~2~58~20~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Entropy | kJ/kg-C | 7.1574 | 7.1737
~2~58~4~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy | kJ/kg | 2648.6372 | 2650.0066
~2~58~3~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Enthalpy H* | kJ/kg | 101.1488 | 102.5181
~2~58~5~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Steam quality |  | 0.98238 | 0.98359
~2~58~10~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Density | kg/m^3 | 0.79011 | 0.7683
~2~58~11~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Specific heat | kJ/kg-C | 4.2257 | 4.2245
~2~58~12~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Thermal conductivity | W/m-C | 0.025652 | 0.025562
~2~58~13~~-5001~ | 58 - Outlet 1 of Splitter [47] -> Inlet of ST Assembly [1]: ST Group [37]: Dynamic viscosity | kg/m-s | 1.2556e-05 | 1.2527e-05
~2~59~0~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Pressure | bar | 0.4 | 0.3887
~2~59~1~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Temperature | C | 75.8568 | 75.1698
~2~59~2~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Mass flow | t/h | 307.5682 | 280.0619
~2~59~20~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Entropy | kJ/kg-C | 7.2351 | 7.2517
~2~59~4~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy | kJ/kg | 2484.623 | 2486.1553
~2~59~3~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Enthalpy H* | kJ/kg | -62.8655 | -61.3332
~2~59~5~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Steam quality |  | 0.93469 | 0.9359
~2~59~10~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Density | kg/m^3 | 0.26794 | 0.2605
~2~59~11~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Specific heat | kJ/kg-C | 4.1933 | 4.1928
~2~59~12~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Thermal conductivity | W/m-C | 0.022502 | 0.02244
~2~59~13~~-5001~ | 59 - Outlet of ST Assembly [1]: ST Group [37] -> Inlet of Splitter [49]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.1437e-05
~2~60~0~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Pressure | bar | 0.4 | 0.3887
~2~60~1~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Temperature | C | 75.8568 | 75.1698
~2~60~2~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Mass flow | t/h | 15.2987 | 13.5597
~2~60~20~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Entropy | kJ/kg-C | 7.2963 | 7.313
~2~60~4~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy | kJ/kg | 2505.9863 | 2507.478
~2~60~3~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Enthalpy H* | kJ/kg | -41.5023 | -40.0104
~2~60~5~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Steam quality |  | 0.9439 | 0.94509
~2~60~10~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Density | kg/m^3 | 0.26532 | 0.25797
~2~60~11~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Specific heat | kJ/kg-C | 4.1933 | 4.1928
~2~60~12~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Thermal conductivity | W/m-C | 0.022502 | 0.02244
~2~60~13~~-5001~ | 60 - Outlet of Mixer [62] -> Inlet of Pipe (PCE) [58]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.1437e-05
~2~61~0~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Pressure | bar | 0.4 | 0.3887
~2~61~1~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Temperature | C | 75.8568 | 75.1698
~2~61~2~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Mass flow | t/h | 293.6464 | 267.7225
~2~61~20~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Entropy | kJ/kg-C | 7.2351 | 7.2517
~2~61~4~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy | kJ/kg | 2484.623 | 2486.1553
~2~61~3~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Enthalpy H* | kJ/kg | -62.8655 | -61.3332
~2~61~5~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Steam quality |  | 0.93469 | 0.9359
~2~61~10~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Density | kg/m^3 | 0.26794 | 0.2605
~2~61~11~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Specific heat | kJ/kg-C | 4.1933 | 4.1928
~2~61~12~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Thermal conductivity | W/m-C | 0.022502 | 0.02244
~2~61~13~~-5001~ | 61 - Outlet 1 of Splitter [49] -> Inlet of ST Assembly [1]: ST Group [39]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.1437e-05
~2~62~0~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Pressure | bar | 0.45741 | 0.45741
~2~62~1~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Temperature | C | 45.5173 | 45.5173
~2~62~2~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Mass flow | t/h | 357.6548 | 325.9262
~2~62~20~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Entropy | kJ/kg-C | 0.6454 | 0.6454
~2~62~4~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy | kJ/kg | 190.5781 | 190.5781
~2~62~3~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Enthalpy H* | kJ/kg | -2356.9104 | -2356.9104
~2~62~5~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Steam quality |  | -0.060882 | -0.060882
~2~62~10~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Density | kg/m^3 | 990.0193 | 990.0193
~2~62~11~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Specific heat | kJ/kg-C | 4.1796 | 4.1796
~2~62~12~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Thermal conductivity | W/m-C | 0.6359 | 0.6359
~2~62~13~~-5001~ | 62 - Condensate outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Makeup / Blowdown [44]: Dynamic viscosity | kg/m-s | 0.00059003 | 0.00059003
~2~63~0~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 119.8959 | 116.1037
~2~63~1~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 204.2087 | 204.2084
~2~63~2~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 388.6693 | 354.5441
~2~63~20~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 2.3541 | 2.3546
~2~63~4~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 875.459 | 875.3013
~2~63~3~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | -1672.0295 | -1672.1873
~2~63~5~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | -0.51506 | -0.49257
~2~63~10~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 867.5713 | 867.2923
~2~63~11~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 4.4589 | 4.4609
~2~63~12~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.67012 | 0.66979
~2~63~13~~-5001~ | 63 - Feedwater outlet of Feedwater Heater (PCE) [32] - HPH-2 -> Feedwater inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 0.00013328 | 0.00013319
~2~64~0~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Pressure | bar | 2.75 | 2.75
~2~64~1~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Temperature | C | 39.3118 | 37.3932
~2~64~2~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Mass flow | t/h | 15118.5244 | 13806.7119
~2~64~20~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Entropy | kJ/kg-C | 0.56313 | 0.5374
~2~64~4~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy | kJ/kg | 164.8359 | 156.8152
~2~64~3~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Enthalpy H* | kJ/kg | -2382.6526 | -2390.6733
~2~64~5~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Steam quality |  | -0.17681 | -0.18051
~2~64~10~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Density | kg/m^3 | 992.599 | 993.3081
~2~64~11~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Specific heat | kJ/kg-C | 4.1779 | 4.1777
~2~64~12~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Thermal conductivity | W/m-C | 0.62836 | 0.62587
~2~64~13~~-5001~ | 64 - CW outlet of Water-cooled Condenser (PCE) [40] - COND -> Inlet of Water Sink [51] - Outfall: Dynamic viscosity | kg/m-s | 0.0006607 | 0.0006854
~2~65~0~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 3.0947 | 3.0947
~2~65~1~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 29.2957 | 27.3761
~2~65~2~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 15118.5244 | 13806.7119
~2~65~20~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.42698 | 0.40036
~2~65~4~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 122.9913 | 114.9643
~2~65~3~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2424.4973 | -2432.5242
~2~65~5~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.20507 | -0.20878
~2~65~10~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 995.9927 | 996.5438
~2~65~11~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1777 | 4.178
~2~65~12~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.61462 | 0.61178
~2~65~13~~-5001~ | 65 - Outlet of Mixer [5] -> CW inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00080843 | 0.00084293
~2~66~0~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Pressure | bar | 27.1373 | 26.3712
~2~66~1~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Temperature | C | 389.3419 | 389.2782
~2~66~2~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Mass flow | t/h | 18.1831 | 16.587
~2~66~20~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Entropy | kJ/kg-C | 6.9389 | 6.9534
~2~66~4~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy | kJ/kg | 3212.314 | 3213.521
~2~66~3~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Enthalpy H* | kJ/kg | 664.8254 | 666.0324
~2~66~5~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Steam quality |  | 1.225 | 1.2249
~2~66~10~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Density | kg/m^3 | 9.2342 | 8.9639
~2~66~11~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Specific heat | kJ/kg-C | 2.2484 | 2.242
~2~66~12~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Thermal conductivity | W/m-C | 0.055887 | 0.055801
~2~66~13~~-5001~ | 66 - Outlet of Pipe (PCE) [53] -> Heating steam inlet of Feedwater Heater (PCE) [46] - HPH-1: Dynamic viscosity | kg/m-s | 2.3943e-05 | 2.3942e-05
~2~67~0~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Pressure | bar | 18.3824 | 17.6065
~2~67~1~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Temperature | C | 343.2908 | 341.6675
~2~67~2~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Mass flow | t/h | 30.6719 | 28.0864
~2~67~20~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Entropy | kJ/kg-C | 6.9773 | 6.9934
~2~67~4~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy | kJ/kg | 3126.1704 | 3124.2595
~2~67~3~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Enthalpy H* | kJ/kg | 578.6818 | 576.771
~2~67~5~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Steam quality |  | 1.1729 | 1.1716
~2~67~10~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Density | kg/m^3 | 6.6933 | 6.4201
~2~67~11~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Specific heat | kJ/kg-C | 2.2138 | 2.2063
~2~67~12~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Thermal conductivity | W/m-C | 0.050024 | 0.049764
~2~67~13~~-5001~ | 67 - Outlet of Pipe (PCE) [54] -> Heating steam inlet of Feedwater Heater (PCE) [32] - HPH-2: Dynamic viscosity | kg/m-s | 2.1995e-05 | 2.1929e-05
~2~68~0~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Pressure | bar | 2.1373 | 2.0769
~2~68~1~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Temperature | C | 127.7141 | 127.9297
~2~68~2~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Mass flow | t/h | 9.4889 | 8.5666
~2~68~20~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Entropy | kJ/kg-C | 7.1341 | 7.1497
~2~68~4~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy | kJ/kg | 2720.9922 | 2722.0752
~2~68~3~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Enthalpy H* | kJ/kg | 173.5037 | 174.5866
~2~68~5~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Steam quality |  | 1.0053 | 1.0064
~2~68~10~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Density | kg/m^3 | 1.1832 | 1.1483
~2~68~11~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Specific heat | kJ/kg-C | 2.1192 | 2.112
~2~68~12~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Thermal conductivity | W/m-C | 0.027599 | 0.02757
~2~68~13~~-5001~ | 68 - Outlet of Pipe (PCE) [56] -> Heating steam inlet of Feedwater Heater (PCE) [23] - LPH-5: Dynamic viscosity | kg/m-s | 1.3264e-05 | 1.3276e-05
~2~69~0~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Pressure | bar | 1.3137 | 1.2767
~2~69~1~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Temperature | C | 107.4171 | 106.5803
~2~69~2~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Mass flow | t/h | 19.168 | 17.3229
~2~69~20~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Entropy | kJ/kg-C | 7.1636 | 7.1799
~2~69~4~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy | kJ/kg | 2647.6375 | 2649.0066
~2~69~3~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Enthalpy H* | kJ/kg | 100.1488 | 101.5182
~2~69~5~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Steam quality |  | 0.98235 | 0.98355
~2~69~10~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Density | kg/m^3 | 0.77564 | 0.75423
~2~69~11~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Specific heat | kJ/kg-C | 4.2249 | 4.2237
~2~69~12~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Thermal conductivity | W/m-C | 0.02559 | 0.025501
~2~69~13~~-5001~ | 69 - Outlet of Pipe (PCE) [57] -> Heating steam inlet of Feedwater Heater (PCE) [22] - LPH-6: Dynamic viscosity | kg/m-s | 1.2536e-05 | 1.2507e-05
~2~70~0~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 0.39216 | 0.38108
~2~70~1~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 75.3816 | 74.6966
~2~70~2~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 15.2987 | 13.5597
~2~70~20~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 7.302 | 7.3187
~2~70~4~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 2504.9863 | 2506.4783
~2~70~3~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -42.5022 | -41.0104
~2~70~5~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | 0.94384 | 0.94503
~2~70~10~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 0.26046 | 0.25325
~2~70~11~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.193 | 4.1925
~2~70~12~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.022459 | 0.022398
~2~70~13~~-5001~ | 70 - Outlet of Pipe (PCE) [58] -> Heating steam inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 1.1444e-05 | 1.1421e-05
~2~71~0~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Pressure | bar | 0.175 | 0.175
~2~71~1~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Temperature | C | 496.5145 | 496.6788
~2~71~2~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Mass flow | t/h | 0.43663 | 0.39801
~2~71~20~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Entropy | kJ/kg-C | 9.6317 | 9.6322
~2~71~4~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~71~3~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~71~5~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Steam quality |  | 1.3714 | 1.3716
~2~71~10~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Density | kg/m^3 | 0.049274 | 0.049263
~2~71~11~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Specific heat | kJ/kg-C | 2.1272 | 2.1273
~2~71~12~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Thermal conductivity | W/m-C | 0.066464 | 0.066485
~2~71~13~~-5001~ | 71 - Outlet 3 of Splitter [26] - k -> Heating steam inlet of Shell-Tube Water Heater (PCE) [63] - GC: Dynamic viscosity | kg/m-s | 2.8439e-05 | 2.8446e-05
~2~72~0~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Pressure | bar | 120.3095 | 116.5174
~2~72~1~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Temperature | C | 158.077 | 157.9403
~2~72~2~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Mass flow | t/h | 204.5898 | 186.4964
~2~72~20~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~72~4~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy | kJ/kg | 673.9966 | 673.1791
~2~72~3~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Enthalpy H* | kJ/kg | -1873.4919 | -1874.3093
~2~72~5~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Steam quality |  | -0.68654 | -0.66124
~2~72~10~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Density | kg/m^3 | 915.9666 | 915.8819
~2~72~11~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~72~12~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~72~13~~-5001~ | 72 - Discharge of General Pump [59] - BFP-A -> Inlet of Valve [71]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~73~0~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Pressure | bar | 86.45 | 83.7
~2~73~1~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Temperature | C | 536.4592 | 535.4362
~2~73~2~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Mass flow | t/h | 407.6178 | 371.5678
~2~73~20~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Entropy | kJ/kg-C | 6.7974 | 6.8119
~2~73~4~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~73~3~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~73~5~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Steam quality |  | 1.5235 | 1.5143
~2~73~10~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Density | kg/m^3 | 24.528 | 23.738
~2~73~11~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Specific heat | kJ/kg-C | 2.4341 | 2.4243
~2~73~12~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Thermal conductivity | W/m-C | 0.078111 | 0.077746
~2~73~13~~-5001~ | 73 - Outlet 2 of Splitter [26] - k -> Inlet of ST Assembly [1]: ST Group [16]: Dynamic viscosity | kg/m-s | 3.0377e-05 | 3.0319e-05
~2~74~0~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Pressure | bar | 120.3095 | 116.5174
~2~74~1~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Temperature | C | 158.077 | 157.9403
~2~74~2~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Mass flow | t/h | 20.5104 | 18.4487
~2~74~20~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~74~4~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy | kJ/kg | 673.9968 | 673.1791
~2~74~3~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Enthalpy H* | kJ/kg | -1873.4917 | -1874.3093
~2~74~5~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Steam quality |  | -0.68654 | -0.66124
~2~74~10~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Density | kg/m^3 | 915.9666 | 915.8819
~2~74~11~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~74~12~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~74~13~~-5001~ | 74 - Outlet 1 of Splitter [15] -> Inlet of Splitter [67]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~75~0~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Pressure | bar | 6.9655 | 6.9655
~2~75~1~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Temperature | C | 46.4533 | 46.4582
~2~75~2~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Mass flow | t/h | 358.765 | 326.891
~2~75~20~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Entropy | kJ/kg-C | 0.65737 | 0.65743
~2~75~4~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy | kJ/kg | 195.0623 | 195.0827
~2~75~3~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Enthalpy H* | kJ/kg | -2352.4263 | -2352.4058
~2~75~5~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Steam quality |  | -0.24257 | -0.24256
~2~75~10~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Density | kg/m^3 | 989.9049 | 989.9028
~2~75~11~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Specific heat | kJ/kg-C | 4.1783 | 4.1783
~2~75~12~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Thermal conductivity | W/m-C | 0.63733 | 0.63734
~2~75~13~~-5001~ | 75 - Feedwater outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Feedwater inlet of Feedwater Heater (PCE) [21] - LPH-7: Dynamic viscosity | kg/m-s | 0.00058054 | 0.00058049
~2~76~0~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Pressure | bar | 6.36 | 6.1804
~2~76~1~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Temperature | C | 226.2648 | 226.4971
~2~76~2~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Mass flow | t/h | 358.384 | 326.6145
~2~76~20~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Entropy | kJ/kg-C | 7.0559 | 7.0713
~2~76~4~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy | kJ/kg | 2905.8972 | 2907.1526
~2~76~3~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Enthalpy H* | kJ/kg | 358.4086 | 359.6642
~2~76~5~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Steam quality |  | 1.0708 | 1.0719
~2~76~10~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Density | kg/m^3 | 2.8369 | 2.7531
~2~76~11~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Specific heat | kJ/kg-C | 2.1638 | 2.1565
~2~76~12~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Thermal conductivity | W/m-C | 0.03687 | 0.036852
~2~76~13~~-5001~ | 76 - Outlet of ST Assembly [1]: ST Group [18] -> Inlet of Splitter [30]: Dynamic viscosity | kg/m-s | 1.7141e-05 | 1.7154e-05
~2~78~0~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.175 | 0.175
~2~78~1~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 52.1018 | 52.1062
~2~78~2~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 63.7705 | 58.0043
~2~78~20~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 0.73089 | 0.73095
~2~78~4~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 218.0898 | 218.1083
~2~78~3~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -2329.3987 | -2329.3801
~2~78~5~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | -0.0090313 | -0.0090235
~2~78~10~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 987.084 | 987.082
~2~78~11~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1816 | 4.1816
~2~78~12~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.64331 | 0.64331
~2~78~13~~-5001~ | 78 - Outlet of Mixer [64] -> Secondary steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 0.00052776 | 0.00052772
~2~79~0~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Pressure | bar | 0.39216 | 0.38108
~2~79~1~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Temperature | C | 52.062 | 52.0668
~2~79~2~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Mass flow | t/h | 63.3339 | 57.6063
~2~79~20~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Entropy | kJ/kg-C | 0.73037 | 0.73043
~2~79~4~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy | kJ/kg | 217.9421 | 217.9615
~2~79~3~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Enthalpy H* | kJ/kg | -2329.5464 | -2329.5271
~2~79~5~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Steam quality |  | -0.042088 | -0.040812
~2~79~10~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Density | kg/m^3 | 987.1121 | 987.1093
~2~79~11~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Specific heat | kJ/kg-C | 4.1815 | 4.1815
~2~79~12~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Thermal conductivity | W/m-C | 0.64327 | 0.64328
~2~79~13~~-5001~ | 79 - Drain outlet of Feedwater Heater (PCE) [21] - LPH-7 -> Inlet 2 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00052811 | 0.00052806
~2~80~0~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Pressure | bar | 0.0985 | 0.0985
~2~80~1~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Temperature | C | 45.5122 | 45.5122
~2~80~2~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Mass flow | t/h | 293.8842 | 267.922
~2~80~20~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Entropy | kJ/kg-C | 7.3819 | 7.3946
~2~80~4~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy | kJ/kg | 2337.2493 | 2341.3037
~2~80~3~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Enthalpy H* | kJ/kg | -210.2394 | -206.1849
~2~80~5~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Steam quality |  | 0.89714 | 0.89884
~2~80~10~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Density | kg/m^3 | 0.074908 | 0.074767
~2~80~11~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Specific heat | kJ/kg-C | 4.1797 | 4.1797
~2~80~12~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Thermal conductivity | W/m-C | 0.019935 | 0.019935
~2~80~13~~-5001~ | 80 - Outlet of ST Assembly [1]: ST Group [39] -> Steam inlet of Water-cooled Condenser (PCE) [40] - COND: Dynamic viscosity | kg/m-s | 1.048e-05 | 1.048e-05
~2~81~0~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Pressure | bar | 0.4 | 0.3887
~2~81~1~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Temperature | C | 75.8568 | 75.1698
~2~81~2~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Mass flow | t/h | 13.9218 | 12.3394
~2~81~20~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Entropy | kJ/kg-C | 7.2351 | 7.2517
~2~81~4~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy | kJ/kg | 2484.623 | 2486.1553
~2~81~3~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Enthalpy H* | kJ/kg | -62.8655 | -61.3332
~2~81~5~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Steam quality |  | 0.93469 | 0.9359
~2~81~10~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Density | kg/m^3 | 0.26794 | 0.2605
~2~81~11~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Specific heat | kJ/kg-C | 4.1933 | 4.1928
~2~81~12~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Thermal conductivity | W/m-C | 0.022502 | 0.02244
~2~81~13~~-5001~ | 81 - Outlet 2 of Splitter [49] -> Inlet 2 of Mixer [62]: Dynamic viscosity | kg/m-s | 1.146e-05 | 1.1437e-05
~2~82~0~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Pressure | bar | 0.175 | 0.175
~2~82~1~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Temperature | C | 57.2007 | 57.2007
~2~82~2~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Mass flow | t/h | 0.43663 | 0.39801
~2~82~20~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Entropy | kJ/kg-C | 0.79593 | 0.79593
~2~82~4~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy | kJ/kg | 239.4447 | 239.4447
~2~82~3~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Enthalpy H* | kJ/kg | -2308.0439 | -2308.0439
~2~82~5~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Steam quality |  | 4.0167e-08 | 4.0167e-08
~2~82~10~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Density | kg/m^3 | 984.2903 | 984.2903
~2~82~11~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Specific heat | kJ/kg-C | 4.1834 | 4.1834
~2~82~12~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Thermal conductivity | W/m-C | 0.64858 | 0.64858
~2~82~13~~-5001~ | 82 - Drain outlet of Shell-Tube Water Heater (PCE) [63] - GC -> Inlet 1 of Mixer [64]: Dynamic viscosity | kg/m-s | 0.00048668 | 0.00048668
~2~83~0~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Pressure | bar | 120.3095 | 116.5174
~2~83~1~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Temperature | C | 158.077 | 157.9403
~2~83~2~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Mass flow | t/h | 204.5898 | 186.4964
~2~83~20~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~83~4~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy | kJ/kg | 673.9966 | 673.1791
~2~83~3~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Enthalpy H* | kJ/kg | -1873.4919 | -1874.3093
~2~83~5~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Steam quality |  | -0.68654 | -0.66124
~2~83~10~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Density | kg/m^3 | 915.9666 | 915.8819
~2~83~11~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~83~12~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~83~13~~-5001~ | 83 - Outlet of Valve [71] -> Inlet 1 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~84~0~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 120.3095 | 116.5174
~2~84~1~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 158.077 | 157.9403
~2~84~2~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 10.2577 | 9.2402
~2~84~20~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~84~4~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 673.9968 | 673.1791
~2~84~3~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | -1873.4917 | -1874.3093
~2~84~5~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | -0.68654 | -0.66124
~2~84~10~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 915.9666 | 915.8819
~2~84~11~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~84~12~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~84~13~~-5001~ | 84 - Outlet 1 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~85~0~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Pressure | bar | 120.3095 | 116.5174
~2~85~1~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Temperature | C | 158.077 | 157.9403
~2~85~2~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Mass flow | t/h | 204.5898 | 186.4964
~2~85~20~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~85~4~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy | kJ/kg | 673.9966 | 673.1791
~2~85~3~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Enthalpy H* | kJ/kg | -1873.4919 | -1874.3093
~2~85~5~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Steam quality |  | -0.68654 | -0.66124
~2~85~10~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Density | kg/m^3 | 915.9666 | 915.8819
~2~85~11~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~85~12~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~85~13~~-5001~ | 85 - Discharge of General Pump [50] - BFP-B -> Inlet of Valve [70]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~86~0~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Pressure | bar | 120.3095 | 116.5174
~2~86~1~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Temperature | C | 158.077 | 157.9403
~2~86~2~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Mass flow | t/h | 409.1796 | 372.9928
~2~86~20~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~86~4~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy | kJ/kg | 673.9968 | 673.1791
~2~86~3~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Enthalpy H* | kJ/kg | -1873.4917 | -1874.3093
~2~86~5~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Steam quality |  | -0.68654 | -0.66124
~2~86~10~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Density | kg/m^3 | 915.9666 | 915.8819
~2~86~11~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~86~12~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~86~13~~-5001~ | 86 - Outlet of Mixer [66] -> Inlet of Splitter [15]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~87~0~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Pressure | bar | 120.3095 | 116.5174
~2~87~1~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Temperature | C | 158.077 | 157.9403
~2~87~2~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Mass flow | t/h | 204.5898 | 186.4964
~2~87~20~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~87~4~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy | kJ/kg | 673.9966 | 673.1791
~2~87~3~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Enthalpy H* | kJ/kg | -1873.4919 | -1874.3093
~2~87~5~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Steam quality |  | -0.68654 | -0.66124
~2~87~10~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Density | kg/m^3 | 915.9666 | 915.8819
~2~87~11~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~87~12~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~87~13~~-5001~ | 87 - Outlet of Valve [70] -> Inlet 2 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~88~0~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Pressure | bar | 120.3095 | 116.5174
~2~88~1~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Temperature | C | 152.1979 | 152.2534
~2~88~2~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~88~20~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Entropy | kJ/kg-C | 1.8515 | 1.8524
~2~88~4~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~88~3~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~88~5~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Steam quality |  | -0.70767 | -0.68129
~2~88~10~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Density | kg/m^3 | 921.4484 | 921.189
~2~88~11~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Specific heat | kJ/kg-C | 4.2799 | 4.2811
~2~88~12~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Thermal conductivity | W/m-C | 0.6917 | 0.69144
~2~88~13~~-5001~ | 88 - Discharge of General Pump [35] - BFP-C -> Inlet of Valve [69]: Dynamic viscosity | kg/m-s | 0.00018204 | 0.00018188
~2~90~0~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Pressure | bar | 120.3095 | 116.5174
~2~90~1~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Temperature | C | 152.1979 | 152.2534
~2~90~2~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~90~20~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Entropy | kJ/kg-C | 1.8515 | 1.8524
~2~90~4~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~90~3~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~90~5~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Steam quality |  | -0.70767 | -0.68129
~2~90~10~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Density | kg/m^3 | 921.4484 | 921.189
~2~90~11~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Specific heat | kJ/kg-C | 4.2799 | 4.2811
~2~90~12~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Thermal conductivity | W/m-C | 0.6917 | 0.69144
~2~90~13~~-5001~ | 90 - Outlet of Valve [69] -> Inlet 3 of Mixer [66]: Dynamic viscosity | kg/m-s | 0.00018204 | 0.00018188
~2~91~0~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Pressure | bar | 96.1447 | 93.0932
~2~91~1~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Temperature | C | 460.0024 | 460.0027
~2~91~2~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Mass flow | t/h | 397.9526 | 362.8685
~2~91~20~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Entropy | kJ/kg-C | 6.4834 | 6.503
~2~91~4~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy | kJ/kg | 3275.2939 | 3279.822
~2~91~3~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Enthalpy H* | kJ/kg | 727.8054 | 732.3334
~2~91~5~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Steam quality |  | 1.4048 | 1.3986
~2~91~10~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Density | kg/m^3 | 31.4686 | 30.3579
~2~91~11~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Specific heat | kJ/kg-C | 2.6386 | 2.6153
~2~91~12~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Thermal conductivity | W/m-C | 0.071012 | 0.070636
~2~91~13~~-5001~ | 91 - HX2 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Desuperheater [68]: Dynamic viscosity | kg/m-s | 2.7152e-05 | 2.7136e-05
~2~92~0~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Pressure | bar | 3.4473 | 3.4473
~2~92~1~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Temperature | C | 138.3289 | 138.3289
~2~92~2~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Mass flow | t/h | 204.5898 | 186.4964
~2~92~20~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~92~4~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~92~3~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~92~5~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Steam quality |  | 0.031068 | 0.031068
~2~92~10~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Density | kg/m^3 | 56.9378 | 56.9378
~2~92~11~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~92~12~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~92~13~~-5001~ | 92 - Outlet 2 of Splitter [61] -> Inlet of Valve [73]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~96~0~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Pressure | bar | 3.4473 | 3.4473
~2~96~1~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Temperature | C | 138.3289 | 138.3289
~2~96~2~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Mass flow | t/h | 204.5898 | 186.4964
~2~96~20~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~96~4~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~96~3~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~96~5~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Steam quality |  | 0.031068 | 0.031068
~2~96~10~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Density | kg/m^3 | 56.9378 | 56.9378
~2~96~11~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~96~12~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~96~13~~-5001~ | 96 - Outlet 3 of Splitter [61] -> Inlet of Valve [75]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~97~0~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Pressure | bar | 3.4473 | 3.4473
~2~97~1~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Temperature | C | 138.3289 | 138.3289
~2~97~2~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Mass flow | t/h | 2.9419e-07 | 2.9419e-07
~2~97~20~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Entropy | kJ/kg-C | 1.8842 | 1.8842
~2~97~4~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy | kJ/kg | 648.8021 | 648.8021
~2~97~3~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Enthalpy H* | kJ/kg | -1898.6864 | -1898.6864
~2~97~5~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Steam quality |  | 0.031068 | 0.031068
~2~97~10~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Density | kg/m^3 | 56.9378 | 56.9378
~2~97~11~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Specific heat | kJ/kg-C | 4.2809 | 4.2809
~2~97~12~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Thermal conductivity | W/m-C | 0.029226 | 0.029226
~2~97~13~~-5001~ | 97 - Outlet 1 of Splitter [61] -> Inlet of Valve [74]: Dynamic viscosity | kg/m-s | 1.3614e-05 | 1.3614e-05
~2~98~0~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Pressure | bar | 1.0135 | 1.0135
~2~98~1~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Temperature | C | 29.2416 | 27.3223
~2~98~2~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Mass flow | t/h | 15118.5244 | 13806.7119
~2~98~20~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Entropy | kJ/kg-C | 0.42629 | 0.39967
~2~98~4~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy | kJ/kg | 122.5733 | 114.5467
~2~98~3~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Enthalpy H* | kJ/kg | -2424.9153 | -2432.9419
~2~98~5~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Steam quality |  | -0.13137 | -0.13493
~2~98~10~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Density | kg/m^3 | 995.916 | 996.4656
~2~98~11~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Specific heat | kJ/kg-C | 4.1783 | 4.1786
~2~98~12~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Thermal conductivity | W/m-C | 0.61443 | 0.61159
~2~98~13~~-5001~ | 98 - Outlet of Water Source [3] - Intake -> Inlet of Splitter [76]: Dynamic viscosity | kg/m-s | 0.00080939 | 0.00084396
~2~99~0~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Pressure | bar | 86.45 | 83.7
~2~99~1~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Temperature | C | 536.4592 | 535.4362
~2~99~2~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Mass flow | t/h | 408.2104 | 372.1087
~2~99~20~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Entropy | kJ/kg-C | 6.7974 | 6.8119
~2~99~4~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~99~3~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~99~5~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Steam quality |  | 1.5235 | 1.5143
~2~99~10~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Density | kg/m^3 | 24.528 | 23.738
~2~99~11~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Specific heat | kJ/kg-C | 2.4341 | 2.4243
~2~99~12~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Thermal conductivity | W/m-C | 0.078111 | 0.077746
~2~99~13~~-5001~ | 99 - Outlet of Pipe (PCE) [4] -> Inlet of Splitter [26] - k: Dynamic viscosity | kg/m-s | 3.0377e-05 | 3.0319e-05
~2~100~0~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Pressure | bar | 119.4822 | 115.69
~2~100~1~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Temperature | C | 228.0941 | 228.0937
~2~100~2~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Mass flow | t/h | 388.6693 | 354.5441
~2~100~20~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Entropy | kJ/kg-C | 2.5748 | 2.5755
~2~100~4~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy | kJ/kg | 983.4664 | 983.3674
~2~100~3~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Enthalpy H* | kJ/kg | -1564.0221 | -1564.1212
~2~100~5~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Steam quality |  | -0.42236 | -0.40165
~2~100~10~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Density | kg/m^3 | 838.1572 | 837.8237
~2~100~11~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Specific heat | kJ/kg-C | 4.5927 | 4.5957
~2~100~12~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Thermal conductivity | W/m-C | 0.65107 | 0.65068
~2~100~13~~-5001~ | 100 - Feedwater outlet of Feedwater Heater (PCE) [46] - HPH-1 -> Inlet of Pipe (PCE) [77]: Dynamic viscosity | kg/m-s | 0.00011886 | 0.00011877
~2~101~0~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 98.0676 | 94.9551
~2~101~1~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 411.5042 | 411.5043
~2~101~2~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 397.9526 | 362.8685
~2~101~20~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 6.2789 | 6.3008
~2~101~4~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 3136.2087 | 3142.3862
~2~101~3~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 588.7203 | 594.8977
~2~101~5~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1.3063 | 1.3025
~2~101~10~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 35.865 | 34.5336
~2~101~11~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 2.9442 | 2.9026
~2~101~12~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.06752 | 0.066993
~2~101~13~~-5001~ | 101 - Steam outlet of Boiler Assembly [1]: Desuperheater [78] -> HX2 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.501e-05 | 2.4996e-05
~2~102~0~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 120.3095 | 116.5174
~2~102~1~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 158.077 | 157.9403
~2~102~2~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 10.2526 | 9.2085
~2~102~20~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 1.9103 | 1.9094
~2~102~4~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 673.9968 | 673.1791
~2~102~3~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | -1873.4917 | -1874.3093
~2~102~5~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | -0.68654 | -0.66124
~2~102~10~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 915.9666 | 915.8819
~2~102~11~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 4.2948 | 4.2956
~2~102~12~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.69063 | 0.6904
~2~102~13~~-5001~ | 102 - Outlet 3 of Splitter [67] -> Desuperheating water inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 0.00017476 | 0.00017483
~2~103~0~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Pressure | bar | 106.4033 | 103.0262
~2~103~1~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Temperature | C | 338.9837 | 339.0041
~2~103~2~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Mass flow | t/h | 387.7 | 353.66
~2~103~20~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Entropy | kJ/kg-C | 5.806 | 5.8404
~2~103~4~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy | kJ/kg | 2851.1492 | 2865.3564
~2~103~3~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Enthalpy H* | kJ/kg | 303.6606 | 317.8678
~2~103~5~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Steam quality |  | 1.1077 | 1.112
~2~103~10~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Density | kg/m^3 | 51.2262 | 48.8207
~2~103~11~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Specific heat | kJ/kg-C | 4.8821 | 4.6642
~2~103~12~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Thermal conductivity | W/m-C | 0.073185 | 0.071427
~2~103~13~~-5001~ | 103 - HX3 outlet of Boiler Assembly [1]: Circulating Fluidized Bed [7] -> Steam inlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH: Dynamic viscosity | kg/m-s | 2.1709e-05 | 2.1689e-05
~2~104~0~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 108.5314 | 105.0868
~2~104~1~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 317.0735 | 314.6631
~2~104~2~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 387.7 | 353.66
~2~104~20~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Entropy | kJ/kg-C | 5.5635 | 5.5845
~2~104~4~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy | kJ/kg | 2709.3022 | 2715.9788
~2~104~3~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 161.8137 | 168.4903
~2~104~5~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Steam quality |  | 1 | 1
~2~104~10~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Density | kg/m^3 | 61.459 | 58.9913
~2~104~11~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Specific heat | kJ/kg-C | 7.3549 | 7.0935
~2~104~12~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Thermal conductivity | W/m-C | 0.083797 | 0.081808
~2~104~13~~-5001~ | 104 - Outlet of Pipe (PCE) [79] -> HX3 inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Dynamic viscosity | kg/m-s | 2.071e-05 | 2.056e-05
~2~105~0~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Pressure | bar | 98.0676 | 94.9551
~2~105~1~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Temperature | C | 434.1031 | 434.1035
~2~105~2~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Mass flow | t/h | 387.7 | 353.66
~2~105~20~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Entropy | kJ/kg-C | 6.3725 | 6.3932
~2~105~4~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy | kJ/kg | 3201.3213 | 3206.6785
~2~105~3~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Enthalpy H* | kJ/kg | 653.8326 | 659.1899
~2~105~5~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Steam quality |  | 1.3553 | 1.3501
~2~105~10~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Density | kg/m^3 | 33.9954 | 32.7651
~2~105~11~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Specific heat | kJ/kg-C | 2.7807 | 2.749
~2~105~12~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Thermal conductivity | W/m-C | 0.06906 | 0.068612
~2~105~13~~-5001~ | 105 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [41] - LTSH -> Steam inlet of Boiler Assembly [1]: Desuperheater [78]: Dynamic viscosity | kg/m-s | 2.602e-05 | 2.6005e-05
~2~110~0~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Pressure | bar | 88.2061 | 85.4066
~2~110~1~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Temperature | C | 537.2003 | 536.1599
~2~110~2~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Mass flow | t/h | 408.2104 | 372.1087
~2~110~20~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Entropy | kJ/kg-C | 6.7886 | 6.8031
~2~110~4~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy | kJ/kg | 3482.1716 | 3482.5215
~2~110~3~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Enthalpy H* | kJ/kg | 934.6831 | 935.0328
~2~110~5~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Steam quality |  | 1.5296 | 1.5201
~2~110~10~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Density | kg/m^3 | 25.0292 | 24.2249
~2~110~11~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Specific heat | kJ/kg-C | 2.4402 | 2.4303
~2~110~12~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Thermal conductivity | W/m-C | 0.078355 | 0.077983
~2~110~13~~-5001~ | 110 - Steam outlet of Boiler Assembly [1]: Superheater (PCE) [38] - FSH -> Inlet of Boiler Assembly [1]: Valve [31]: Dynamic viscosity | kg/m-s | 3.0418e-05 | 3.0359e-05
~2~112~0~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Pressure | bar | 118.2992 | 114.5446
~2~112~1~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Temperature | C | 226.1392 | 226.1398
~2~112~2~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Mass flow | t/h | 388.6693 | 354.5441
~2~112~20~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Entropy | kJ/kg-C | 2.5571 | 2.5578
~2~112~4~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy | kJ/kg | 974.4664 | 974.3673
~2~112~3~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Enthalpy H* | kJ/kg | -1573.0221 | -1573.1212
~2~112~5~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Steam quality |  | -0.42326 | -0.40283
~2~112~10~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Density | kg/m^3 | 840.5917 | 840.2652
~2~112~11~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Specific heat | kJ/kg-C | 4.5809 | 4.5837
~2~112~12~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Thermal conductivity | W/m-C | 0.65273 | 0.65235
~2~112~13~~-5001~ | 112 - Outlet of Boiler Assembly [1]: Valve [13] -> Water inlet of Boiler Assembly [1]: Economiser (PCE) [42] - ECO: Dynamic viscosity | kg/m-s | 0.0001199 | 0.0001198
~3~9~0~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Pressure | bar | 1.0124 | 1.0124
~3~9~1~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Temperature | C | 33 | 33
~3~9~2~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Mass flow | t/h | 73.3954 | 63.9258
~3~9~3~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Enthalpy H* | kJ/kg | 15181.7607 | 15424.9043
~3~9~4~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: LHV | kJ/kg | 15162.0674 | 15407.5234
~3~9~5~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: HHV | kJ/kg | 16747 | 16747
~3~9~8~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Molecular weight | M.W. | 6.9687 | 7.5583
~3~9~6~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (LHV) | kW | 309123.0938 | 273598.1875
~3~9~7~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Energy flow (HHV) | kW | 341436.5625 | 297383.8438
~3~9~120~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Fuel LHV price | USD/GJ | 2.4392 | 2.4392
~3~9~20~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Ash | % | 6.61 | 6.61
~3~9~21~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Moisture | % | 40.05 | 30
~3~9~22~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Carbon | % | 39.35 | 39.35
~3~9~23~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Hydrogen | % | 2.78 | 2.78
~3~9~24~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Oxygen | % | 10.41 | 20.46
~3~9~25~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Nitrogen | % | 0.55 | 0.55
~3~9~26~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Sulfur | % | 0.25 | 0.25
~3~9~27~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Chlorine | % | 0 | 0
~3~9~28~~-5001~ | 9 - Outlet of Fuel Source [10] - Coal -> Fuel inlet of Boiler Assembly [1]: Circulating Fluidized Bed [7]: Weight percent of Argon | % | 0 | 0
Note on D6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,3
Note on E6: ****************** Advisory Messages ******************* General Pump [50] - BFP-B : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. General Pump [59] - BFP-A : Advisory: 8 - Two-phase fluid is at pump inlet and the pump power computation assumes inlet is liquid only. You should precool or pressurize the fluid upstream of pump. Valve [74] : Advisory: 5 - Your selection to set the valve 'completely closed' has been overridden by the system's imposition of a throughflow. You may re-set the flow priority from 'Moderate' to 'Strong'. Boiler Assembly [1]: Advisory: 9 - Assembly is in TD mode so Assembly cannot be completely computed. ***************** Computation Remarks ****************** Boiler Assembly [1]: Economiser (PCE) [42] - ECO : Remark: 6 - Water exit temperature has been reduced by minimum DT allowed. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [21] - LPH-7 : Remark: 6 - Heating steam energy is not enough for desuperheating section. No desuperheating section designed Feedwater Heater (PCE) [21] - LPH-7 : Remark: 8 - Feedwater exit temperature cut off by minimum pinch. Feedwater Heater (PCE) [22] - LPH-6 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [23] - LPH-5 : Remark: 3 - Desired feedwater exit temperature is cut off by the maximum achievable value. Feedwater Heater (PCE) [46] - HPH-1 : Remark: 9 - The specified terminal difference -4.1 C is too low. It has been raised to satisfy the minimum pinch ST Assembly [1]: Remark: 28 - Makeup steam (from HPT inlet) has been sent to Steam Sealing Regulator (SSR) system to supply the demanded sealing steam. ST Assembly [1]: Remark: 29 - There is zero leakage flow to the Steam Sealing Regulator (SSR) system. Computation time = 00:00:00,5

## Eng_Info
Power Out | 110 | MW
Turbine Pressure
Load | Power | Range | Elink | HP | 100% Case (bara) |  | 75% Case (bara) |  | 50% Case (bara) |  | Power (MW) | Ps (bara) | Ts ( C ) | Ms' ( tph ) | FEGT ( C ) | Stack ( C ) | 75% Case (bara)
50% | 70 | 55 - <70 | ELINK (3) | Main steam (1st stage) | 86.13 |  | 79.5825 |  | 71.3475 |  | 55 | 71.3475 | 530.798 | 200.5 | 857 | 149.3 | 86.15
75% | 82.5 | 70 - 93 | ELINK (2) | 2nd Stage | 27.68 | 0.32137 | 25.5758 | 0.32137 | 22.9293 | 0.32137 | 85 | 79.5825 | 533.906 |  |  |  | 20.83 | 0.24179
100% | 93 | >93 - 110 | ELINK | 3rd Stage | 18.48 | 0.21456 | 17.0752 | 0.21456 | 15.3083 | 0.21456 | 110 | 86.445 | 536.496 | 387.7 | 894 | 148.2 | 14.24 | 0.16529
Full Load | 110 | MW |  | 4th Stage | 6.36 | 0.073842 | 5.8765 | 0.073842 | 5.2684 | 0.073842 | [6 empty] | 5.244 | 0.060871
|  |  |  | 5th Stage | 5.5 | 0.063857 | 5.0819 | 0.063857 | 4.556 | 0.063857 | [6 empty] | 4.2 | 0.048752
|  | 61.5 |  | LP
|  |  |  | 6th Stage | 2.18 | 0.025311 | 2.0143 | 0.025311 | 1.8058 | 0.025311 | [6 empty] | 2.18 | 0.025305
|  | 55 |  | 7th Stage | 1.34 | 0.015558 | 1.2381 | 0.015558 | 1.11 | 0.015558 | [6 empty] | 1.34 | 0.015554
|  | 18.3333 |  | 8th Stage | 0.4 | 0.0046441 | 0.36959 | 0.0046441 | 0.33135 | 0.0046441 | [6 empty] | 0.4 | 0.0046431
[11 empty] | Pw | Ps
HHV Fuel | kJ/kg | [9 empty] | 55 | 71.35 |  | 85 | 79.5825
100% | 15026 | 3588.8984 | [8 empty] | 110 | 86.45
75% | 14599 | 3486.9112
50% | 15332 | 3661.9853
[11 empty] | Pw | Ts
| Trial Fuel | [9 empty] | 55 | 530.8 |  | 85 | 533.906
| 3600 | 15072.48 | [8 empty] | 110 | 536.5
| 4000 | 16747.2
[11 empty] | Pw | Ms | DSH
[11 empty] | 55 | 210 | 9.8 | 85 | 317.7795
[11 empty] | 110 | 407.6 | 20.5
[11 empty] | Pw | Ms'-20
[11 empty] | 55 | 200.5 |  | 85 | 302.606
[11 empty] | 110 | 387.7
[11 empty] | Pw | FEGT
[11 empty] | 55 | 857 |  | 85 | 877.1795
[11 empty] | 110 | 894

## input
Expected Output Power |  | 65 | MW | ELINK (3)
Sheet Name
Group | Status | Parameters | Unit | short_name | Baris (New) | Notes | min | max |  | Value
Generator | view | Generator Power Factor |  | generator_power_factor | 388 |  | 0.75 | 0.95 | ST Assembly [1]: Generator design point power factor | 0.9 | 1
Boiler | view | Desired Coal HHV (kJ/kg) | kcal/kg | desired_coal_hhv | 181 |  | 3375 | 4775 | Fuel Source [10] - Coal : HHV @ 25C | 16747 | 1
Boiler | view | Total Moisture (% wg) | % | total_moisture | 173 |  | 25 | 45 | Fuel Source [10] - Coal : Weight percent of Moisture | 30 | 1
Boiler | view | Main Steam Temp. | C | main_steam_temp | 296 |  | 510 | 538 | Boiler Assembly [1]: Superheater (PCE) [38] - FSH : Desired steam outlet temperature | 532.534
Boiler | view | Saturated Steam Mass Flow | ton/h | sat_steam_mass_flow | 21 |  | 345 | 1175 | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Steam production rate | 234.534
Boiler | view | Main Steam Press. | bara | main_steam_press | 391 |  | 60 | 167 | ST Assembly [1]: ST Group [16] : Design point Inlet pressure (upstream of any stop or control valves) | 74.0925
Boiler | view | Excess Air | % |  | 24 |  | 15 | 40 | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Excess air | 25 | 1
Ambient Condition | view | Ambient Temperature ( C ) | C |  | 17 |  | 25 | 33 | Site Menu: Ambient temperature | 30 | 1
Ambient Condition | view | Relative Humidity (%) | % |  | 18 |  | 60 | 80 | Site Menu: Ambient relative humidity | 75 | 1
Ambient Condition | view | Ambient Pressure (bar) | bar |  | 20 |  | 1.0123 | 1.0132 | Site Menu: Ambient pressure | 1.0124 | 1
Boiler | background input | FEGT | C | fegt | 23 | Korelasi formula dari main steam press |  |  | Boiler Assembly [1]: Circulating Fluidized Bed [7] : Design point furnace temperature | 863.7255
Turbine | background input | 2nd Stage | bar | hp_turbine2_in | 400 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [17] : Design point Inlet pressure (upstream of any stop or control valves) | 23.8111
Turbine | background input | 3rd Stage | bar | hp_turbine3_in | 409 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [18] : Design point Inlet pressure (upstream of any stop or control valves) | 15.8973
Turbine | background input | 4th Stage | bar | hp_turbine4_in | 418 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [19] : Design point Inlet pressure (upstream of any stop or control valves) | 5.471
Turbine | background input | 5th Stage | bar | hp_turbine5_in | 427 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [20] : Design point Inlet pressure (upstream of any stop or control valves) | 4.7308
Turbine | background input | 6th Stage | bar | lp_turbine1_in | 436 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [36] : Design point Inlet pressure (upstream of any stop or control valves) | 1.8753
Turbine | background input | 7th Stage | bar | lp_turbine2_in | 445 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [37] : Design point Inlet pressure (upstream of any stop or control valves) | 1.1527
Turbine | background input | 8th Stage | bar | lp_turbine3_in | 454 | Korelasi formula dari main steam press |  |  | ST Assembly [1]: ST Group [39] : Design point Inlet pressure (upstream of any stop or control valves) | 0.34409
Condenser | View | Water Coling Inlet Temp |  |  | 348 |  |  |  | Water Source [3] - Intake : Temperature | 27.3 | 1
Condenser | View | Cooling Temp. Rise |  |  | 355 |  |  |  | Water-cooled Condenser (PCE) [40] - COND : Cooling water temperature rise | 10 | 1
Note on F5: Adhy Marwanto: di konversi ke kJ/kg ketika di inject ke thermoflow. kali dengan 4.1868
Note on M5: Adhy Marwanto: input from what if sim. This default value is just tracing back value from the default modelling coal HHV.

## output
CODE |  | Drawing | Show at View | Param Type | Param Group |  | Unit |  | Ref | Value | Cell Address | Param Name | Baseline Value
1 | 5 | N/A |  | output | Generator | Generator Power Factor |  | generator_power_factor | E1610 | #REF! | 1610 | #REF! | #REF!
2 | 6 |  |  | output | Generator | Gross Power Output | kW | gross_power_output | E470 | #REF! | 470 | #REF! | #REF!
3 | 7 | N/A |  | output | Generator | Auxiliary Power consumption | kW | auxiliary_power_consumption | E473 | #REF! | 473 | #REF! | #REF!
4 | 8 | D31 |  | output | Boiler | Coal HHV | kJ/kg | desired_coal_hhv | E1019 | #REF! | 1019 | #REF! | #REF!
5 | 9 | D53 | 1 | output | Generator | Gross Output | kW | gross_output | E470 | #REF! | 470 | #REF! | #REF!
6 | 10 |  |  | output | Boiler | Boiler Efficiency | % | boiler_efficiency | E475 | #REF! | 475 | #REF! | #REF!
7 | 11 | N/A | 1 | output | Generator | Net Output | kW | net_output | E471 | #REF! | 471 | #REF! | #REF!
8 | 12 | N/A | 1 | output | Boiler | Net Heatrate (HHV) | kcal/kWh | net_heatrate | E484 | #REF! | 484 | #REF! | #REF!
9 | 13 | N/A | 1 | output | Plant | Gross Heatrate (LHV) | kcal/kWh | gross_heatrate | E476 | #REF! | 476 | #REF! | #REF!
10 | 14 | N/A |  | output | Plant | Plant Efficiency (HHV) | kcal/kWh | plant_efficiency | E481 | #REF! | 481 | #REF! | #REF!
11 | 15 | N/A |  | output | Boiler | SSH Steam Outlet Temperature | C | ssh_steam_outlet_temperature | E1475 | #REF! | 1475 | #REF! | #REF!
12 | 16 | N/A |  | output | Boiler | SSH Steam Outlet Pressure | MPa | ssh_steam_outlet_pressure | E1474 | #REF! | 1474 | #REF! | #REF!
13 | 17 | N/A |  | output | Boiler | SSH Steam Outlet Flow | t/h | ssh_steam_outlet_flow | E1473 | #REF! | 1473 | #REF! | #REF!
14 | 18 | D41 |  | output | Boiler | Main Steam Inlet Temperature | C | main_steam_inlet_temperature | E3238 | #REF! | 3238 | #REF! | #REF!
15 | 19 | D42 |  | output | Boiler | Main Steam Inlet Pressure | MPa | main_steam_inlet_pressure | E3237 | #REF! | 3237 | #REF! | #REF!
16 | 20 | D40 |  | output | Boiler | Main Steam Inlet Flow | t/h | main_steam_inlet_flow | E3239 | #REF! | 3239 | #REF! | #REF!
17 | 21 | D51 |  | output | Turbine | LP ST Steam Inlet Temperature | C | lp_st_steam_inlet_temperature | E3029 | #REF! | 3029 | #REF! | #REF!
18 | 22 | D52 |  | output | Turbine | LP ST Steam Inlet Pressure | MPa | lp_st_steam_inlet_pressure | E3028 | #REF! | 3028 | #REF! | #REF!
19 | 23 | D50 |  | output | Turbine | LP ST Steam Inlet Flow | t/h | lp_st_steam_inlet_flow | E3030 | #REF! | 3030 | #REF! | #REF!
20 | 24 | D20 |  | output | Condenser | Cond. CW Flow | t/h | cond_cw_flow | E3459 | #REF! | 3459 | #REF! | #REF!
21 | 25 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff1 | E1663 | #REF! | 1663 | #REF! | #REF!
22 | 26 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff2 | E1690 | #REF! | 1690 | #REF! | #REF!
23 | 27 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff3 | E1717 | #REF! | 1717 | #REF! | #REF!
24 | 28 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff4 | E1744 | #REF! | 1744 | #REF! | #REF!
25 | 29 | N/A |  | output | Turbine | HP Dry Step Eff. | % | hp_dry_step_eff5 | E1771 | #REF! | 1771 | #REF! | #REF!
26 | 30 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff1 | E1798 | #REF! | 1798 | #REF! | #REF!
27 | 31 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff2 | E1825 | #REF! | 1825 | #REF! | #REF!
28 | 32 | N/A |  | output | Turbine | LP Dry Step Eff. | % | lp_dry_step_eff3 | E1857 | #REF! | 1857 | #REF! | #REF!
29 | 33 | D11 |  | output | FWH1 | FWH1 Terminal Temperature Difference | C | fwh1_terminal_temperature_difference | E997 | #REF! | 997 | #REF! | #REF!
30 | 34 | D09 |  | output | FWH2 | FWH2 Terminal Temperature Difference | C | fwh2_terminal_temperature_difference | E979 | #REF! | 979 | #REF! | #REF!
31 | 35 | D07 |  | output | Condensate | FWH4 Terminal Temperature Difference | C | fwh4_terminal_temperature_difference | E961 | #REF! | 961 | #REF! | #REF!
32 | 36 | D05 |  | output | Condensate | FWH5 Terminal Temperature Difference | C | fwh5_terminal_temperature_difference | E943 | #REF! | 943 | #REF! | #REF!
33 | 37 | D03 |  | output | Condensate | FWH6 Terminal Temperature Difference | C | fwh6_terminal_temperature_difference | E926 | #REF! | 926 | #REF! | #REF!
34 | 38 | D01 |  | output | Condensate | FWH7 Terminal Temperature Difference | C | fwh7_terminal_temperature_difference | E909 | #REF! | 909 | #REF! | #REF!
35 | 39 | D12 |  | output | FWH1 | FWH1 Drain Cooler Approach | C | fwh1_drain_cooler_approach | E998 | #REF! | 998 | #REF! | #REF!
36 | 40 | D10 |  | output | FWH2 | FWH2 Drain Cooler Approach | C | fwh2_drain_cooler_approach | E980 | #REF! | 980 | #REF! | #REF!
37 | 41 | D08 |  | output | Condensate | FWH4 Drain Cooler Approach | C | fwh4_drain_cooler_approach | E962 | #REF! | 962 | #REF! | #REF!
38 | 42 | D06 |  | output | Condensate | FWH5 Drain Cooler Approach | C | fwh5_drain_cooler_approach | E944 | #REF! | 944 | #REF! | #REF!
39 | 43 | D04 |  | output | Condensate | FWH6 Drain Cooler Approach | C | fwh6_drain_cooler_approach | E927 | #REF! | 927 | #REF! | #REF!
40 | 44 | D02 |  | output | Condensate | FWH7 Drain Cooler Approach | C | fwh7_drain_cooler_approach | E910 | #REF! | 910 | #REF! | #REF!
41 | 45 | D18 |  | output | Condenser | Cond. Main Steam Inlet Pressure | MPa | cond_main_steam_inlet_pressure | E3303 | #REF! | 3303 | #REF! | #REF!
42 | 46 | D19 |  | output | Condenser | Cond. Cooling Water Inlet Temperature | C | cond_cooling_water_inlet_temperature | E348 | #REF! | 348 | #REF! | #REF!
43 | 47 | D21 |  | output | Condenser | Cond. Cooling Water Exit Temperature | C | cond_cooling_water_exit_temperature | E1593 | #REF! | 1593 | #REF! | #REF!
44 | 48 | D20 |  | output | Condenser | Cond. Cooling Water Inlet Flow | t/h | cond_cooling_water_inlet_flow | E3459 | #REF! | 3459 | #REF! | #REF!
45 | 49 | D30 |  | output | Boiler | Coal Flow | t/h | coal_flow | E3569 | #REF! | 3569 | #REF! | #REF!
46 | 50 | D39 |  | output | Boiler | Stack Temperature | C | stack_temperature | E2297 | #REF! | 2297 | #REF! | #REF!
50 | 54 | D32 |  | output | Air Preheater | APH Flue gas inlet temperature | C | aph_flue_gas_inlet_temperature | E2027 | #REF! | 2027 | #REF! | #REF!
51 | 55 | D36 |  | output | Air Preheater | SA Outlet Temp. | C | sa_outlet_temp | E2189 | #REF! | 2189 | #REF! | #REF!
52 | 56 | D34 |  | output | Air Preheater | PA Outlet Temp. | C | pa_outlet_temp | E2108 | #REF! | 2108 | #REF! | #REF!
53 | 57 | D33 |  |  |  | Flue Gas Outlet Temp | C | flue_gas_outlet_temp | E1919 | #REF! | 1919 | #REF! | #REF!
54 | 58 | D37 |  |  |  | SA Inlet Temp | C | sa_inlet_temp | E2216 | #REF! | 2216 | #REF! | #REF!
55 | 59 | D35 |  |  |  | PA Inlet Temp | C | pa_inlet_temp | E2135 | #REF! | 2135 | #REF! | #REF!
56 | 60 | D56 |  |  |  | LP Steam Efficiency | % | lp_steam_efficiency | AVERAGE(J25:J29) | #REF!
57 | 61 | D57 |  |  |  | HP Steam Efficiency | % | hp_steam_efficiency | AVERAGE(J30:J32) | #REF!
58 | 62 | D61 |  |  |  | Ambient Temperature | C | ambient_temperature | E17 | #REF! | 17 | #REF! | #REF!
59 | 63 | D62 |  |  |  | Relative Humidity | % | relative_humidity | E18 | #REF! | 18 | #REF! | #REF!
60 | 64 | D63 |  |  |  | Ambient Pressure | MPa | ambient_pressure | E2027 | #REF! | 2027 | #REF! | #REF!
61 | 65 | D15 |  |  |  | Feedwater mass flow | t/h | feedwater_mass_flow | E3481 | #REF! | 3481 | #REF! | #REF!
62 | 66 | D16 |  |  |  | Feedwater Temperature | C | feedwater_temperature | E3480 | #REF! | 3480 | #REF! | #REF!
63 | 67 | D17 |  |  |  | Feedwater Pressure | MPa | feedwater_pressure | E3479 | #REF! | 3479 | #REF! | #REF!
Note on G6: Adhy Marwanto: Yang ditampilkan MW hasil kalkulasi oleh thermoflow, bukan expected. Tampilan dalam MW.
Note on C59: Adhy Marwanto: ketiga item ini tampilkan di drawing posisi di bawah Air Heater.